STATE OF NORTH CAROLINA

DEPARTMENT OF ENVIRONMENTAL QUALITY

DIVISION OF WATER RESOURCES

GENERAL PERMIT NO. WQGxxxxxx – Accessory Dwelling Units (ADUs)

PERMITTING ACCESSORY DWELLING UNITS AND ACCESSORY RESIDENTIAL BUILDINGS TO SHARE A SHARED SEWER LINE WITH A PRIMARY RESIDENCE

15A NCAC 02T.0300

In compliance with the provisions of North Carolina General Statute 143-215.1, and other lawful standards and regulations promulgated and adopted by the North Carolina Environmental Management Commission, this permit is hereby issued to all owners and/or operators, hereafter permittees, which are covered by this permit as evidenced by receipt of a Certificate of Coverage from the Division of Water Resources to allow the allow accessory dwelling units and accessory residential buildings to share a common private sewer line with a primary residence, in accordance with the  conditions set forth in Parts I, II, and III hereof.

This permit shall become effective Month, Day, Year.

This permit shall expire at midnight on Month, Day, Year.

Signed this day Month, Day, Year.

____________________________________________

Linda Culpepper, Director

Division of Water Resources

By Authority of the Environmental Management Commission

PART I.

SECTION A. Coverage

- Eligibility of Coverage

- Existing primary residential property owners which wish to construct an accessory dwelling unit (ADU) or an accessory residential building (ARB) on their existing parcel, and which seek to allow the new ADU/ARB to share a common private sewer line with the existing primary residence.

- New construction which includes a primary residence and an ADU/ARB, which share a common private sewer line.

- Existing primary residential property owners with an existing ARB not currently served by a separate building sewer line, which they wish to covert to an ADU by adding a building sewer.

- Sewer lines shared between two or more buildings require a sewer line extension permit in accordance with 15A NCAC 02T.0300 and NCGS 143-215.1. Nothing in this permit shall be deemed to apply to or permit disposal systems for which a state National Pollutant Discharge Elimination System permit or where any other state or local discharge/non-discharge permit is otherwise required.

- The parcel on which both the primary residence and the ADU/ARB are to be located must be deed restricted in perpetuity from subdivision of the parcel in any form that would result in the separation of the primary residence and the ADU/ARB to discrete parcels.

- Limitations on Coverage

- Although this general permit does not cover the following types of sewer line configurations, other permits such as an individual sewer line extension permit from the Division may be obtained. This permit does not authorize shared sewer lines in the following configurations:

- Where both building sewers are pressurized, with a pump station serving both the primary residence and the ADU/ARB.

- Shared private gravity sewer lines with a diameter of less than 4-inches.

- Sewer lines shared between more than one primary residence and one ADU/ARB.

- Shared sewer lines where either of the two buildings is non-residential (e.g. commercial, industrial, or other).

- Shared sewer lines where the ADU is larger than 3-bedrooms, with a calculated flow of 360 gallons per day (GPD) as specified in 15A NCAC 02T.0114.

- This permit does not authorize shared sewer line extensions that the Division has determined to be or which may reasonably be expected to be contributing to a violation of a water quality standard (as defined in the “Red Book” or NC Administrative Code 15A NCAC 02B .0100, .0200, and .0300).

- If the Division determines at any time that the shared sewer line is causing or contributing to a violation of water quality standards or if the Division has any other grounds for modifying or revoking this permit, the Division may require corrective action to be completed by the property owner or require the shared sewer line be permitted differently in accordance with Part II, Section B of this permit. The Division may deny coverage under this permit and require submittal of an application for an individual sewer line extension permit based on a review of the Notice of Intent (NOI) or other information.

- Coverage of existing sewer systems

Upon issuance of this general permit, all existing shared private sewer lines which meet all requirements listed herein shall be considered to be covered under this general permit. New and currently under construction shared private sewer lines shall not be considered to be covered by this general permit until a Certificate of Coverage is applied for and obtained.

SECTION B. Sewer Extension Installation Requirements

[NCGS 143-215.1]

[15A NCAC 02T.0300]

(1) Existing Building Sewer Line Serving an Existing Primary Residence

- Existing gravity sewer lines with a diameter of less than 4-inches must be replaced from the point of connection of the ADU/ARB sewer line to the sewer main with a private sewer line of a minimum of 4-inches in diameter.

- The existing line, including pump station as applicable, must be verified by the property owner to be flowing clearly to the main sewer line without impedance. Documentation shall be provided to the local building inspector upon request.

- The existing building sewer, being converted to a shared private sewer line, must meet the separation requirements as outlined in 15A NCAC 02T.0305(f) to the maximum extent possible. These separations shall be achieved, to the maximum extent possible, by locating the tie-in for the new sewer line appropriately. In no case shall the tie-in from the building sewer for the ADU/ARB be located closer to the primary residence’s foundation/basement, a private well, or swimming pool than the existing building sewer.

(2) Sewer Line Serving A New ADU/ARB

- The building sewer may be either a) non-pressurized gravity sewer, with a minimum of 4-inches in diameter in accordance with current NC Plumbing Code or b) a pressurized sewer comprised of a pump station and force main with a diameter of 1.25 to 3 inches.

- If the existing building sewer for the primary residence is comprised of a pump station and force main, the new building sewer for the ADU/ARB must be non-pressurized and tie into the existing pump station or gravity building sewer from the primary residence to the pump station.

- The new building sewer line must be installed to the most current plumbing code requirements.

- All work must be completed by a North Carolina licensed plumber.

(3) New Construction

- Where both the primary residence and the ADU/ARB are new construction, all separations as outlined in 15A NCAC 02T.0305(f) shall be met. Any deviations from those separations shall negate coverage by this general permit.

(4) Miscellaneous

- In no case shall the tie-in from the building sewer for the ADU/ARB be located under the foundation for the primary residence or within the primary residence in any manner.

SECTION C. Application for Coverage.

        - Application for coverage must be made by the property owner or a designated authority.

        - Records Retention: The permittee (property owner) shall retain records of coverage by this general permit for the lifetime of the shared sewer line extension [15A NCAC 02T.0___]

PART II.

STANDARD CONDITIONS

Section A. Definitions

Accessory Dwelling Unit (ADU)

A single-family residence comprised of 3-bedrooms or less, constructed on the same parcel as a primary residence.

Accessory Residential Building (ARB)

An accessory building to a primary residence, such as a garage or workshop, which may be served by a sewer lateral due to the presence of a sink, shower, toilet, or other fixture.

Building

Any structure occupied or intended for supporting or sheltering any occupancy.

Building Sewer

That part of the drainage system which conveys the discharge from a single building to a public gravity sewer, private gravity sewer, individual sewage disposal system, or other point of disposal.

Certificate of Coverage

A document issued by the Division to a property owner, which states that an eligible primary residence with ADU/ARB, which share a private sewer line at a specific address, are covered under this general permit.

Designated Authority

Any person or corporation authorized by the property owner of the primary residence to sign documents for the purpose of obtaining a Certificate of Coverage under this general permit.

DWR or “the Division”

The Division of Water Resources, Department of Environmental Quality.

New ADU/ARB

A new ADU or ARB shall be one where the building sewer serving that building is new, regardless of whether the structure itself was existing previously.

Permit Issuing Authority

The Director of the Division of Water Resources.

Permittee

The holder of a Certificate of Coverage as issued by this general permit.

Primary Residence

A residential building governed by the North Carolina One- and Two-Family Building Code. May be a single-family residence or a duplex, multi-family residence. Triplex and larger multi-family residential structures are excluded from this definition and from coverage by this general permit.

Private Sewer

Any part of a sewer system which collects wastewater from more than one building and is located on private property.

Property Owner

The owner of a parcel on which a primary residence and an ADU/ARB are physically located.

Shared/Common Sewer Line

A gravity sewer line with a diameter of 4-inches or greater, or a pump station with force main; that is shared between two residential buildings.

Single Family Residence

A single, residential building intended to house a single family/family unit.

Section B. General Conditions

- Duty to Comply

The Permittee must comply with all conditions of this permit, including construction of any new private sewer lines. Any permit noncompliance constitutes a violation and is grounds for enforcement action; for permit termination, revocation and reissuance, or modification; or denial of a permit renewal application. The issuance of this permit shall not exempt the Permittee from complying with any and all statutes, rules, regulations, or ordinances that may be imposed by the Division any other Federal, State, or Local government agencies which have jurisdiction or obtaining other permits which may be required by the Division or any other Federal, State, of Local government agencies.  [G.S.143-215.1(b); 15A NCAC 02T.0110; 15A NCAC 02T.0111]

- Duty to Mitigate

In the event that the wastewater collection facilities fail to perform satisfactorily, including the creation of nuisance conditions, the Permittee shall take immediate corrective action, including those as may be required by this Division, such as the construction of additional or replacement facilities.  [15A NCAC 02T .0110; 15A NCAC 02T .0108(b)]

3.   Permit Transferability

This permit shall not be transferable.  In the event there is a desire for the wastewater collection facilities to change ownership, or there is a name change of the Permittee, a formal permit request shall be submitted to the Division accompanied by documentation from the parties involved, and other supporting materials as may be appropriate.  The approval of this request shall be considered on its merits and may or may not be approved.  [15A NCAC 02T.0104; G.S. 143-215.1(d3)

4.  Operation and Maintenance

The sewer system shall be effectively maintained and operated at all times to prevent discharge to land or surface waters, and to prevent any contravention of groundwater standards or surface water standards. [15A NCAC 02T.0403]

- Property Rights

The issuance of this permit does not convey any property rights in either real or personal property, or any exclusive privileges, nor does it authorize any injury to private property or any invasion of personal rights, nor any infringement of Federal, State or local laws or regulations.

- Duty to Provide Information

The Permittee shall furnish to the Permit Issuing Authority, within a reasonable time, any information which the Permit Issuing Authority may request to determine whether cause exists for modifying, revoking and reissuing, or terminating this permit or to determine compliance with this permit. The Permittee shall also furnish to the Permit Issuing Authority upon request, copies of records required by this permit. [15A NCAC 02T.0111]

- Expiration of Permit

The Permittee is hereby authorized to operate the shared sewer line as covered by this permit, in perpetuity, for as long as the general permit is effective. [15A NCAC 02T.0111]

- Signatory Requirements

All applications, reports, or information submitted to the Permit Issuing Authority shall be signed and certified [15A NCAC 02T.0106]

- All permit applications shall be signed as follows:

  - For a corporation: by a responsible corporate officer. For the purpose of this Section, a responsible corporate officer means: (a) a president, secretary, treasurer or vice president of the corporation in charge of a principal business function, or any other person who performs similar policy or decision making functions for the corporation, or (b) the manager of one or more manufacturing, production, or operating facilities, provided, the manager is authorized to make management decisions which govern the operation of the regulated facility including having the explicit or implicit duty of making major capital investment recommendations, and initiating and directing other comprehensive measures to assure long term environmental compliance with environmental laws and regulations; the manager can ensure that the necessary systems are established or actions taken to gather complete and accurate information for permit application requirements; and where authority to sign documents has been assigned or delegated to the manager in accordance with corporate procedures.

  - For a partnership or sole proprietorship: by a general partner or the proprietor, respectively; or

  - For a municipality, State, Federal, or other public agency: by either a principal executive officer or ranking elected official.

  - For a primary residence as defined in Section II(A) above, by all owners of that property, or by an owner documented as being the designated signature authority by all other property owners.

- Permit Actions

This permit may be modified, revoked and reissued, or terminated for cause. The filing of a request by the Permittee for a permit modification, revocation and reissuance, or termination, or a notification of planned changes or anticipated noncompliance does not stay any permit condition [15A NCAC 02T.0111]

- Permit Modification, Revocation and Reissuance, or Termination

The issuance of this permit does not prohibit the permit issuing authority from reopening and modifying the permit, revoking and reissuing the permit, or terminating the permit as allowed by the laws, rules, and regulations contained in Title 15A of the North Carolina Administrative Code, Subchapter 02T; and North Carolina General Statute 143.215.1 et. al.

PART III.

OTHER REQUIREMENTS

Section A. Facility Closure Requirements

The Permittee must notify the Division prior to the closure of any sewer system covered by this permit. The Division may require specific measures during deactivation of the system to prevent adverse impacts to waters of the State. This permit cannot be rescinded while any activities requiring this permit continue at the permitted facility.