## 2017 Summary
|  |  | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [13 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [16 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [10 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [12 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project
2017-09-21 |  |  | PACKAGE DATA (Pages 1 - 6) | [12 empty] | 2017-09-21 | ANNUAL ENERGY USAGE (x1,000,000 BTU/YEAR) (Pages 7 -12) | [15 empty] | 2017-09-21 | ANNUAL ENERGY USAGE ($/YEAR) (pages 13-18) | [9 empty] | 2017-09-21 | ANNUAL INDOOR WATER USAGE (GALLONS/YEAR) (Pages 19 - 24) | [11 empty] | 2017-09-21 | Construction and Design Costs and Fees (Pages 25 - 30)
Project | # | LEED | Agency or Institution | County | Energy Contact | State ID# | Energy Model Report Date | Energy Model Report Phase | Construction Contract Award Date | Actual or Projected Acceptance Date | Principal Occupancy / Category / Use(s) | Number of Beds | Size (GSF from building code summary) | GSF/Bed | Floors (from building code summary) | Project | ASHRAE Standard | Climate Zone (3, 4 or 5) | Baseline | Site EUI Baseline (kBtu/Sq Ft/yr) | Proposed | Site EUI Proposed (kBtu/Sq Ft/yr) | Proposed improvement in energy efficiency | Proposed Energy Savings | Date of Meter Data | Metered Energy Usage | Site EUI Metered (kBtu/Sq Ft/yr) | ASHRAE 100 Bldg Type No. | ASHRAE 100 25th(kBtu/Sq Ft/yr) | Metered improvement in energy efficiency | Meets SB 668 (from unclean data) | Metered Energy Savings (from unclean data) | Project | Baseline | ECI (Energy Cost Intensity) Baseline ($/Yr/Sq Ft) | Proposed | ECI Proposed ($/Yr/Sq Ft) | Proposed % improvement in energy cost | Proposed Savings in Energy Cost | Metered | ECI Metered ($/Yr/Sq Ft) | Metered % improvement in energy cost | Metered Savings in Energy Cost | Project | Baseline (Gallons/Year) | Baseline (Gal/Res/Yr) | WUI (Water Use Intensity) Baseline (Gal/Sq Ft/Yr) | Proposed (Gallons/Year) | Proposed (Gal/Res/Yr) | WUI Proposed (Gal/Sq Ft/Yr) | Proposed % improvement in water usage | Proposed Savings (Gallons/Year) | Metered (Gallons/Year) | Metered (Gal/Res/Yr) | WUI Metered (Gal/Sq Ft/Yr) | Metered improvement in water usage | Project | Cost Estimate or Original Amount Construction Contract | Construction Cost/SF | Designer's Baseline (non-SB668) Estimate | Original Total Design Fee (without amendments) | Additional Design Fees (LEED or SB 668 - included in OTDF) | Advance Planning Contract Item G | Commissioning Fee | Simple Payback in Years (Net Savings Required /HB 628) | Modeler | ASHRAE Standard
Cone Residence Hall Renovation | 1 | Gold | ASU | Watauga | Patrick Richardson richardsonpj@appstate.edu | 08-07272-01A | 2009-01-20 | CD | 2009-09-14 | 2010-06-23 | Residence Hall | 278 | 58803 | 211.5216 | 8 | Cone Residence Hall Renovation | 90.1-2004 | 5 | 3467 | 58.9596 | 1993 | 33.8928 | 42.52% | 1474 | 2017-08-11 | 4518.4712 | 76.8408 | Dorm | 78 | -30.33% |  | -1051.4712 | Cone Residence Hall Renovation | 81830 | 1.3916 | 43969 | 0.74773 | 46.27% | 37861 | 104124.1382 | 1.7707 | -27.24% | -22294.1382 | Cone Residence Hall Renovation | 2000376 | 7195.5971 | 34.0183 | 1397116 | 5025.5971 | 23.7593 | 30.16% | 603260 | 1664987.0001 | 5989.1619 | 28.3147 | 16.77% | Cone Residence Hall Renovation | 7585100 | 128.9917 | 5965486 | 883660 | 0 |  | 62500 | 44.4287 | SKA | 90.1-2004
Prospector Hall Renovation Phase II | 2 | None | UNCC | Mecklenburg | Tom Sparks | 06-07223-01A | 2013-03-15 | LEED submit. | 2010-08-12 | 2011-05-30 | Food Service/Dining | NA | 22705 |  | 2 | Prospector Hall Renovation Phase II | 90.1-2004 | 3 | 2082 | 91.6979 | 1477 | 65.0518 | 29.06% | 605 |  |  | 0 | Fast food | 277 |  |  |  | Prospector Hall Renovation Phase II | 30538 | 1.345 | 21943 | 0.96644 | 28.15% | 8595 |  | 0 |  |  | Prospector Hall Renovation Phase II | 48654 | NA | 2.1429 | 27934 | NA | 1.2303 | 42.59% | 20720 |  |  |  |  | Prospector Hall Renovation Phase II | 4029200 | 177.4587 | 3944812 | 295500 | 0 |  | 65100 | 17.3924 | M&C | 90.1-2004
Miltimore Residence Hall | 3 | Silver | UNCC | Mecklenburg | Tom Sparks | 05-06656-01A | 2009-06-10 | CD | 2009-07-22 | 2011-07-19 | Residence Hall | 431 | 173086 | 401.5916 | 5 | Miltimore Residence Hall | 90.1-2004 | 3 | 38283 | 221.1791 | 32882 | 189.9749 | 14.11% | 5401 |  |  | 0 | Dorm | 47 |  |  |  | Miltimore Residence Hall | 478677 | 2.7655 | 411144 | 2.3754 | 14.11% | 67533 |  | 0 |  |  | Miltimore Residence Hall | 6961135 | 16151.1253 | 40.2178 | 5188175 | 12037.529 | 29.9746 | 25.47% | 1772960 |  |  |  |  | Miltimore Residence Hall | 32995620 | 190.6314 | 33000165 | 2747550 | 58700 |  | 177000 | 3.4228 | CN | 90.1-2004
Nursing Building | 4 | Silver | NCCU | Durham | Ondin Mihalcescu <o.mihalcescu@nccu.edu> | 07-07203-02A | 2009-12-22 | CD | 2010-01-25 | 2011-08-05 | Offices/Classrooms | NA | 69610 |  | 5 | Nursing Building | 90.1-2004 | 4 | 6048.6 | 86.8927 | 2596.2 | 37.2964 | 57.08% | 3452.4 | 2017-08-25 | 2987.7913 | 42.9219 | Col/Univ | 72 | 50.6% |  | 3060.8087 | Nursing Building | 148249 | 2.1297 | 61035 | 0.87681 | 58.83% | 87214 | 54160.73 | 0.77806 | 63.47% | 94088.27 | Nursing Building | 871150 | NA | 12.5147 | 601563 | NA | 8.6419 | 30.95% | 269587 | 1549564.28 | NA | 22.2607 | -77.88% | Nursing Building | 16198787 | 232.7078 | 16003466 | 1795875 | 82875 | 16175 | 265694 | 6.4217 | RMF | 90.1-2004
Chidley North Residence Hall | 5 | Gold | NCCU | Durham | Ondin Mihalcescu <o.mihalcescu@nccu.edu> | 05-07248-02A | 2012-03-23 | LEED submit. | 2009-08-03 | 2011-08-10 | Residence Hall | 528 | 133570 | 252.9735 | 4 | Chidley North Residence Hall | 90.1-2004 | 4 | 16482 | 123.396 | 10635 | 79.6212 | 35.48% | 5847 | 2017-08-25 | 7098.8763 | 53.1472 | Dorm | 58 | 56.93% |  | 9383.1237 | Chidley North Residence Hall | 292778 | 2.1919 | 198708 | 1.4877 | 32.13% | 94070 | 115109.27 | 0.86179 | 60.68% | 177668.73 | Chidley North Residence Hall | 6283057 | 11899.7292 | 47.0394 | 4373148 | 8282.4773 | 32.7405 | 30.4% | 1909909 | 7548082.96 | 14295.6117 | 56.5103 | -20.13% | Chidley North Residence Hall | 23276802 | 174.2667 | 21956196 | 2186050 | 173500 |  | 104934 | 16.9984 | SWA | 90.1-2004
The Loudermilk Center for Excellence | 6 | None | UNC-CH | Orange | O'Hara, Jessica K <johara@email.unc.edu> | 09-07851-01A | 2010-05-17 | CD | No Contract (Found. Proj) | 2011-08-18 | Offices/Locker rooms/Club | NA | 170189 |  | 6 | The Loudermilk Center for Excellence | 90.1-2004 | 4 | 10672 | 62.7068 | 7143 | 41.971 | 33.07% | 3529 | 2017-08-21 | 25243.1031 | 148.3239 | Col/Univ | 72 | -136.5% |  | -14571.1031 | The Loudermilk Center for Excellence | 116674 | 0.68556 | 78320 | 0.46019 | 32.87% | 38354 | 261560.66 | 1.5369 | -124.2% | -144886.66 | The Loudermilk Center for Excellence | 1518337 | NA | 8.9215 | 991995 | NA | 5.8288 | 34.67% | 526342 | 1916000 | NA | 11.2581 | -26.19% | The Loudermilk Center for Excellence | (Foundation Project) |  |  | (Foundation Project) |  | (Foundation Project) | (Foundation Project) |  | MSWG | 90.1-2004
Davis Event Center | 7 | In Progress | DoAG&CS | Buncombe | Debbie Robertson <debbie.robertson@ncagr.gov> | 08-07347-02A | 2010-05-06 | CD | 2010-10-26 | 2011-08-19 | Assembly | NA | 67904 |  | 1 | Davis Arena Add & Renov | 90.1-2004 | 4 | 2961 | 43.6057 | 1736 | 25.5655 | 41.37% | 1225 | 2017-08-28 | 3116.2126 | 45.8914 | Other Assembly | 31 | -5.242% |  | -155.2126 | Davis Arena Add & Renov | 72840 | 1.0727 | 42637 | 0.6279 | 41.46% | 30203 | 64193.28 | 0.94535 | 11.87% | 8646.72 | Davis Arena Add & Renov | 109500 | NA | 1.6126 | 87313 | NA | 1.2858 | 20.26% | 22187 | 555802.5437 | NA | 8.1851 | -407.6% | Davis Arena Add & Renov | 5507600 | 81.1086 | 5351000 | 484000 | 15000 |  | 43640 | 7.1264 |  | 90.1-2004
Student Health Center Add and Renovation | 8 | Gold | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 07-07345-02A | 2010-03-12 | CD | 2010-06-10 | 2011-09-12 | Offices/Clinics | NA | 24663 |  | 2 | Student Health Center Addition and Renovation | 90.1-2004 | 4 | 2746 | 111.3409 | 1547 | 62.7255 | 43.66% | 1199 | 2017-09-08 | 12306.9475 | 186.108 | Clinic | 48 | -348.2% |  | -9560.9475 | Student Health Center Addition and Renovation | 69316 | 2.8105 | 38688 | 1.5687 | 44.19% | 30628 | 184274.9052 | 2.7866 | -165.8% | -114958.9052 | Student Health Center Addition and Renovation | 320198 | NA | 12.9829 | 230958 | NA | 9.3646 | 27.87% | 89240 | 436185.5647 | NA | 17.6858 | -36.22% | Student Health Center Addition and Renovation | 6017900 | 244.0052 | 5778782 | 634045 | 65575 |  | 106438 | 13.4234 | RMF | 90.1-2004
Gilchrist Education and Psychology Complex | 9 | In Progress | ECSU | Pasquotank | Elizabeth Linney | 07-07081-02A | 2010-01-11 | CD | 2010-01-05 | 2012-02-01 | Office/Classroom | NA | 48112 |  | 3 | Gilchrist Education and Psychology Complex | 90.1-2004 | 3 | 3078 | 63.9757 | 1625 | 33.7754 | 47.21% | 1453 | 2017-08-31 | 2936.6237 | 61.0372 | Col/Univ | 62 | 4.593% |  | 141.3763 | Gilchrist Education and Psychology Complex | 64655 | 1.3438 | 34128 | 0.70934 | 47.22% | 30527 | 80983.54 | 1.6832 | -25.25% | -16328.54 | Gilchrist Education and Psychology Complex | 1506938 | NA | 31.3215 | 1056525 | NA | 21.9597 | 29.89% | 450413 | 72889.68 | NA | 1.515 | 95.16% | Gilchrist Education and Psychology Complex | 14394127 | 299.1796 | 13822099 | 1654600 | 35000 |  | 57000 | 21.7522 | AEI | 90.1-2004
EPIC | 10 | None | UNCC | Mecklenburg | Tom Sparks | 07-07078-02A | 2009-08-21 | CD | 2009-09-30 | 2012-04-12 | Offices/Labs/Classrooms | NA | 200164 |  | 4 | EPIC | 90.1-2004 | 3 | 30494.5 | 152.3476 | 18910.6 | 94.4755 | 37.99% | 11583.9 |  |  |  | Lab | 175 |  |  |  | EPIC | 284103 | 1.4194 | 165774 | 0.82819 | 41.65% | 118329 |  | 0 |  |  | EPIC | 3172838 | NA | 15.8512 | 1985718 | NA | 9.9205 | 37.42% | 1187120 |  |  |  |  | EPIC | 61500000 | 307.2481 | 51725930 | 5792635 | 221084 |  | 404815 | 87.8903 | M&L | 90.1-2004
SENC Ag Center | 11 | None | DoAG&CS | Robeson | Debbie Robertson <debbie.robertson@ncagr.gov> | 08-07348-02A | 2010-06-28 | DD | 2011-03-22 | 2012-04-12 | Equine & Livestock | NA | 55605 |  | 1 | SENC Ag Center | 90.1-2004 | 3 | 1743 | 31.3461 | 749 | 13.47 | 57.03% | 994 | 2017-08-28 | 1208.8461 | 21.7399 | Other Assembly | 28 | 30.65% | ü | 534.1539 | SENC Ag Center | 42886 | 0.77126 | 28420 | 0.51111 | 33.73% | 14466 | 35398.51 | 0.63661 | 17.46% | 7487.49 | SENC Ag Center | 243256 | NA | 4.3747 | 171756 | NA | 3.0889 | 29.39% | 71500 | 70990 | NA | 1.2767 | 70.82% | SENC Ag Center | 4072395 | 73.2379 | 3919435 | 363080 | 0 |  | 11870 | 11.3943 |  | 90.1-2004
NC Veterans Home - Black Mountain | 12 | None | NCM&VA | Buncombe | diane.norris@doa.nc.gov | 06-06924-05A | 2009-12-22 | CD | 2010-05-24 | 2012-05-31 | Nursing Home /Assisted Living | 100 | 108770 |  | 1 | NC Veterans Home - Black Mountain | 90.1-2004 | 4 | 8495 | 78.1006 | 5163 | 47.4671 | 39.22% | 3332 | 2017-08-02 | 9257.7494 | 85.1131 | Nursing home | 91 | -8.979% |  | -762.7494 | NC Veterans Home - Black Mountain | 213106 | 1.9592 | 120807 | 1.1107 | 43.31% | 92299 | 168501.81 | 1.5492 | 20.93% | 44604.19 | NC Veterans Home - Black Mountain | 4378540 | 43785.4 | 40.255 | 3400982 | 34009.82 | 31.2676 | 22.33% | 977558 | 3837240 | 38372.4 | 35.2785 | 12.36% | NC Veterans Home - Black Mountain | 16135100 | 148.3415 | 15834228 | 1250000 | 0 |  | 96941 | 4.31 | MCBH | 90.1-2004
Russell Classroom Building | 13 | None | Pitt CC | Pitt | Don Heisey 'dheisey@email.pittcc.edu' | 08-07329-02A | 2010-04-12 | CD | 2010-12-06 | 2012-06-27 | Office/Classroom | NA | 50434 |  | 2 | Russell Classroom Building | 90.1-2004 | 3 | 3018 | 59.8406 | 1900 | 37.673 | 37.04% | 1118 |  |  |  | Col/Univ | 62 |  |  |  | Russell Classroom Building | 91928 | 1.8227 | 56777 | 1.1258 | 38.24% | 35151 |  |  |  |  | Russell Classroom Building | 1217970 | NA | 24.1498 | 954495 | NA | 18.9256 | 21.63% | 263475 |  |  |  |  | Russell Classroom Building | 7393799 | 146.6035 | 7243287 | 943138 | 52150 |  | 42310 | 6.9691 | PDC | 90.1-2004
Bailey Residence Hall Renovation | 14 | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Bailey Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2017-08-31 | 3114.5656 | 101.3361 | Dorm | 58 | 23.21% | ü | 941.4344 | Bailey Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 19080.0081 | 0.62079 | 67.99% | 40527.9919 | Bailey Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 700500 | 8145.3488 | 22.7916 | -113.6% | Bailey Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Coit Residence Hall Renovation | 15 | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Coit Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2017-08-31 | 3716.9568 | 120.9356 | Dorm | 58 | 8.359% |  | 339.0432 | Coit Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 18272.5856 | 0.59452 | 69.35% | 41335.4144 | Coit Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 1385500 | 16110.4651 | 45.0789 | -322.6% | Coit Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Cotten Residence Hall Renovation | 16 | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Cotten Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2017-08-31 | 3420.6582 | 111.2952 | Dorm | 58 | 15.66% | ü | 635.3418 | Cotten Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 18684.2126 | 0.60791 | 68.65% | 40923.7874 | Cotten Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 906500 | 10540.6977 | 29.4941 | -176.5% | Cotten Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Gray Residence Hall Renovation | 17 | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Gray Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2017-08-31 | 3180.9487 | 103.496 | Dorm | 58 | 21.57% | ü | 875.0513 | Gray Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 18985.146 | 0.6177 | 68.15% | 40622.854 | Gray Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 887400 | 10318.6047 | 28.8726 | -170.6% | Gray Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Hinshaw Residence Hall Renovation | 18 | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Hinshaw Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2017-08-31 | 3204.3862 | 104.2585 | Dorm | 58 | 21% | ü | 851.6138 | Hinshaw Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 21548.2678 | 0.7011 | 63.85% | 38059.7322 | Hinshaw Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 794900 | 9243.0233 | 25.863 | -142.4% | Hinshaw Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Jamison Residence Hall Renovation | 19 | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Jamison Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2017-08-31 | 3061.4836 | 99.609 | Dorm | 58 | 24.52% | ü | 994.5164 | Jamison Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 17245.887 | 0.56112 | 71.07% | 42362.113 | Jamison Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 929100 | 10803.4884 | 30.2294 | -183.4% | Jamison Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Shaw Residence Hall Renovation | 20 | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 118 | 54847 | 464.8051 | 4 | Shaw Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 73.9512 | 3076 | 56.0833 | 24.16% | 980 | 2017-08-31 | 7790.518 | 142.0409 | Dorm | 58 | -92.07% |  | -3734.518 | Shaw Residence Hall Renovation | 59608 | 1.0868 | 46163 | 0.84167 | 22.56% | 13445 | 32425.1868 | 0.59119 | 45.6% | 27182.8132 | Shaw Residence Hall Renovation | 327880 | 2778.6441 | 5.9781 | 209536 | 1775.7288 | 3.8204 | 36.09% | 118344 | 1269600 | 10759.322 | 23.148 | -287.2% | Shaw Residence Hall Renovation | 6196641.1429 | 112.9805 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Harrill Residence Hall Renovation | 21 | Gold | WCU | Jackson | David King <dbking@email.wcu.edu> | 03-07291-02A | 2011-01-07 | CD | 2011-08-03 | 2012-08-02 | Residence Hall | 350 | 71505 | 204.3 | 10 | Harrill Residence Hall Renovation | 90.1-2004 | 4 | 5122 | 71.6314 | 3189 | 44.5983 | 37.74% | 1933 | 2017-07-28 | 2782.2742 | 38.9102 | Dorm | 58 | 45.68% | ü | 2339.7258 | Harrill Residence Hall Renovation | 114129 | 1.5961 | 82978 | 1.1605 | 27.29% | 31151 | 50031.581 | 0.69969 | 56.16% | 64097.419 | Harrill Residence Hall Renovation | 2675470 | 7644.2 | 37.4165 | 1801347 | 5146.7057 | 25.1919 | 32.67% | 874123 | 1534907.3992 | 4385.4497 | 21.4657 | 42.63% | Harrill Residence Hall Renovation | 13435000 | 187.889 | 11750000 | 998800 | 0 |  | 153235 | 59.0105 | Optima | 90.1-2004
Renaissance Residence Hall | 22 | Silver | FSU | Cumberland | Jon Parsons | 11-08594-01A | 2011-09-12 | CD | No Contract (Found. Proj) | 2012-08-07 | Residence Hall | 340 | 85000 | 250 | 3 | Renaissance Residence Hall | 90.1-2004 | 3 | 5499 | 64.6941 | 3624 | 42.6353 | 34.1% | 1875 |  |  |  | Dorm | 47 |  |  |  | Renaissance Residence Hall | 174915 | 2.0578 | 88110 | 1.0366 | 49.63% | 86805 |  |  |  |  | Renaissance Residence Hall | 2636463 | 7754.3029 | 31.0172 | 1734140 | 5100.4118 | 20.4016 | 34.22% | 902323 |  |  |  |  | Renaissance Residence Hall | (Foundation Project) |  |  | (Foundation Project) | (Foundation Project) |  | (Foundation Project) |  | Optima | 90.1-2004
Health Science Building | 23 | Silver | UNCP | Robeson | Terry W. Divine <terry.divine@uncp.edu> | 06-06859-02A | 2009-11-17 | CD | 2010-07-16 | 2012-08-07 | Office/Classroom | NA | 87000 |  | 3 | Health Science Building | 90.1-2004 | 3 | 7163 | 82.3333 | 4954 | 56.9425 | 30.84% | 2209 |  |  |  | Col/Univ | 62 |  |  |  | Health Science Building | 98379 | 1.1308 | 65154 | 0.7489 | 33.77% | 33225 |  | 0 |  |  | Health Science Building | 2606625 | NA | 29.9612 | 1672375 | NA | 19.2227 | 35.84% | 934250 |  |  |  |  | Health Science Building | 14834300 | 170.5092 | 14419316 | 2004260 | 47460 |  | 0 | 13.9186 | MSWG | 90.1-2004
Overlook Residence Hall | 24 | None | UNCA | Buncombe | 'dtodd@unca.edu' | 09-07924-02B | 2011-02-28 | CD | 2011-07-14 | 2012-08-08 | Residence Hall | 300 | 91370 | 304.5667 | 6 | Overlook Residence Hall | 90.1-2004 | 4 | 5737 | 62.7887 | 3460 | 37.868 | 39.69% | 2277 | 2017-09-06 | 5240.7468 | 57.3574 | Dorm | 58 | 8.65% |  | 496.2532 | Overlook Residence Hall | 89281 | 0.97714 | 63609 | 0.69617 | 28.75% | 25672 | 118312 | 1.2949 | -32.52% | -29031 | Overlook Residence Hall | 2888310 | 9627.7 | 31.6111 | 1728304 | 5761.0133 | 18.9154 | 40.16% | 1160006 | 2955348 | 9851.16 | 32.3448 | -2.321% | Overlook Residence Hall | 16467600 | 180.2298 | 14927082 | 1685000 | 0 |  | 85000 | 63.3187 | MSWG | 90.1-2004
Viking Tower Residence Hall | 25 | None | ECSU | Pasquotank | Elizabeth Linney | 00-06539-03A | 2010-09-03 | CD | 2011-01-25 | 2012-08-17 | Residence Hall | 210 | 53896 | 256.6476 | 3 | Viking Tower Residence Hall | 90.1-2004 | 3 | 9118 | 169.1777 | 6399 | 118.7287 | 29.82% | 2719 | 2017-08-31 | 2032.2026 | 37.706 | Dorm | 47 | 77.71% | ü | 7085.7974 | Viking Tower Residence Hall | 217417 | 4.034 | 145256 | 2.6951 | 33.19% | 72161 | 54681.08 | 1.0146 | 74.85% | 162735.92 | Viking Tower Residence Hall | 1193460 | 5683.1429 | 22.1438 | 938250 | 4467.8571 | 17.4085 | 21.38% | 255210 | 3873798 | 18446.6571 | 71.8754 | -224.6% | Viking Tower Residence Hall | 12474496 | 231.455 | 12222788 | 1199950 | 40000 |  | 85000 | 5.2204 | RMF | 90.1-2004
Teaching Laboratory Building | 26 | Silver | UNCW | New Hanover | Steve Sharpe | 07-07129-02A | 2010-08-06 | CD | 2011-01-21 | 2012-08-24 | Office/Classroom/Labs | NA | 85000 |  | 3 | Teaching Laboratory Building | 90.1-2004 | 3 | 7739 | 91.0471 | 4808 | 56.5647 | 37.87% | 2931 | 2017-09-05 | 3473.9289 | 40.8698 | Col/Univ | 62 | 55.11% |  | 4265.0711 | Teaching Laboratory Building | 142633 | 1.678 | 90792 | 1.0681 | 36.35% | 51841 | 142076.03 | 1.6715 | 0.3905% | 556.97 | Teaching Laboratory Building | 751030 | NA | 8.8356 | 507514 | NA | 5.9708 | 32.42% | 243516 | 671290 | NA | 7.8975 | 10.62% | Teaching Laboratory Building | 15645200 | 184.0612 | 15440699 | 2615450 | 156820 |  | 0 | 6.9698 | RMF | 90.1-2004
Rhoades Hall Renovation | 27 | None | UNCA | Buncombe | 'dtodd@unca.edu' | 06-06994-02B | 2009-05-11 | CD | 2010-04-26 | 2012-09-10 | Classroom/Lab/Offices | NA | 40434 |  | 3 and 4 | Rhoades Hall Renovation | 90.1-2004 | 4 | 3231 | 79.908 | 1185 | 29.307 | 63.32% | 2046 | 2017-09-06 | 1172.9798 | 29.0097 | Col/Univ | 72 | 63.7% | ü | 2058.0202 | Rhoades Hall Renovation | 98370 | 2.4329 | 43014 | 1.0638 | 56.27% | 55356 | 26480 | 0.65489 | 73.08% | 71890 | Rhoades Hall Renovation | 957500 | NA | 23.6806 | 655500 | NA | 16.2116 | 31.54% | 302000 | 1053932 | NA | 26.0655 | -10.07% | Rhoades Hall Renovation | 5996300 | 148.2985 | 5834600 | 859165 | 76500 |  | 0 |  | ESE | 90.1-2004
Ledyard E. Ross Hall | 28 | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 07-07054-02A | 2010-04-16 | CD | 2010-07-01 | 2012-09-14 | Offices/Classrooms/Labs | NA | 157410 |  | 5 | Ledyard E. Ross Hall | 90.1-2004 | 3 | 43253 | 274.7792 | 27864 | 177.0154 | 35.58% | 15389 | 2017-07-28 | 27796.5314 | 176.5868 | Lab | 175 | 35.74% | ü | 15456.4686 | Ledyard E. Ross Hall | 420065 | 2.6686 | 302543 | 1.922 | 27.98% | 117522 | 287706.7244 | 1.8278 | 31.51% | 132358.2756 | Ledyard E. Ross Hall | 1373584 | NA | 8.7262 | 905161 | NA | 5.7503 | 34.1% | 468423 | No data |  |  |  | Ledyard E. Ross Hall | 33176057 | 210.7621 | 32922547 | 5394860 | 100000 |  | 346397 |  | BR+A | 90.1-2004
Lena Sue Beam Renovation | 29 | None | Gaston College | Gaston | Cynthia McCrory | 07-07395-02A | 2011-03-03 | CD | 2011-07-29 | 2012-10-03 | Office/Classroom | NA | 31418 |  | 2 | Lena Sue Beam Renovation | 90.1-2004 | 4 | 1732 | 55.1276 | 1161 | 36.9533 | 32.97% | 571 | 2017-08-24 | 3405.8745 | 108.4052 | Col/Univ | 72 | -96.64% |  | -1673.8745 | Lena Sue Beam Renovation | 36406 | 1.1588 | 25403 | 0.80855 | 30.22% | 11003 | 45654.9847 | 1.4531 | -25.41% | -9248.9847 | Lena Sue Beam Renovation | 689715 | NA | 21.9529 | 403299 | NA | 12.8366 | 41.53% | 286416 | 106323 | NA | 3.3841 | 84.58% | Lena Sue Beam Renovation | 4701800 | 149.6531 | 4657494 | 474000 | 0 |  | 56984 | 9.2057 | M&L | 90.1-2004
Hunt Library | 30 | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 07-07171-02A | 2010-08-06 | CD-2 | 2009-08-25 | 2012-10-18 | Library/Offices/Lecture Hall/Meeting | NA | 253028 |  | 4 | Hunt Library | 90.1-2004 | 4 | 15191 | 60.0368 | 10342 | 40.8729 | 31.92% | 4849 | 2017-09-08 | 27639.7157 | 109.2358 | Library | 67 | -81.95% |  | -12448.7157 | Hunt Library | 268448 | 1.0609 | 184680 | 0.72988 | 31.2% | 83768 | 536268.4599 | 2.1194 | -99.77% | -267820.4599 | Hunt Library | 4536750 | NA | 17.9298 | 2948625 | NA | 11.6534 | 35.01% | 1588125 | 673200 | NA | 2.6606 | 85.16% | Hunt Library | 81306000 | 321.332 | 80844228 | 9829956 | 200000 |  | 605005 |  | AEI | 90.1-2004
NC Veterans Home - Kinston | 31 | None | NCM&VA | Lenoir | diane.norris@doa.nc.gov | 06-06924-05A | 2009-12-22 | CD | 2010-05-24 | 2012-10-31 | Nursing Home /Assisted Living | 100 | 108770 |  | 1 | NC Veterans Home - Kinston | 90.1-2004 | 3 | 8495 | 78.1006 | 5163 | 47.4671 | 39.22% | 3332 | 2017-08-02 | 10516.7398 | 96.6879 | Nursing home | 83 | -23.8% |  | -2021.7398 | NC Veterans Home - Kinston | 213106 | 1.9592 | 120807 | 1.1107 | 43.31% | 92299 | 221773.42 | 2.0389 | -4.067% | -8667.42 | NC Veterans Home - Kinston | 4378540 | 43785.4 | 40.255 | 3400982 | 34009.82 | 31.2676 | 22.33% | 977558 | 3289700 | 32897 | 30.2446 | 24.87% | NC Veterans Home - Kinston | 12903000 | 118.6265 | 12602128 | 1077600 | 0 |  | 107804 | 4.4277 | MCBH | 90.1-2004
Judy W. Rose Football Center | 32 | Certified | UNCC | Mecklenburg | Tom Sparks | 08-07833-02A | 2010-12-10 | CD | 2011-03-29 | 2012-10-31 | Locker rooms/Offices | NA | 43290 |  | 2 | Judy W. Rose Football Center | 90.1-2004 | 3 | 8320 | 192.1922 | 5184 | 119.7505 | 37.69% | 3136 |  |  |  | Col/Univ | 62 |  |  |  | Judy W. Rose Football Center | 65175 | 1.5055 | 44151 | 1.0199 | 32.26% | 21024 |  | 0 |  |  | Judy W. Rose Football Center | 1349491 | NA | 31.1733 | 1113354 | NA | 25.7185 | 17.5% | 236137 |  |  |  |  | Judy W. Rose Football Center | 12987000 | 300 | 12521456 | 3448472 | 45000 |  | 99500 |  | M&C | 90.1-2004
Continuing Education and Industrial Center | 33 | Gold | Randolph CC | Randolph | Cindi Goodwin | 07-07252-03A | 2010-12-08 | CD | 2011-10-14 | 2012-11-27 | Office/Classroom/Labs | NA | 43967 |  | 1 | Continuing Education and Industrial Center | 90.1-2004 | 3 | 2940 | 66.8683 | 1839 | 41.8268 | 37.45% | 1101 | 2017-08-10 | 3781.1489 | 85.9997 | Col/Univ | 72 | -28.61% |  | -841.1489 | Continuing Education and Industrial Center | 67485 | 1.5349 | 43675 | 0.99336 | 35.28% | 23810 | 78610.3 | 1.7879 | -16.49% | -11125.3 | Continuing Education and Industrial Center | 544858 | NA | 12.3924 | 436998 | NA | 9.9392 | 19.8% | 107860 | 9260.24 | NA | 0.21062 | 98.3% | Continuing Education and Industrial Center | 6361300 | 144.6835 | 6060565 | 363200 | 0 |  | 49800 | 14.7222 | PDC | 90.1-2004
Plemmons Student Union Addition | 34 | Gold | ASU | Watauga | Patrick Richardson richardsonpj@appstate.edu | 08-07327-02A | 2010-08-19 | CD | 2010-06-08 | 2012-12-18 | Office/Classroom/Conference | NA | 50560 |  | 4 | Plemmons Student Union | 90.1-2004 | 5 | 2185 | 43.216 | 1346 | 26.6218 | 38.4% | 839 | 2017-08-11 | 10127.2588 | 200.3018 | Rest/Cafet | 179 | -363.5% |  | -7942.2588 | Plemmons Student Union | 53367 | 1.0555 | 32912 | 0.65095 | 38.33% | 20455 | 232099.1884 | 4.5906 | -334.9% | -178732.1884 | Plemmons Student Union | 1220706 | NA | 24.1437 | 950466 | NA | 18.7988 | 22.14% | 270240 | 3193821.0004 | NA | 63.1689 | -161.6% | Plemmons Student Union | 15232506 | 301.2758 | 14629006 | 985521.6 | 90950 |  | 71248.14 | 37.4333 | SKA | 90.1-2004
Summit Living Learning Center | 35 | Silver | ASU | Watauga | Patrick Richardson richardsonpj@appstate.edu | 08-07327-02A | 2010-08-19 | CD | 2010-06-08 | 2012-12-18 | Residence Hall / Office Classrooms | 333 | 128585 | 386.1411 | 11 and 3 | Summit Living Learning Center | 90.1-2004 | 5 | 6323 | 49.1737 | 3660 | 28.4637 | 42.12% | 2663 | 2017-08-11 | 7860.4999 | 61.1308 | Col/Univ | 78 | -24.32% |  | -1537.4999 | Summit Living Learning Center | 153208 | 1.1915 | 89024 | 0.69234 | 41.89% | 64184 | 192429.9734 | 1.4965 | -25.6% | -39221.9734 | Summit Living Learning Center | 3388865 | 10176.7718 | 26.3551 | 1928009 | 5789.8168 | 14.994 | 43.11% | 1460856 | 2507192.0001 | 7529.1051 | 19.4983 | 26.02% | Summit Living Learning Center | 40691217 | 316.4538 | 39309739 | 2664558.4 | 94925 |  | 192633.86 | 26.0039 | SKA | 90.1-2004
MARBIONC | 36 | Certified | UNCW | New Hanover | Steve Sharpe | 07-07853-02A | 2010-06-03 | DD | 2011-08-01 | 2013-01-29 | Labs/Offices | NA | 68000 |  | 2 | MARBIONIC | 90.1-2004 | 3 | 31233 | 459.3088 | 19781 | 290.8971 | 36.67% | 11452 | 2017-09-05 | 22187.4634 | 326.2862 | Lab | 175 | 28.96% | ü | 9045.5366 | MARBIONIC | 425995 | 6.2646 | 301801 | 4.4383 | 29.15% | 124194 | 182400.86 | 2.6824 | 57.18% | 243594.14 | MARBIONIC | 5139169 | NA | 75.576 | 4083469 | NA | 60.051 | 20.54% | 1055700 | No meter |  |  |  | MARBIONIC | 24371201 | 358.4 | 19975000 | 2804957 | 110280 |  | 294243 | 38.655 | CRB/AEI | 90.1-2004
NC State Bar HQ | 37 | Silver | DOA | Wake | Joe Cerone <jcerone@ncbar.gov> | 09-07858-01A | 2011-05-31 | CD | 2011-11-28 | 2013-04-25 | Office/Courtroom | NA | 54565 |  | 4 | NC State Bar HQ | 90.1-2004 | 4 | 1689 | 30.9539 | 1116 | 20.4527 | 33.93% | 573 | 2017-07-24 | 3056.0002 | 56.0066 | Prof Office | 46 | -80.94% |  | -1367.0002 | NC State Bar HQ | 45238 | 0.82907 | 29457 | 0.53985 | 34.88% | 15781 | 76948.42 | 1.4102 | -70.1% | -31710.42 | NC State Bar HQ | 175310 | NA | 3.2129 | 116629 | NA | 2.1374 | 33.47% | 58681 | 172040 | NA | 3.1529 | 1.865% | NC State Bar HQ | 12962700 | 237.5644 | 12687413 | 1125000 | 6000 |  | 56200 | 21.3857 | CJMW | 90.1-2004
Science and Technology Building | 38 | Silver | FSU | Cumberland | Jon Parsons | 06-06971-02A | 2011-01-11 | Final | 2011-06-27 | 2013-05-21 | Office/Classrooms/Labs | NA | 65861 |  | 4 | Science and Technology Building | 90.1-2004 | 3 | 13356 | 202.7907 | 9641 | 146.3841 | 27.82% | 3715 |  |  |  | Col/Univ | 62 |  |  |  | Science and Technology Building | 151889 | 2.3062 | 100888 | 1.5318 | 33.58% | 51001 |  |  |  |  | Science and Technology Building | 2163492 | NA | 32.8494 | 1785946 | NA | 27.1169 | 17.45% | 377546 |  |  |  |  | Science and Technology Building | 17028032 | 258.545 | 16327000 | 1576000 | 135000 |  | 290182 | 22.0822 | M&C | 90.1-2004
Student Recreation Facility Addition | 39 | Certified | UNCW | New Hanover | Steve Sharpe | 07-07060-03A | 2010-06-02 | CD | 2011-04-25 | 2013-05-22 | Gym/pool/fitness/courts/locker-room | NA | 93917 |  | 2 | Student Recreation Facility Addition | 90.1-2004 | 3 | 22917 | 244.0133 | 15931 | 169.6285 | 30.48% | 6986 | 2017-09-05 | 6097.327 | 64.9225 | Recreat | 26 | 73.39% |  | 16819.673 | Student Recreation Facility Addition | 351452 | 3.7422 | 248190 | 2.6427 | 29.38% | 103262 | 182400.86 | 1.9421 | 48.1% | 169051.14 | Student Recreation Facility Addition | 810220 | NA | 8.627 | 634243 | NA | 6.7532 | 21.72% | 175977 | 975900 | NA | 10.3911 | -20.45% | Student Recreation Facility Addition | 21478228 | 228.6937 | 20845432 | 2510110 | 215000 |  | 126000 | 9.4303 | SWA | 90.1-2004
Reaves Student Activities Center | 40 | Gold | WSSU | Forsyth | Dick Kabis | 06-07181-01A | 2010-10-25 | CD | 2011-05-17 | 2013-06-24 | Gym/Food Service/ | NA | 91513 |  | 3 | Reaves Student Activities Center | 90.1-2004 | 4 | 7587 | 82.9063 | 5004 | 54.6808 | 34.05% | 2583 | 2017-08-28 | 9845.5802 | 107.5867 | Col/Univ | 72 | -29.77% |  | -2258.5802 | Reaves Student Activities Center | 105529 | 1.1532 | 66125 | 0.72257 | 37.34% | 39404 | 190473.1364 | 2.0814 | -80.49% | -84944.1364 | Reaves Student Activities Center | 1434603 | NA | 15.6765 | 990985 | NA | 10.8289 | 30.92% | 443618 | 2529212.4 | NA | 27.6377 | -76.3% | Reaves Student Activities Center | 25393206 | 277.482 | 25315267 | 2408119 | 177240 |  | 287625 | 13.7754 | Sud | 90.1-2004
Creative Arts Building | 41 | Platinum | Haywood CC | Haywood | Josh Best rjbest@haywood.edu | 07-07315-03A | 2009-11-02 | DD-2 | 2010-10-28 | 2013-06-30 | Art studios, classrooms, offices | NA | 40722 |  | 3 | Creative Arts Building | 90.1-2004 | 4 | 3603 | 88.478 | 1672 | 41.0589 | 53.59% | 1931 | 2017-08-09 | 1783.0509 | 43.7859 | Col/Univ | 72 | 50.51% | ü | 1819.9491 | Creative Arts Building | 65069 | 1.5979 | 19856 | 0.4876 | 69.48% | 45213 | 32993.8461 | 0.81022 | 49.29% | 32075.1539 | Creative Arts Building | 977508 | NA | 24.0044 | 255213 | NA | 6.2672 | 73.89% | 722295 | 155086.4326 | NA | 3.8084 | 84.13% | Creative Arts Building | 8385286 | 205.9154 | 6402774 | 851000 | 50000 |  | 80000 | 46.7236 | Elm | 90.1-2004
Belk Residence Hall | 42 | None | UNCC | Mecklenburg | Tom Sparks | 10-08450-02A | 2011-12-22 | CD-2 | 2012-01-17 | 2013-07-09 | Residence Hall | 400 | 164377 | 410.9425 | 5 | Belk Residence Hall | 90.1-2004 | 3 | 10765 | 65.4897 | 7239 | 44.039 | 32.75% | 3526 |  |  |  | Dorm | 47 |  |  |  | Belk Residence Hall | 149183 | 0.90757 | 97190 | 0.59126 | 34.85% | 51993 |  | 0 |  |  | Belk Residence Hall | 2719308 | 6798.27 | 16.5431 | 1869230 | 4673.075 | 11.3716 | 31.26% | 850078 |  |  |  |  | Belk Residence Hall | 30027284 | 182.6733 | 30027284 | 2167790 | 126000 |  | 186000 |  |  | 90.1-2004
Cherry Building Renovation | 43 | None | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 10-08698-02A | 2011-11-17 | CD | 2012-07-12 | 2013-07-15 | Office/Classroom | NA | 22482 |  | 2.5 | Cherry Building Renovation | 90.1-2004 | 4 | 1449 | 64.4516 | 1017 | 45.2362 | 29.81% | 432 | 2017-09-08 | 1696.688 | 75.4687 | High School | 52 | -17.09% |  | -247.688 | Cherry Building Renovation | 27666 | 1.2306 | 21821 | 0.9706 | 21.13% | 5845 | 33512.9697 | 1.4907 | -21.13% | -5846.9697 | Cherry Building Renovation | 166500 | NA | 7.4059 | 120425 | NA | 5.3565 | 27.67% | 46075 | 83476.8 | NA | 3.7131 | 49.86% | Cherry Building Renovation | 2670270 | 118.7737 | 2645494 | 292501 | 0 |  | 0 |  | SWA | 90.1-2004
Hunt Residence Hall | 44 | None | UNCC | Mecklenburg | Tom Sparks | 10-08610-03A | 2012-02-24 | CD | 2012-01-17 | 2013-07-29 | Residence Hall | 436 | 144175 | 330.6766 | 5 | Hunt Residence Hall | 90.1-2004 | 3 | 11671 | 80.9502 | 6976 | 48.3856 | 40.23% | 4695 |  |  |  | Dorm | 47 |  |  |  | Hunt Residence Hall | 141674 | 0.98265 | 87499 | 0.60689 | 38.24% | 54175 |  | 0 |  |  | Hunt Residence Hall | 1100206 | 2523.4083 | 7.631 | 860579 | 1973.805 | 5.969 | 21.78% | 239627 |  |  |  |  | Hunt Residence Hall | 24655367 | 171.01 | 22816693 | 2078598 | 0 |  | 297680 |  | CN | 90.1-2004
Wolf Ridge at Centennial Bldg 6 - Lakeview Hall | 45 | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-08-01 | Residence Hall | 151 | 67202 | 445.0464 | 6 | Wolf Ridge at Centennial Bldg 6 | 90.1-2004 | 4 | 4126 | 61.397 | 2853 | 42.4541 | 30.85% | 1273 | 2017-09-08 | 7129.9572 | 106.0974 | Dorm | 58 | -72.81% |  | -3003.9572 | Wolf Ridge at Centennial Bldg 6 | 76622 | 1.1402 | 51093 | 0.76029 | 33.32% | 25529 | 107563.3747 | 1.6006 | -40.38% | -30941.3747 | Wolf Ridge at Centennial Bldg 6 | 1630661 | 10799.0795 | 24.2651 | 1029702 | 6819.2185 | 15.3225 | 36.85% | 600959 | 599148 | 3967.8675 | 8.9156 | 63.26% | Wolf Ridge at Centennial Bldg 6 | 14207759 | 211.4187 | 11410139.74 | 995826.9923 | 0 |  | 47050.2499 |  | Dewberry | 90.1-2004
Wolf Ridge at Centennial Bldg 1 - Tower Hall | 46 | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-08-01 | Residence Hall & Dining Hall | 251 | 154726 | 616.4382 | 6 | Wolf Ridge at Centennial Bldg 1 - Tower Hall | 90.1-2004 | 4 | 12056 | 77.9184 | 8300 | 53.6432 | 31.15% | 3756 | 2017-09-08 | 15964.6064 | 103.1799 | Dorm | 58 | -32.42% |  | -3908.6064 | Wolf Ridge at Centennial Bldg 1 - Tower Hall | 220350 | 1.4241 | 143383 | 0.92669 | 34.93% | 76967 | 271838.9537 | 1.7569 | -23.37% | -51488.9537 | Wolf Ridge at Centennial Bldg 1 - Tower Hall | 5618485 | 22384.4024 | 36.3125 | 4483837 | 17863.8924 | 28.9792 | 20.19% | 1134648 | 2965820 | 11816.0159 | 19.1682 | 47.21% | Wolf Ridge at Centennial Bldg 1 | 32712171 | 211.42 | 26270927.62 | 2292793.7742 | 0 |  | 108328.5759 |  | Dewberry | 90.1-2004
Spartan Village 1 - Lee Residence Hall | 47 | Silver | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 243 | 116224 | 478.2881 | 5 | Spartan Village 1 - Lee Residence Hall | 90.1-2004 | 4 | 5889 | 50.6694 | 4141 | 35.6295 | 29.68% | 1748 | 2017-08-31 | 3256.6266 | 28.0203 | Apart | 46 | 44.7% | ü | 2632.3734 | Spartan Village 1 - Lee Residence Hall | 127318 | 1.0955 | 80286 | 0.69079 | 36.94% | 47032 | 67928.96 | 0.58447 | 46.65% | 59389.04 | Spartan Village 1 - Lee Residence Hall | 2900134 | 11934.7078 | 24.953 | 2258696 | 9295.0453 | 19.434 | 22.12% | 641438 | 1613548.164 | 6640.1159 | 13.8831 | 44.36% | Spartan Village 1 - Lee Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Spartan Village 3 - Haywood Residence Hall | 48 | Silver | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 130 | 56295 | 433.0385 | 5 | Spartan Village 3 - Haywood Residence Hall | 90.1-2004 | 4 | 5889 | 104.6096 | 4141 | 73.5589 | 29.68% | 1748 | 2017-08-31 | 2168.4506 | 38.5194 | Apart | 46 | 63.18% | ü | 3720.5494 | Spartan Village 3 - Haywood Residence Hall | 127318 | 2.2616 | 80286 | 1.4262 | 36.94% | 47032 | 45823.79 | 0.81399 | 64.01% | 81494.21 | Spartan Village 3 - Haywood Residence Hall | 1736095 | 13354.5769 | 30.8392 | 1384588 | 10650.6769 | 24.5952 | 20.25% | 351507 | 2223210.544 | 17101.6196 | 39.4921 | -28.06% | Spartan Village 3 - Haywood Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Spartan Village 4 - Union Residence Hall | 49 | Silver | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 209 | 89104 | 426.3349 | 5 | Spartan Village 4 - Union Residence Hall | 90.1-2004 | 4 | 5889 | 66.0913 | 4141 | 46.4738 | 29.68% | 1748 | 2017-08-31 | 2660.4062 | 29.8573 | Apart | 46 | 54.82% | ü | 3228.5938 | Spartan Village 4 - Union Residence Hall | 127318 | 1.4289 | 80286 | 0.90104 | 36.94% | 47032 | 54137.49 | 0.60758 | 57.48% | 73180.51 | Spartan Village 4 - Union Residence Hall | 2627757 | 12573 | 29.4909 | 2069683 | 9902.7895 | 23.2277 | 21.24% | 558074 | 2450140.416 | 11723.1599 | 27.4975 | 6.759% | Spartan Village 4 - Union Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Martin-Schexnider Residence Hall | 50 | Certified | WSSU | Forsyth | Dick Kabis | 11-09099-02A | 2012-07-18 | CD | No Contract (Privately Funded) | 2013-08-13 | Residence Hall | 227 | 55626 | 245.0485 | 5 | Martin-Schexnider Residence Hall | 90.1-2004 | 4 | 6193 | 111.3328 | 4672 | 83.9895 | 24.56% | 1521 | 2017-08-28 | 7804.1191 | 140.2962 | Dorm | 58 | -26.02% |  | -1611.1191 | Martin-Schexnider Residence Hall | 87219 | 1.568 | 53012 | 0.95301 | 39.22% | 34207 | 96312.6864 | 1.7314 | -10.43% | -9093.6864 | Martin-Schexnider Residence Hall | 2317437 | 10208.9736 | 41.661 | 1848705 | 8144.0749 | 33.2345 | 20.23% | 468732 | 5569940.86 | 24537.1844 | 100.132 | -140.3% | Martin-Schexnider Residence Hall | 10000000 | 179.772 | 9516280 | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | M&C | 90.1-2004
Union Station | 51 | Silver | Cape Fear CC | New Hanover | David Kanoy | 07-07399-03A | 2010-05-05 | CD | 2010-11-10 | 2013-08-22 | Office/Classroom/Auditorium | NA | 233900 |  | 6 | Union Station | 90.1-2004 | 3 | 12463 | 53.2835 | 8391 | 35.8743 | 32.67% | 4072 | 2017-07-19 | 26434.0887 | 113.0145 | Col/Univ | 62 | -112.1% |  | -13971.0887 | Union Station | 407210 | 1.741 | 294497 | 1.2591 | 27.68% | 112713 | 352676.93 | 1.5078 | 13.39% | 54533.07 | Union Station | 1939781 | NA | 8.2932 | 1222056 | NA | 5.2247 | 37% | 717725 | 3911000 | NA | 16.7208 | -101.6% | Union Station | 38141300 | 163.0667 | 37627193 | 6113085 | 339250 |  | 237711 | 9.6801 | Cheatham | 90.1-2004
Smith-Williams Center | 52 | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 08-07305-01F | 2012-03-01 | CD | 2012-05-01 | 2013-08-27 | Gym/Office | NA | 49170 |  | 2 | Smith-Williams Center | 90.1-2004 | 3 | 2396 | 48.7289 | 1518 | 30.8725 | 36.64% | 878 | 2017-07-28 | 3443.563 | 70.0338 | Recreat | 26 | -43.72% |  | -1047.563 | Smith-Williams Center | 48568 | 0.98776 | 38507 | 0.78314 | 20.72% | 10061 | 37685.115 | 0.76642 | 22.41% | 10882.885 | Smith-Williams Center | 347984 | NA | 7.0772 | 227682 | NA | 4.6305 | 34.57% | 120302 |  |  |  |  | Smith-Williams Center | 13828376 | 281.236 | 12357348 | 736500 |  |  | 128800 |  | Edi | 90.1-2004
Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 53 | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-12-05 | Residence Hall | 223 | 84876 | 380.6099 | 6 | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 90.1-2004 | 4 | 5653 | 66.603 | 3934 | 46.35 | 30.41% | 1719 | 2017-09-08 | 7127.5925 | 83.9765 | Dorm | 58 | -26.09% |  | -1474.5925 | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 102040 | 1.2022 | 70049 | 0.82531 | 31.35% | 31991 | 112774.3118 | 1.3287 | -10.52% | -10734.3118 | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 2385879 | 10699.009 | 28.1102 | 1498371 | 6719.1525 | 17.6536 | 37.2% | 887508 | 893112 | 4004.9865 | 10.5226 | 62.57% | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 17944484 | 211.42 | 14286216 | 1257727.6242 | 0 |  | 59424.3774 |  | Dewberrry | 90.1-2004
Spartan Village 2 - Highland Residence Hall | 54 | Silver | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2014-01-09 | Residence Hall | 231 | 110627 | 478.9048 | 5 | Spartan Village 2 - Highland Residence Hall | 90.1-2004 | 4 | 5889 | 53.2329 | 4141 | 37.4321 | 29.68% | 1748 | 2017-08-31 | 3353.1612 | 30.3105 | Apart | 46 | 43.06% | ü | 2535.8388 | Spartan Village 2 - Highland Residence Hall | 127318 | 1.1509 | 80286 | 0.72574 | 36.94% | 47032 | 72196.21 | 0.65261 | 43.29% | 55121.79 | Spartan Village 2 - Highland Residence Hall | 2916495 | 12625.5195 | 26.3633 | 2297942 | 9947.8009 | 20.772 | 21.21% | 618553 | 1823002.724 | 7891.7867 | 16.4788 | 37.49% | Spartan Village 2 - Highland Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
PORTAL | 55 | None | UNCC | Mecklenburg | Tom Sparks | 08-07560-03A | 2011-02-03 | CD | 2012-04-09 | 2014-01-28 | Office | NA | 102914 |  | 4 | PORTAL | 90.1-2004 | 3 | 7934 | 77.0935 | 5513 | 53.569 | 30.51% | 2421 |  |  |  | Col/Univ | 62 |  |  |  | PORTAL | 142246 | 1.3822 | 98494 | 0.95705 | 30.76% | 43752 |  | 0 |  |  | PORTAL | 776459 | NA | 7.5447 | 565009 | NA | 5.4901 | 27.23% | 211450 |  |  |  |  | PORTAL | 25748184 | 250.1913 | 24736184 | 2215000 | 0 |  | 240424 | 28.6255 | M&C | 90.1-2004
Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 56 | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-02-06 | Residence Hall | 219 | 88512 | 404.1644 | 6 | Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 90.1-2004 | 4 | 5069 | 57.2691 | 3543 | 40.0285 | 30.1% | 1526 | 2017-09-08 | 5330.8613 | 60.2276 | Dorm | 58 | -5.166% |  | -261.8613 | Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 91459 | 1.0333 | 63494 | 0.71735 | 30.58% | 27965 | 89674.0415 | 1.0131 | 1.952% | 1784.9585 | Wolf Ridge at Centennial Bldg 3 | 2343922 | 10702.8402 | 26.4814 | 1472334 | 6722.9863 | 16.6343 | 37.19% | 871588 | 805596 | 3678.5205 | 9.1015 | 65.63% | Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 18713207 | 211.42 |  | 1311607.3739 | none noted |  | 61970.0562 |  | Dewberry | 90.1-2004
Hill Hall Renovation | 57 | Gold | WSSU | Forsyth | Dick Kabis | 11-08884-03A | 2012-09-27 | CD | 2012-12-13 | 2014-03-25 | Offices | NA | 37898 |  | 3 | Hill Hall Renovation - Student Success Center | 90.1-2007 | 4 | 2638 | 69.6079 | 1913 | 50.4776 | 27.48% | 725 | 2017-08-28 | 6143.5831 | 162.1084 | Col/Univ | 72 | -132.9% |  | -3505.5831 | Hill Hall Renovation - Student Success Center | 41267 | 1.0889 | 25579 | 0.67494 | 38.02% | 15688 | 82853.878 | 2.1862 | -100.8% | -41586.878 | Hill Hall Renovation - Student Success Center | 2719308 | NA | 71.7533 | 1869230 | NA | 49.3227 | 31.26% | 850078 | 159772.8 | NA | 4.2159 | 94.12% | Hill Hall Renovation - Student Success Center | 10890470 | 287.3627 | 10890470 | 1125000 | 100000 |  | 90000 | 12.1112 | CN | 90.1-2007
Wolf Ridge at Centennial Bldg 5 - Grove Hall | 58 | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-04-09 | Residence Hall | 144 | 62645 | 435.0347 | 6 | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 90.1-2004 | 4 | 3959 | 63.1974 | 2756 | 43.9939 | 30.39% | 1203 | 2017-09-08 | 4371.5196 | 69.7824 | Dorm | 58 | -10.42% |  | -412.5196 | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 73439 | 1.1723 | 49084 | 0.78353 | 33.16% | 24355 | 72614.296 | 1.1591 | 1.123% | 824.704 | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 1557237 | 10814.1458 | 24.8581 | 984137 | 6834.2847 | 15.7097 | 36.8% | 573100 | 569228 | 3952.9722 | 9.0866 | 63.45% | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 13244406 | 211.42 |  | 928299.4841 | none noted |  | 43859.7498 |  | Dewberry | 90.1-2004
Wolf Ridge at Centennial Bldg 4 - Valley Hall | 59 | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-05-09 | Residence Hall | 219 | 83460 | 381.0959 | 6 | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 90.1-2004 | 4 | 5197 | 62.2694 | 3476 | 41.6487 | 33.12% | 1721 | 2017-09-08 | 4094.2685 | 49.0567 | Dorm | 58 | 21.22% | ü | 1102.7315 | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 96219 | 1.1529 | 61768 | 0.74009 | 35.8% | 34451 | 68640.49 | 0.82244 | 28.66% | 27578.51 | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 2343922 | 10702.8402 | 28.0844 | 1472334 | 6722.9863 | 17.6412 | 37.19% | 871588 | 190740 | 870.9589 | 2.2854 | 91.86% | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 17645113 | 211.42 |  | 1236744.7513 | none noted |  | 58432.9909 |  | Dewberry | 90.1-2004
Aviation Center III Building | 60 | In Progress | GTCC | Guilford | mjohnson@gtcc.edu | 08-07309-02A | 2012-03-09 | CD | 2012-09-17 | 2014-07-21 | Office/Classroom | NA | 42087 |  | 4 | Aviation Center III Building | 90.1-2004 | 4 | 2425 | 57.6187 | 1699 | 40.3688 | 29.94% | 726 |  |  |  | Col/Univ | 72 |  |  |  | Aviation Center III Building | 68705 | 1.6325 | 55378 | 1.3158 | 19.4% | 13327 |  | 0 |  |  | Aviation Center III Building | 1135125 | NA | 26.9709 | 550575 | NA | 13.0818 | 51.5% | 584550 |  |  |  |  | Aviation Center III Building | 6535600 | 155.2879 |  | 686500 | 20000 |  | 149249 |  | SWA | 90.1-2004
Martin Residence Hall | 61 | None | UNCC | Mecklenburg | Tom Sparks | 11-09156-02A | 2012-12-19 | CD | 2013-04-05 | 2014-08-13 | Residence Hall | 408 | 174657 | 428.0809 | 6 | Martin Residence Hall | 90.1-2007 | 3 | 21396 | 122.503 | 13060 | 74.7751 | 38.96% | 8336 |  |  |  | Dorm | 47 |  |  |  | Martin Residence Hall | 306609 | 1.7555 | 210750 | 1.2067 | 31.26% | 95859 |  | 0 |  |  | Martin Residence Hall | 4970906 | 12183.5931 | 28.461 | 3510140 | 8603.2843 | 20.0973 | 29.39% | 1460766 |  |  |  |  | Martin Residence Hall | 35192772 | 201.4965 | 29686104 | 2733245 | 15000 |  | 175000 | 59.4276 |  | 90.1-2007
New Library Building | 62 | None | UNCSA | Forsyth | boydc@uncsa.edu | 06-06981-05A | 2012-07-27 | FI | 2013-01-18 | 2014-09-09 | Library/Offices | NA | 73432 |  | 4 | New Library Building | 90.1-2004 | 4 | 6402 | 87.1827 | 4631 | 63.0651 | 27.66% | 1771 |  |  |  | Fol/Univ | 67 |  |  |  | New Library Building | 90245 | 1.229 | 62106 | 0.84576 | 31.18% | 28139 |  |  |  |  | New Library Building | 706800 | NA | 9.6252 | 478350 | NA | 6.5142 | 32.32% | 228450 |  |  |  |  | New Library Building | 15433000 | 210.1672 | 17328709 | 1833332 | 0 |  | 108825 | -63.502 |  | 90.1-2004
Student Health Center | 63 | In Progress | NCA&T | Guilford | barlow@ncat.edu | 08-08109-02A | 2011-12-21 | DD | 2013-04-08 | 2014-10-29 | Offices/Clinics | NA | 27548 |  | 2 | Student Health Center | 90.1-2004 | 4 | 1911 | 69.3698 | 1336 | 48.4972 | 30.09% | 575 | 2017-08-02 | 2146.1854 | 77.9071 | Med Off Diag | 32 | -12.31% |  | -235.1854 | Student Health Center | 50033 | 1.8162 | 33648 | 1.2214 | 32.75% | 16385 | 28335.53 | 1.0286 | 43.37% | 21697.47 | Student Health Center | 154588 | NA | 5.6116 | 101825 | NA | 3.6963 | 34.13% | 52763 | 115940 | NA | 4.2087 | 25% | Student Health Center | 7444000 | 270.2193 | 7251633 | 785500 | 92000 |  | 51400 | 20.4923 | RMF | 90.1-2004
Campus Police Facility | 64 | Silver | UNCG | Guilford | Douglas Cato | 10-08905-03A | 2012-03-29 | CD | 2012-11-01 | 2014-11-12 | Offices | NA | 25877 |  | 2 | Campus Police Facility | 90.1-2004 | 4 | 2330 | 90.0413 | 1242 | 47.9963 | 46.7% | 1088 | 2017-08-31 | 2478.4919 | 95.7797 | Police Sta | 71 | -6.373% |  | -148.4919 | Campus Police Facility | 44281 | 1.7112 | 29471 | 1.1389 | 33.45% | 14810 | 40423.6136 | 1.5621 | 8.711% | 3857.3864 | Campus Police Facility | 617945 | NA | 23.8801 | 478128 | NA | 18.4769 | 22.63% | 139817 | 92010.396 | NA | 3.5557 | 85.11% | Campus Police Facility | 6143700 | 237.4193 |  | 854040 | 43000 |  | 81680 |  | SWA | 90.1-2004
South Village Dining Facility | 65 | None | UNCC | Mecklenburg | Tom Sparks | 10-08633-03A | 2013-04-17 | FI | 2012-10-04 | 2014-11-21 | Food Service/Dining | NA | 56146 |  | 2 | South Village Dining Facility | 90.1-2004 | 3 | 12578 | 224.0231 | 7334 | 130.6237 | 41.69% | 5244 |  |  | 0 | Rest/café | 150 |  |  |  | South Village Dining Facility | 163454 | 2.9112 | 113314 | 2.0182 | 30.68% | 50140 |  | 0 |  |  | South Village Dining Facility | 546557 | NA | 9.7346 | 435029 | NA | 7.7482 | 20.41% | 111528 |  |  |  |  | South Village Dining Facility | 26618418.39 | 474.0929 | 25649718.39 | 1918410 | 78000 |  | 182024 | 24.5059 | M&C | 90.1-2004
Moran Commons Dining Hall Renovation | 66 | None | UNCG | Guilford | Douglas Cato | 08-07382-02A | 2011-04-28 | CD | 2011-06-06 | 2015-02-05 | Food Service/Dining | NA | 111160 |  | 2 | Moran Commons Dining Hall Renovation | 90.1-2004 | 4 | 18584 | 167.1824 | 12522 | 112.6484 | 32.62% | 6062 | 2017-08-31 | 59609.8727 | 536.2529 | Rest/café | 166 | -220.8% |  | -41025.8727 | Moran Commons Dining Hall Renovation | 269366 | 2.4232 | 187898 | 1.6903 | 30.24% | 81468 | 213510.5072 | 1.9207 | 20.74% | 55855.4928 | Dining Hall Renovation | 6216053 | NA | 55.9199 | 3532573 | NA | 31.7792 | 43.17% | 2683480 | 4751999.12 | NA | 42.7492 | 23.55% | Dining Hall Renovation | 28459035 | 256.0187 |  | 2837884 | 60000 |  | 283540 |  | M&L | 90.1-2004
Center for Design Innovation | 67 | In Progress | WSSU | Forsyth | Dick Kabis | 06-06646-03A | 2013-05-03 | FI | 2012-04-12 | 2015-03-03 | Offices, classrooms, labs | NA | 23982 |  | 3 | Center for Design Innovation | 90.1-2007 | 4 | 4288 | 178.8008 | 2361 | 98.4488 | 44.94% | 1927 | 2017-08-28 | 1387.6644 | 57.8627 | Col/Univ | 72 | 67.64% | ü | 2900.3356 | Center for Design Innovation | 106582 | 4.4442 | 65369 | 2.7258 | 38.67% | 41213 | 37178.36 | 1.5503 | 65.12% | 69403.64 | Center for Design Innovation | 67775 | NA | 2.8261 | 44733 | NA | 1.8653 | 34% | 23042 | 6754.44 | NA | 0.28165 | 90.03% | Center for Design Innovation | 8727727 | 363.9282 | 6497174 | 700000 | 50000 |  | 80300 | 57.2842 | RMF | 90.1-2007
Jones Student Center - Renovation and Addition | 68 | In Progress | FSU | Cumberland | Jon Parsons | 11-09090-03A | 2013-06-28 | FI | 2013-06-10 | 2015-03-06 | Assembly/Dining/Offices | NA | 82961 |  | 2 | Jones Student Center - Renovation and Addition | 90.1-2007 | 3 | 14304 | 172.4184 | 11048 | 133.171 | 22.76% | 3256 |  |  |  | Rest/café | 150 |  |  |  | Jones Student Center - Renovation and Addition | 215110 | 2.5929 | 143121 | 1.7252 | 33.47% | 71989 |  |  |  |  | Jones Student Center - Renovation and Addition | 4017684 | NA | 48.4286 | 3910346 | NA | 47.1348 | 2.672% | 107338 |  |  |  |  | Jones Student Center - Renovation and Addition | 17090447 | 206.0058 | 16915711 | 1536300 | 0 |  | 207560 | 5.3105 | Optima | 90.1-2007
Campus Police Facility | 69 | None | UNCSA | Forsyth | boydc@uncsa.edu | 08-07845-03A | 2012-04-05 | CD | 2013-05-30 | 2015-03-12 | Offices | NA | 9023 |  | 2 | Campus Police Facility | 90.1-2004 | 4 | 1171 | 129.7795 | 689 | 76.3604 | 41.16% | 482 |  |  |  | Police Sta | 71 |  |  |  | Campus Police Facility | 18288 | 2.0268 | 12209 | 1.3531 | 33.24% | 6079 |  |  |  |  | Campus Police Facility | 289717 | NA | 32.1087 | 195438 | NA | 21.66 | 32.54% | 94279 |  |  |  |  | Campus Police Facility | 3059704 | 339.1005 |  | 292220 | none noted |  | 68561 |  | SWA | 90.1-2004
Central Storage Facility | 70 | None | UNCSA | Forsyth | boydc@uncsa.edu | 08-07844-03A | 2012-05-23 | CD | 2013-05-01 | 2015-03-25 | Warehouse/Storage | NA | 43637 |  | 2 | Central Storage Facility | 90.1-2007 | 4 | 1506 | 34.512 | 754 | 17.2789 | 49.93% | 752 | [8 empty] | Central Storage Facility | 27891 | 0.63916 | 14976 | 0.34319 | 46.31% | 12915 |  |  |  |  | Central Storage Facility | 128138 | NA | 2.9365 | 58898 | NA | 1.3497 | 54.04% | 69240 |  |  |  |  | Central Storage Facility | 5260039 | 120.5408 | 1412707 | 596884 | 0 |  | 65343 |  |  | 90.1-2007
Talley Student Center Renovation and Addition | 71 | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07847-03A | 2012-02-22 | CD | 2011-02-21 | 2015-05-07 | Offices/Theater/Conference/Food Service/Book Store | NA | 294736 |  | 5 | Talley Student Center Renovation and Addition | 90.1-2004 | 4 | 41725 | 141.5674 | 27808 | 94.3488 | 33.35% | 13917 | 2017-09-08 | 43327.5023 | 147.0044 | Rest/café | 166 | -3.841% |  | -1602.5023 | Talley Student Center Renovation and Addition | 940212 | 3.19 | 699461 | 2.3732 | 25.61% | 240751 | 766115.7711 | 2.5993 | 18.52% | 174096.2289 | Talley Student Center Renovation and Addition | 1088442 | NA | 3.6929 | 869385 | NA | 2.9497 | 20.13% | 219057 | 5175987.5536 | NA | 17.5614 | -375.5% | Talley Student Center Renovation and Addition | 89115690 | 302.3577 |  | 9079497 | 178918 |  | 526000 |  | SWA | 90.1-2004
CE and BLET | 72 | None | Nash CC | Nash | Adrienne Covington <ascovington197@nashcc.edu> | 09-07972-03A | 2012-11-19 | CD | 2013-11-05 | 2015-06-05 | Offices/Classrooms/Gym/Training | NA | 79295 |  | 2 | CE and BLET | 90.1-2007 | 4 | 5941 | 74.9228 | 4122 | 51.9831 | 30.62% | 1819 | 2017-09-06 | 5346.1845 | 67.4215 | Col/Univ | 62 | 10.01% |  | 594.8155 | CE and BLET | 95436 | 1.2036 | 64835 | 0.81764 | 32.06% | 30601 | 125375.38 | 1.5811 | -31.37% | -29939.38 | CE and BLET | 2356578 | NA | 29.7191 | 1527392 | NA | 19.2621 | 35.19% | 829186 | 440572 | NA | 5.5561 | 81.3% | CE and BLET | 11310270 | 142.6353 |  | 861998 | None Noted |  | 52620 |  | SWA | 90.1-2007
Film School Production Design Facility | 73 | None | UNCSA | Forsyth | boydc@uncsa.edu | 08-08115-03A | 2012-03-30 | CD | 2013-04-11 | 2015-06-16 | Various | NA | 29936 |  | 2 | Film School Production Design Facility | 90.1-2004 | 4 | 8887 | 296.8666 | 5860 | 195.7509 | 34.06% | 3027 |  |  |  | Lab | 194 |  |  |  | Film School Production Design Facility | 148285 | 4.9534 | 99346 | 3.3186 | 33% | 48939 |  |  |  |  | Film School Production Design Facility | 55005 | NA | 1.8374 | 40257 | NA | 1.3448 | 26.81% | 14748 |  |  |  |  | Film School Production Design Facility | 7820696 | 261.2472 |  | 827850 | none noted |  | 47760 |  |  | 90.1-2004
Holshouser Residence Hall Renovation | 74 | None | UNCC | Mecklenburg | Tom Sparks | 12-09461-02A | 2014-03-17 | FD | 2014-02-06 | 2015-07-28 | Residence Hall | 400 | 99713 | 249.2825 | 12 | Holshouser Residence Hall Renovation | 90.1-2007 | 3 | 12163 | 121.9801 | 9302 | 93.2877 | 23.52% | 2861 |  |  |  | Dorm | 47 |  |  |  | Holshouser Residence Hall Renovation | 169440 | 1.6993 | 126115 | 1.2648 | 25.57% | 43325 |  |  |  |  | Holshouser Residence Hall Renovation | 3663471 | 9158.6775 | 36.7402 | 2570153 | 6425.3825 | 25.7755 | 29.84% | 1093318 |  |  |  |  | Holshouser Residence Hall Renovation | 15172636 | 152.1631 | 14796933 | 1251550 | 11880 |  | 95000 | 11.1387 | CN | 90.1-2007 | 375703
Laurel Residence Hall | 75 | None | UNCC | Mecklenburg | Tom Sparks | 12-09496-03A | 2013-10-11 | DD-2 | 2014-01-02 | 2015-07-29 | Residence Hall | 412 | 143986 | 349.4806 | 6 | Laurel Residence Hall | 90.1-2007 | 3 | 7705 | 53.5121 | 5840 | 40.5595 | 24.21% | 1865 |  |  |  | Dorm | 47 |  |  |  | Laurel Residence Hall | 102473 | 0.71169 | 56750 | 0.39414 | 44.62% | 45723 |  |  |  |  | Laurel Residence Hall | 4730466 | 11481.7136 | 32.8537 | 2731460 | 6629.7573 | 18.9703 | 42.26% | 1999006 |  |  |  |  | Laurel Residence Hall | 28765101 | 199.7771 | 26520850 | 2312090 | 13945 |  | 200000 | 53.7628 | Optima | 90.1-2007
Belk Residence Hall Renovation | 76 | Silver | ASU | Watauga | Patrick Richardson richardsonpj@appstate.edu | 10-09113-02A | 2014-02-21 | FD-2 | 2014-05-05 | 2015-07-30 | Residence Hall | 176 | 32839 | 186.5852 | 5 | Belk Residence Hall Renovation | 90.1-2007 | 5 | 3330 | 101.4038 | 2305 | 70.1909 | 30.78% | 1025 | 2017-08-11 | 2402.9625 | 73.174 | Dorm | 47 | 27.84% | ü | 927.0375 | Belk Residence Hall Renovation | 87029 | 2.6502 | 60703 | 1.8485 | 30.25% | 26326 | 55948.56 | 1.7037 | 35.71% | 31080.44 | Belk Residence Hall Renovation | 1209992 | 6874.9545 | 36.8462 | 755467 | 4292.4261 | 23.0052 | 37.56% | 454525 | 1156000 | 6568.1818 | 35.202 | 4.462% | Belk Residence Hall Renovation | 7222300 | 219.9306 | 6512106 | 806400 | 50600 |  | 19450 | 29.6378 | CN | 90.1-2007
Osprey Hall Renovation | 77 | None | UNCW | New Hanover | Steve Sharpe | 07-09975-02A | 2014-07-02 | CD | 2014-05-30 | 2015-08-03 | Offices, classrooms, labs | NA | 43554 |  | 2 | Osprey Hall Renovation | 90.1-2010 | 3 | 5934.9 | 136.2653 | 5079 | 116.6139 | 14.42% | 855.9 | 2017-09-05 | 7499.9559 | 172.199 | Col/Univ | 62 | -26.37% |  | -1565.0559 | Osprey Hall Renovation | 110349 | 2.5336 | 91957 | 2.1113 | 16.67% | 18392 | 83804.64 | 1.9242 | 24.05% | 26544.36 | Osprey Hall Renovation | 1075870 | NA | 24.702 | 760602 | NA | 17.4634 | 29.3% | 315268 | 161728 | NA | 3.7133 | 84.97% | Osprey Hall Renovation | 9820475 | 225.4781 | 5837018 | 859450 |  | 17250 | 0 | 217.5243 | MCBH | 90.1-2010
Gateway Residence Hall (Belk Replacement) | 78 | In Progress | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-09246-03A | 2013-10-03 | CD | 2013-05-22 | 2015-08-10 | Residence Hall | 720 | 208077 | 288.9958 | 5 | Gateway Residence Hall (Belk Replacement) | 90.1-2007 | 3 | 22829 | 109.7142 | 15444 | 74.2225 | 32.35% | 7385 |  |  |  | Dorm | 47 |  |  |  | Gateway Residence Hall (Belk Replacement) | 519318 | 2.4958 | 339219 | 1.6303 | 34.68% | 180099 |  | 0 |  |  | Gateway Residence Hall (Belk Replacement) | 11970900 | 16626.25 | 57.5311 | 7250002 | 10069.4472 | 34.8429 | 39.44% | 4720898 |  |  |  |  | Gateway Residence Hall (Belk Replacement) | 48137413 | 231.3442 | 41707231 | 3917050 | 91100 |  | 322840 | 38.002 | SWA | 90.1-2007
Oak Residence Hall Renovation | 79 | None | UNCC | Mecklenburg | Tom Sparks | 12-09648-03A | 2014-01-06 | CD-2 | 2014-05-19 | 2015-08-24 | Residence Hall | 248 | 52844 | 213.0806 | 4 | Oak Residence Hall Renovation | 90.1-2007 | 3 | 4104 | 77.6626 | 2776 | 52.532 | 32.36% | 1328 |  |  |  | Dorm | 47 |  |  |  | Oak Residence Hall Renovation | 78156 | 1.479 | 52863 | 1.0004 | 32.36% | 25293 |  |  |  |  | Oak Residence Hall Renovation | 3786332 | 15267.4677 | 71.6511 | 2951199 | 11899.996 | 55.8474 | 22.06% | 835133 |  |  |  |  | Oak Residence Hall Renovation | 7187260 | 136.009 | 5929373 | 591176 | 0 |  | 77500 | 52.7967 | Peterson | 90.1-2007
Holding Hall Renovation | 80 | In Progress | Wake TCC | Wake | John Majernik <jlmajernik@waketech.edu> | 06-06753-02A | 2013-11-18 | CD | 2014-08-19 | 2015-12-21 | Offices/Classrooms | NA | 47729 |  | 1 | Holding Hall Renovation | 90.1-2007 | 4 | 2614 | 54.7675 | 1818 | 38.0901 | 30.45% | 796 | 2017-08-17 | 3466.5263 | 72.6294 | Col/Univ | 72 | -32.61% |  | -852.5263 | Holding Hall Renovation | 52390 | 1.0977 | 33542 | 0.70276 | 35.98% | 18848 | 59031.56 | 1.2368 | -12.68% | -6641.56 | Holding Hall Renovation | 1075022 | NA | 22.5235 | 817762 | NA | 17.1334 | 23.93% | 257260 | 360597.4548 | NA | 7.5551 | 66.46% | Holding Hall Renovation | 4947300 | 103.654 | 3327846 | 449750 | 41200 |  |  | 88.1077 | Dewberry | 90.1-2007
McLean Hall at Rizzo | 81 | None | UNC-CH | Orange | O'Hara, Jessica K <johara@email.unc.edu> | 11-08953-01A | 2012-09-04 | CD | Privately Funded | 2016-01-29 | Hotel/Classrooms/Conference | 66 | 97014 | 1469.9091 | 5 | McLean Hall at Rizzo | 90.1-2004 | 4 | 6933 | 71.4639 | 4473 | 46.1067 | 35.48% | 2460 | 2017-08-21 | 8920.5727 | 91.9514 |  |  | -28.67% |  | -1987.5727 | McLean Hall at Rizzo | 14092 | 0.14526 | 10313 | 0.1063 | 26.82% | 3779 | 91991.55 | 0.94823 | -552.8% | -77899.55 | McLean Hall at Rizzo | 2116678 | 32070.8788 | 21.8183 | 1698607 | 25736.4697 | 17.5089 | 19.75% | 418071 | 1248000 | 18909.0909 | 12.8641 | 41.04% | McLean Hall at Rizzo | 25040939 | 258.1168 |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | 90.1-2004
Belk Gymnasium Renovation | 82 | None | UNCC | Mecklenburg | Tom Sparks | 12-09471-03A | 2013-10-18 | DD | 2014-05-05 | 2016-02-18 | Gym, Pool, Offices | NA | 105000 |  | 3 | Belk Gymnasium Renovation (Student Recreation Facility) | 90.1-2010 | 3 | 5893 | 56.1238 | 5553 | 52.8857 | 5.77% | 340 | [8 empty] | Belk Gymnasium Renovation (Student Recreation Facility) | 96234 | 0.91651 | 84246 | 0.80234 | 12.46% | 11988 |  |  |  |  | Belk Gymnasium Renovation (Student Recreation Facility) | 2939272 | NA | 27.9931 | 1888963 | NA | 17.9901 | 35.73% | 1050309 |  |  |  |  | Belk Gymnasium Renovation (Student Recreation Facility) | 14388687 | 137.0351 | 13744319 | 1224800 | 0 |  | 136650 | 65.15 | M&L | 90.1-2010
Winkler Residence Hall Renovation Demolished 06/01/14 |  |  | ASU |  | Jerry Marshall | 10-08894-03A | 2012-09-14 | CD | Demolished 06/01/14 | 2016-06-29 | Residence Hall | 192 | 78450 |  | 12 | Winkler Residence Hall Renovation Demolished 06/01/14 | 90.1-2004 |  | 6070 | 77.3741 | 3601 | 45.9018 | 40.68% | 2469 | [8 empty] | Winkler Residence Hall Renovation Demolished 06/01/14 | 143502 | 1.8292 | 87933 | 1.1209 | 38.72% | 55569 |  |  |  |  | Winkler Residence Hall Renovation Demolished 06/01/14 | 2528379 | 13168.6406 | 32.2292 | 1493037 | 7776.2344 | 19.0317 | 40.95% | 1035342 |  |  |  |  | Winkler Residence Hall Renovation Demolished 06/01/14 | 11873469 | 151.3508 |  | 1313285 | 103000 |  | 92600 | 217.1907 |  | 90.1-2004
Bio-tech & Med Sim Center NOT SB 668 |  |  | Edgecombe CC |  |  | 05-06644-02A | 2014-04-09 | DD | Design Build / NOT SB 668 | Design Build / NOT SB 668 | Office/Classroom/Labs | NA | 44978 |  | 3 | Bio-tech & Med Sim Center NOT SB 668 | 90.1-2007 |  | 6871 | 152.7636 | 4929 | 109.5869 | 28.26% | 1942 | [8 empty] | Bio-tech & Med Sim Center NOT SB 668 | 134054 | 2.9804 | 98221 | 2.1838 | 26.73% | 35833 |  |  |  |  | Bio-tech & Med Sim Center NOT SB 668 |  | NA | 0 |  | NA | 0 |  | 0 |  |  |  |  | Bio-tech & Med Sim Center NOT SB 668 | 4825393 | 107.2834 | 4180000 | 932460 | 308832 |  | 28700 | 27.4307 |  | 90.1-2007
Leonard J. Kaplan Center for Wellness | 83 | Gold | UNCG | Guilford | Douglas Cato | 09-07928-02A | 2014-03-17 | CD | 2014-03-06 | 2016-06-29 | Gym/Pool | NA | 213000 |  | 3 | Student Recreation Center | 90.1-2007 | 4 | 20211 | 94.8873 | 15288 | 71.7746 | 24.36% | 4923 | 2017-08-31 | 32368.4239 | 151.9644 |  |  | -60.15% |  | -12157.4239 | Student Recreation Center | 275822 | 1.2949 | 188166 | 0.88341 | 31.78% | 87656 | 451041.07 | 2.1176 | -63.53% | -175219.07 | Student Recreation Center | 2060500 | NA | 9.6737 | 1524900 | NA | 7.1592 | 25.99% | 535600 | 4071364 | NA | 19.1144 | -97.59% | Student Recreation Center (cost includes CUP?) | 69872746 | 328.0411 | 63588816 | 6427000 | 67200 |  | 344800 | 76.3887 | M&L | 90.1-2007
Reynolds Coliseum Renovation | 84 | In Progress | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 12-09912-01B | 2014-11-18 | CD | 2015-06-16 | 2016-09-01 | Basketball Arena, locker rooms, offices | NA | 165584 |  | 3 | Reynolds Coliseum Renovation | 90.1-2007 | 4 | 29857 | 180.3133 | 22062 | 133.2375 | 26.11% | 7795 | 2017-09-08 | 16841.8529 | 101.7118 |  |  | 43.59% | ü | 13015.1471 | Reynolds Coliseum Renovation | 534913 | 3.2305 | 426967 | 2.5786 | 20.18% | 107946 | 290782.3309 | 1.7561 | 45.64% | 244130.6691 | Reynolds Coliseum Renovation | 330635 | NA | 1.9968 | 247594 | NA | 1.4953 | 25.12% | 83041 | 1585115.1853 | NA | 9.5729 | -379.4% | Reynolds Coliseum Renovation | 23473863 | 141.7641 | 23473863 | 3170473 | 35000 | 60000 | 330235 | 3.9393 | BNK | 90.1-2007
Totals 2016-2017 | [11 empty] | 9309 | 7300141 | [5 empty] | 763483 |  | 518812.8 |  | 32.05% | 244670.2 | [14 empty] | 4099688 | [12 empty] | 51922584 | [5 empty] | 1447680418.39
Levine Residence Hall | 85 | None | UNCC | Mecklenburg | Tom Sparks | 12-10117-03A | 2014-10-22 | CD | 2015-03-30 | 2016-12-06 | Residence Hall | 436 | 157219 | 360.594 | 6 | Levine Residence Hall | 90.1-2007 | 3 | 8086 | 51.4314 | 6532 | 41.5471 | 19.22% | 1554 |  |  |  | Dorm | 47 |  |  |  | Levine Residence Hall | 132669 | 0.84385 | 106400 | 0.67676 | 19.8% | 26269 |  |  |  |  | Levine Residence Hall | 3855098 | 8841.9679 | 24.5206 | 2204228 | 5055.5688 | 14.0201 | 42.82% | 1650870 |  |  |  |  | Levine Residence Hall | 38708442 | 246.2072 | 36840000 | 3018220 |  | 27500 | 164340 | 78.4302 | Optima
Health Sciences Campus - Student Services Facility | 86 | In Progress | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-10217-02A | 2015-01-19 | CD | 2015-06-17 | 2017-04-13 | Offices/Gym/ Food Service/ Book Store | NA | 75843 |  | 4 | Health Sciences Campus - Student Services Facility | 90.1-2010 | 3 | 10944 | 144.2981 | 9185 | 121.1054 | 16.07% | 1759 | [8 empty] | Health Sciences Campus - Student Services Facility | 107685 | 1.4198 | 91262 | 1.2033 | 15.25% | 16423 |  |  |  |  | Health Sciences Campus - Student Services Facility | 1899740 | NA | 25.0483 | 1215180 | NA | 16.0223 | 36.03% | 684560 |  |  |  |  | Health Sciences Campus - Student Services Facility | 26731311 | 352.4559 | 21220000 | 2903738 | 154488 |  | 300000 | 363.2588 | RDK | 90.1-2004
Brown Building Renovation & Addition | 87 | In Progress | WCU | Jackson | David King <dbking@email.wcu.edu> | 13-10964-02A | 2015-09-04 | CD | 2015-11-30 | 2017-07-12 | Food Service/Dining | NA | 64342 |  | 3 | Brown Building Renovation & Addition | 90.1-2010 | 4 | 9679 | 150.4305 | 9209 | 143.1258 | 4.856% | 470 |  |  |  | Rest/Cafet | 166 |  |  |  | Brown Building Renovation & Addition | 137469 | 2.1365 | 123584 | 1.9207 | 10.1% | 13885 |  |  |  |  | Brown Building Renovation & Addition | 649069 | NA | 10.0878 | 492976 | NA | 7.6618 | 24.05% | 156093 |  |  |  |  | Brown Building Renovation & Addition | 21056907 | 327.2653 | 20955798 | 2504600 | 62800 | 17574 | 139652 | 23.1282 | Optima | 90.1-2010
Clement Residence Hall Renovation | 88 | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-10689-02A | 2016-05-18 | CD | Phase 1 3/11/2016 | 2017-07-28 | Residence Hall | 395 | 83462 | 211.2962 | 10 | Clement Residence Hall Renovation | 90.1-2010 | 3 | 5199 | 62.2918 | 5139 | 61.5729 | 1.154% | 60 |  |  |  | Dorm | 47 |  |  |  | Clement Residence Hall Renovation | 123606 | 1.481 | 119683 | 1.434 | 3.174% | 3923 |  |  |  |  | Clement Residence Hall Renovation | 2958825 | 7490.6962 | 35.4512 | 1891131 | 4787.6734 | 22.6586 | 36.09% | 1067694 |  |  |  |  | Clement Residence Hall Renovation | 17178395 | 205.8229 | 17047276 | 1750000 |  | 23400 | 89500 | 62.2021 | EDi | 90.1-2010
Elm Residence Hall Renovation | 89 | None | UNCC | Mecklenburg | Tom Sparks | 12-09940-03A | 2015-09-25 | CD | 2016-06-03 | 2017-09-14 | Residence Hall | 95 | 29845 | 314.1579 | 3 | Elm Residence Hall Renovation | 90.1-2007 | 3 | 2122 | 71.1007 | 1669 | 55.9223 | 21.35% | 453 |  |  |  | Dorm | 47 |  |  |  | Elm Residence Hall Renovation | 34775 | 1.1652 | 26751 | 0.89633 | 23.07% | 8024 |  |  |  |  | Elm Residence Hall Renovation | 1044184 | 10991.4105 | 34.9869 | 677227 | 7128.7053 | 22.6915 | 35.14% | 366957 |  |  |  |  | Elm Residence Hall Renovation | 5379480 | 180.2473 | 5158196.28 | 448389 |  | 3312 | 23400 | 30.9067 | Peterson | 90.1-2007
Pine Residence Hall Renovation | 90 | None | UNCC | Mecklenburg | Tom Sparks | 12-09940-03A | 2015-09-25 | CD | 2016-06-03 | 2017-10-01 | Residence Hall | 95 | 29799 | 313.6737 | 3 | Pine Residence Hall Renovation | 90.1-2007 | 3 | 2122 | 71.2104 | 1669 | 56.0086 | 21.35% | 453 |  |  |  | Dorm | 47 |  |  |  | Pine Residence Hall Renovation | 34775 | 1.167 | 26751 | 0.89771 | 23.07% | 8024 |  |  |  |  | Pine Residence Hall Renovation | 1044184 | 10991.4105 | 35.0409 | 677227 | 7128.7053 | 22.7265 | 35.14% | 366957 |  |  |  |  | Pine Residence Hall Renovation | 5379480 | 180.5255 | 5158196.28 | 448389 |  | 3312 | 23400 | 30.9067 | Peterson | 90.1-2007
Western Crime Lab | 91 | None | NCDoJ | Henderson |  | 12-09454-02A | 2014-10-31 | CD-2 | 2015-07-30 | 2017-09-18 | Labs/Offices | NA | 35357 |  | 2 | Western Crime Lab | 90.1-2007 | 4 | 7819 | 221.1443 | 5695 | 161.0714 | 27.16% | 2124 |  |  |  | Lab | 194 |  |  |  | Western Crime Lab | 205920 | 5.824 | 145347 | 4.1108 | 29.42% | 60573 |  |  |  |  | Western Crime Lab | 142308 | NA | 4.0249 | 97350 | NA | 2.7533 | 31.59% | 44958 |  |  |  |  | Western Crime Lab | 14468100 | 409.2004 | 13630000 | 1440000 |  |  | 120000 | 15.8173 | M&C | 90.1-2007
Advanced Applied Technology Center | 92 | In Progress | Alamance CC | Alamance |  | 07-07353-03A | 2015-12-18 | CD | 2016-05-02 | 2017-10-03 | Shops/Offices | NA | 55099 |  | 1 | Advanced Applied Technology Center | 90.1-2010 | 4 | 5015 | 91.018 | 4773 | 86.6259 | 4.826% | 242 |  |  |  | Col/Univ | 72 |  |  |  | Advanced Applied Technology Center | 128985 | 2.341 | 124246 | 2.255 | 3.674% | 4739 |  |  |  |  | Advanced Applied Technology Center | 152441 | NA | 2.7667 | 85722 | NA | 1.5558 | 43.77% | 66719 |  |  |  |  | Advanced Applied Technology Center | 13631526 | 247.4006 | 13659954 | 861500 | 43500 | 0 | 153000 | 35.4657 | Little | 90.1-2010
Maple Residence Hall Renovation | 93 | None | UNCC | Mecklenburg | Tom Sparks | 12-09940-03A | 2015-09-25 | CD | 2016-06-03 | 2017-11-22 | Residence Hall | 64 | 23270 | 363.5938 | 3 | Maple Residence Hall Renovation | 90.1-2007 | 3 | 1704 | 73.2273 | 1196 | 51.3966 | 29.81% | 508 |  |  |  | Dorm | 47 |  |  |  | Maple Residence Hall Renovation | 28673 | 1.2322 | 19427 | 0.83485 | 32.25% | 9246 |  |  |  |  | Maple Residence Hall Renovation | 692800 | 10825 | 29.7722 | 449405 | 7021.9531 | 19.3126 | 35.13% | 243395 |  |  |  |  | Maple Residence Hall Renovation | 4184040 | 179.804 | 4011930.44 | 348747 |  | 2576 | 18200 | 20.8615 | Peterson | 90.1-2007
Workforce Solutions Complex | 94 | In Progress | Catawba Valley CC | Catawba |  | 07-07389-02A | 2015-06-09 | DD | 2016-09-22 | 2018-03-16 | Classrooms/Offices/Lab&Shop/conf training/etc | NA | 80200 |  | 1 | Workforce Solutions Complex | 90.1-2010 | 4 | 6020 | 75.0623 | 5167 | 64.4264 | 14.17% | 853 |  |  |  |  | 72 |  |  |  | Workforce Solutions Complex | 88975 | 1.1094 | 79804 | 0.99506 | 10.31% | 9171 |  |  |  |  | Workforce Solutions Complex | 935004 | NA | 11.6584 | 509544 | NA | 6.3534 | 45.5% | 425460 |  |  |  |  | Workforce Solutions Complex | 20463200 | 255.1521 | 20407437 | 1928500 | 53000 |  | 45670 | 16.8393 | M&L | 90.1-2004
Main Campus - Student Union | 95 | In Progress | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-09263-02A | 2015-07-20 | CD | 2015-12-18 | 2018-03-18 | Offices/Theater/Conference/ Food Service/ Book Store | NA | 213911 |  | 4 | Main Campus - Student Union | 90.1-2007 | 3 | 38581 | 180.3601 | 23447 | 109.611 | 39.23% | 15134 | [8 empty] | Main Campus - Student Union | 629463 | 2.9426 | 393838 | 1.8411 | 37.43% | 235625 |  |  |  |  | Main Campus - Student Union | 1394940 | NA | 6.5211 | 863295 | NA | 4.0358 | 38.11% | 531645 |  |  |  |  | Main Campus - Student Union | 95491076 | 446.4056 | 93491076 | 9640712 | 161300 |  | 707030 | 12.1733 | AEI | 90.1-2007
New Student Center | 96 | In Progress | NCA&T | Guilford |  | 03-08608-02A | 2014-05-09 | CD | 2014-02-20 | 2018-05-11 | Offices/Theater/Conference/Food Service/Book Store | NA | 182275 |  | 4 | New Student Center | 90.1-2007 | 4 | 31691 | 173.8637 | 23425 | 128.5146 | 26.08% | 8266 |  |  |  | Rest/café | 166 |  |  |  | New Student Center | 529117 | 2.9029 | 366504 | 2.0107 | 30.73% | 162613 |  |  |  |  | New Student Center | 5763776 | NA | 31.6213 | 4434106 | NA | 24.3265 | 23.07% | 1329670 |  |  |  |  | New Student Center | 71806942 | 393.9484 | 64958142 | 7250000 | 166000 |  | 594000 | 46.7908 | RMF | 90.1-2007
New Residence Hall - Freshman Living/Learning | 97 | None | WSSU | Forsyth | Dick Kabis | 13-10372-03A | 2014-10-20 | CD | 2015-12-28 | 2018-06-06 | Residence Hall | 290 | 71021 | 244.9 | 6 | New Residence Hall - Freshman Living/Learning | 90.1-2010 | 4 | 3347 | 47.1269 | 3202 | 45.0853 | 4.332% | 145 |  |  |  | Dorm | 58 |  |  |  | New Residence Hall - Freshman Living/Learning | 54763 | 0.77108 | 50499 | 0.71104 | 7.786% | 4264 |  |  |  |  | New Residence Hall - Freshman Living/Learning | 2798472 | 9649.9034 | 39.4034 | 2000107 | 6896.9207 | 28.1622 | 28.53% | 798365 |  |  |  |  | New Residence Hall - Freshman Living/Learning | 17750570 | 249.9341 | 16000000 | 1735188 | 75000 | 11000 | 176132 | 472.022 | RMF | 90.1-2010
Allied Health & Workforce (Courtesy review only of DD phase) |  |  | ABTCC |  |  | 12-09487-01A | 2012-11-13 | DD | No Contract | No Contract (Creating) | Office/Classroom/Lab/Assembly | NA | 185810 | #VALUE! | 6 | Allied Health & Workforce | 90.1-2004 |  | 10582 | 56.9506 | 3675 | 19.7783 | 65.27% | 6907 | [8 empty] | Allied Health & Workforce | 267259 | 1.4383 | 93214 | 0.50166 | 65.12% | 174045 |  |  |  |  | Allied Health & Workforce | 115375 | NA | 0.62093 | 50944 | NA | 0.27417 | 55.84% | 64431 |  |  |  |  | Allied Health & Workforce | 45400738 | 244.3396 | 42736000 | no contract |  |  |  | 15.3106 |  | 90.1-2004
Building 600 NOT SB 668 |  |  | RCCC |  |  | 11-08937-02A | 2013-01-25 | DD | No Contract | No Contract (Creating) | Classroom, offices | NA | 69250 | #VALUE! | 2 | Building 600 NOT SB 668 | 90.1-2004 |  | 4413 | 63.7256 | 2774 | 40.0578 | 37.14% | 1639 | [8 empty] | Building 600 NOT SB 668 | 82649 | 1.1935 | 58907 | 0.85064 | 28.73% | 23742 |  |  |  |  | Building 600 NOT SB 668 | 60744 | NA | 0.87717 | 45643 | NA | 0.6591 | 24.86% | 15101 |  |  |  |  | Building 600 NOT SB 668 | 10191099 | 147.1639 | 8586550 | Included w/ Bldgs 300 and 500. | 0 |  | 0 | 67.5827 |  | 90.1-2004
Heavy Equipment + Transport Technology Center NOT SB 668 |  |  | CFCC |  |  | 11-08585-02A |  | DD | 2015-07-07 | 2017-10-05 | Equipment repair, offices, classrooms | NA | 32221 |  | 2 | Heavy Equipment + Transport Technology Center NOT SB 668 | 90.1-2007 | 3 | [14 empty] | Heavy Equipment + Transport Technology Center NOT SB 668 | 28938 | 0.89811 | 22854 | 0.70929 | 21.02% | 6084 |  |  |  |  | Heavy Equipment + Transport Technology Center NOT SB 668 | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. |  |  |  |  | Heavy Equipment + Transport Technology Center NOT SB 668 | included in AET Center bid amount |  | 2041899 | Included w/A+ETC | 0 |  | NOT SB 668 |  |  | 90.1-2007
Scott Residence Hall Renovation | 98 | None | UNCC | Mecklenburg | Tom Sparks | 14-11473-01A | 2016-08-22 | CD | 2017-02-12 | 2018-06-15 | Residence Hall | 402 | 102000 | 253.7313 | 12 | Scott Residence Hall Renovation | 90.1-2010 | 3 | 5644 | 55.3333 | 5896 | 57.8039 | -4.465% | -252 |  |  |  | Dorm | 47 |  |  |  | Scott Residence Hall Renovation | 70232 | 0.68855 | 81265 | 0.79672 | -15.71% | -11033 |  |  |  |  | Scott Residence Hall Renovation | 5477216 | 13624.9154 | 53.6982 | 4142946 | 10305.8358 | 40.6171 | 24.36% | 1334270 |  |  |  |  | Scott Residence Hall Renovation | 17387927 | 170.4699 | 17300000 | 1485000 |  | 12000 | 130409.4525 | -20.877 | KSQ | 90.1-2010
Mary Ellen Jones Renovation | 99 | In Progress | UNC | Orange |  | 11-09861-02A and 11-09861-02C | 2015-02-09 | DD-2 | 2016-01-04 | 2018-07-04 | Labs/Offices | NA | 221618 |  | 11 | Mary Ellen Jones Renovation | 90.1-2010 | 4 | 27375.8 | 123.527 | 22956.3 | 103.585 | 16.14% | 4419.5 |  |  |  | Lab | 194 |  |  |  | Mary Ellen Jones Renovation | 1006324 | 4.5408 | 813664 | 3.6715 | 19.14% | 192660 |  |  |  |  | Mary Ellen Jones Renovation | 663675 | NA | 2.9947 | 445591 | NA | 2.0106 | 32.86% | 218084 |  |  |  |  | Mary Ellen Jones Renovation | 84957809 | 383.3525 | 75208000 | 8628179 |  | 10370 | 730000 | 54.4492 | Newcomb & Boyd | 90.1-2007
Sarah & Edward Smith Health Sciences Center | 100 | In Progress | Davidson CCC | Davidson |  | 07-07386-02A | 2016-08-04 | FD-2 | 2017-01-10 | 2018-08-01 | Classrooms/Offices/Labs | NA | 48794 |  | 3 | Health Sciences Center | 90.1-2010 | 3 | 2713 | 55.6011 | 1981 | 40.5993 | 26.98% | 732 | [8 empty] | Health Sciences Center | 66149 | 1.3557 | 48211 | 0.98805 | 27.12% | 17938 |  |  |  |  | Health Sciences Center | 854321 | NA | 17.5087 | 540545 | NA | 11.0781 | 36.73% | 313776 |  |  |  |  | Health Sciences Center | 10391571 | 212.9682 | 8685925 | 811900 | 32900 | 23500 | 98750 | 103.7349 | Little | 90.1-2010
Advanced Technology Center | 101 | None | Rowan-Cabarrus CCC |  |  | 16-15695-02A | 2017-03-16 | SD | No Contract | 2018-12-04 | Classrooms/Offices/Labs | NA | 55294 |  | 3 | Advanced Technology Center | 90.1-2010 | 3 | 3043.336 | 55.0392 | 2810.44 | 50.8272 | 7.653% | 232.896 |  |  |  | Col/Univ | 72 |  |  |  | Advanced Technology Center | 102036 | 1.8453 | 94226 | 1.7041 | 7.654% | 7810 |  |  |  |  | Advanced Technology Center | 1602716 | NA | 28.9854 | 866197 | NA | 15.6653 | 45.95% | 736519 |  |  |  |  | Advanced Technology Center | 12584164 | 227.5864 |  | 1250000 | 0 | 16000 |  | 1613.3373 | Little | 90.1-2010
Science and Office Bldg | 102 | In Progress | WSSU | Forsyth | Dick Kabis | 07-07236-01B | 2017-06-14 | CD-2 | No Contract | 2019-09-17 | Classroom/Lab/Offices | NA | 102095 |  | 5 | Science and Office Bldg | 90.1-2010 | 4 | 18355 | 179.7835 | 13275 | 130.026 | 27.68% | 5080 | [8 empty] | Science and Office Bldg | 246679 | 2.4162 | 195121 | 1.9112 | 20.9% | 51558 |  |  |  |  | Science and Office Bldg | 1071543 | NA | 10.4955 | 715542 | NA | 7.0086 | 33.22% | 356001 |  |  |  |  | Science and Office Bldg | 42805871 | 419.2749 | 41343286 | 4603210 | 138000 |  | 455967 | 39.8881 | AEI | 90.1-2010
Engineering Research & Innovation Complex (ERIC) | 103 | In Progress | NCA&T | Guilford |  | 16-15521-02A | 2017-05-15 | SD | No Contract | 2020-12-12 | Offices/Labs/Classrooms | NA | 130000 |  | 5 | Engineering Research & Innovation Complex (ERIC) | 90.1-2010 | 4 | 22207 | 170.8231 | 13985 | 107.5769 | 37.02% | 8222 |  |  |  | Lab | 175 |  |  |  | Engineering Research & Innovation Complex (ERIC) | 374077 | 2.8775 | 253210 | 1.9478 | 32.31% | 120867 |  |  |  |  | Engineering Research & Innovation Complex (ERIC) | 3986280 | NA | 30.6637 | 3044169 | NA | 23.4167 | 23.63% | 942111 |  |  |  |  | Engineering Research & Innovation Complex (ERIC) | 74530558 | 573.312 | 73798919 | 8198361.38 | 37265.279 | 36000 | 298122.232 | 9.126 | RMF/TWG | 90.1-2010
Division 2 Equipment Shop | 104 | None | DOT |  | Eric Frazier | 12-09859-03A | 2016-05-04 | FD | No Contract | No Contract | Repair garage/storage/offices | NA | 36215 |  | 1 | Division 2 Equipment Shop | 90.1-2010 | 3 | 4215 | 116.3882 | 3907 | 107.8835 | 7.307% | 308 |  |  |  |  | 32 |  |  |  | Division 2 Equipment Shop | 66838 | 1.8456 | 33837 | 0.93434 | 49.37% | 33001 |  |  |  |  | Division 2 Equipment Shop | 252297 | NA | 6.9666 | 187574 | NA | 5.1795 | 25.65% | 64723 |  |  |  |  | Division 2 Equipment Shop | 6807340.17 | 187.9702 | 6767100.17 | 539733 | 12290 | 8000 | 37090 | 2.9581 | Dibble and Pledger | 90.1-2010
Facilities Operations Offices/Shops Building | 105 | None | UNCC |  | Tom Sparks | 16-15656-01A | 2017-02-02 | SD | No Contract | No Contract | Offices/Shops | NA | 38000 |  | 1 | Facilities Operations Offices/Shops Building | 90.1-2010 | 4 | 2199 | 57.8684 | 1860 | 48.9474 | 15.42% | 339 |  |  |  | 5 Mixed-use office & 46 Other service | 59 |  |  |  | Facilities Operations Offices/Shops Building | 38591 | 1.0156 | 33870 | 0.89132 | 12.23% | 4721 |  |  |  |  | Facilities Operations Offices/Shops Building | 999115 | NA | 26.2925 | 599526 | NA | 15.777 | 39.99% | 399589 |  |  |  |  | Facilities Operations Offices/Shops Building | 7280513 | 191.5924 | 6936265 | 1748670 | 52800 | 10000 |  | 86.2207 | Optima | 90.1-2010
Facilities Operations Warehouse w/offices | 106 | None | UNCC |  | Tom Sparks | 16-15656-01A | 2016-10-14 | AP | No Contract | No Contract | Warehouse/Storage | NA | 23000 |  | 1 | Facilities Operations Warehouse w/offices | 90.1-2010 | 4 | [9 empty] | 9 Nonrefrigerated warehouse w/Mixed use offices | 33 |  |  |  | Facilities Operations Warehouse w/offices | [10 empty] | Facilities Operations Warehouse w/offices | [12 empty] | Facilities Operations Warehouse w/offices | [8 empty] | Optima | 90.1-2010
Student Housing Phase III | 107 | None | UNC | Orange |  | 12-09765-02A | 2015-01-14 | DD | Project on Hold | Project on Hold | Residence Hall and Offices | 275 | 112886 | 410.4945 | 7 | Student Housing Phase III | 90.1-2010 | 4 | 9032 | 80.0099 | 7916 | 70.1238 | 12.36% | 1116 |  |  |  | Dorm | 58 |  |  |  | Student Housing Phase III | 219320 | 1.9428 | 186485 | 1.652 | 14.97% | 32835 |  |  |  |  | Student Housing Phase III | 917871 | 3337.7127 | 8.131 | 584333 | 2124.8473 | 5.1763 | 36.34% | 333538 |  |  |  |  | Student Housing Phase III | 26052469 | 230.7857 | 25799369 | 1961668 | 53300 | 31970 | 250000 | 17.919 | CN | 90.1-2010
Sanford Residence Hall Renovation | 108 | None | UNCC | Mecklenburg | Tom Sparks | 12-09978-03A | 2014-07-09 | DD | No Contract | Project on Hold | Residence Hall | 440 | 99436 | 225.9909 | 12 | Sanford Residence Hall Renovation | 90.1-2010 | 3 | 5384 | 54.1454 | 4674 | 47.0051 | 13.19% | 710 |  |  |  | Dorm | 47 |  |  |  | Sanford Residence Hall Renovation | 58913 | 0.59247 | 50839 | 0.51127 | 13.7% | 8074 |  |  |  |  | Sanford Residence Hall Renovation | 4280271 | 9727.8886 | 43.0455 | 2887348 | 6562.1545 | 29.0373 | 32.54% | 1392923 |  |  |  |  | Sanford Residence Hall Renovation | 15688400 | 157.7738 | 15615290 | 1287470 |  | 4100 | 100000 | 21.9482 | M&L | 90.1-2010 | 73110
Collaborative Science Building | 109 | None | UNC | Orange |  | 11-09030-02A | 2013-11-01 | DD | No Contract | Project on Hold | Labs/Offices | NA | 274810 |  | 9 | Collaborative Science Building | 90.1-2007 | 4 | 15342 | 55.8277 | 11509 | 41.8798 | 24.98% | 3833 | [8 empty] | Collaborative Science Building | 293091 | 1.0665 | 229379 | 0.83468 | 21.74% | 63712 |  |  |  |  | Collaborative Science Building | 1871354 | NA | 6.8096 | 1339798 | NA | 4.8754 | 28.4% | 531556 |  |  |  |  | Collaborative Science Building | 72817169 | 264.9728 | 78341076 | 7995000 | 223000 | 65350 | 500000 | -74.3276 | Atelier Ten | 90.1-2007
Highway Patrol Training Facility | 110 |  | DOA | Wake |  | 10-08389-02A | 2012-06-28 | CD | Project on Hold | Project on Hold | Office/Classroom/Training | NA | 34386 |  | 2 | Highway Patrol Training Facility | 90.1-2004 | 4 | 2484 | 72.2387 | 1436 | 41.7612 | 42.19% | 1048 | [8 empty] | Highway Patrol Training Facility | 59882 | 1.7415 | 41042 | 1.1936 | 31.46% | 18840 |  |  |  |  | Highway Patrol Training Facility | 667359 | NA | 19.4079 | 310095 | NA | 9.0181 | 53.53% | 357264 |  |  |  |  | Highway Patrol Training Facility | 6245727 | 181.6358 | 5604454 | is for multiple buildings | is for multiple buildings |  | 84000 |  |  | 90.1-2004
School of Aviation | 111 |  | ECSU | Pasquotank | Elizabeth Linney | 07-07166-02A | 2011-01-24 | CD | Project on Hold | Project on Hold | Office/Classroom/Hangar | NA | 44000 |  | 1 | School of Aviation | 90.1-2004 | 3 | 1913 | 43.4773 | 1115 | 25.3409 | 41.71% | 798 | [8 empty] | School of Aviation | 118819 | 2.7004 | 67443 | 1.5328 | 43.24% | 51376 |  |  |  |  | School of Aviation | 179563 | NA | 4.081 | 121788 | NA | 2.7679 | 32.18% | 57775 |  |  |  |  | School of Aviation | [9 empty] | 90.1-2004
Locomotive and Railcar Maint. Facility | 112 |  | DOT | Mecklenburg |  | 10-08634-03A | 2011-10-20 | SD | Project on Hold | Project on Hold | Offices & Railcar | NA | 68400 |  | 1 | Locomotive and Railcar Maint. Facility | 90.1-2004 | 3 | 23291 | 340.5117 | 8015 | 117.1784 | 65.59% | 15276 | [8 empty] | Locomotive and Railcar Maint. Facility | 210152 | 3.0724 | 107570 | 1.5727 | 48.81% | 102582 |  |  |  |  | Locomotive and Railcar Maint. Facility | [12 empty] | Locomotive and Railcar Maint. Facility | [9 empty] | 90.1-2004
Basic Skills Building | 113 |  | Robeson CC | Robeson |  | 07-07572-01A | 2010-12-22 | AP/SD | Project on Hold | Project on Hold | Office/Classroom | NA | 34271 |  | 2 | Basic Skills Building | 90.1-2004 | 3 | 2178 | 63.5523 | 1492 | 43.5354 | 31.5% | 686 | [8 empty] | Basic Skills Building | 51338 | 1.498 | 36026 | 1.0512 | 29.83% | 15312 |  |  |  |  | Basic Skills Building |  | NA | 0 |  | NA | 0 |  | 0 |  |  |  |  | Basic Skills Building | [9 empty] | 90.1-2004
Multipurpose Bldg | 114 |  | South Piedmont CC |  |  | 07-07352-03A | 2010-07-23 | CD | Approved to bid 05/15/2011 | Project on Hold | Office/Classroom/Labs | NA | 75000 |  | 3 | Multipurpose Bldg | 90.1-2004 | 4 | 5827 | 77.6933 | 3550 | 47.3333 | 39.08% | 2277 | [8 empty] | Multipurpose Bldg | 135642 | 1.8086 | 87360 | 1.1648 | 35.6% | 48282 |  |  |  |  | Multipurpose Bldg | 587500 | NA | 7.8333 | 398125 | NA | 5.3083 | 32.23% | 189375 |  |  |  |  | Multipurpose Bldg | [9 empty] | 90.1-2004
Discovery Center Project - Reynolds East | 115 |  | NCSSM | Durham |  | 07-07313-04A | 2010-05-10 | CD | Final Not Approved 05/23/2011 | Project on Hold | Residence Hall / Classroom | 31 | 26000 | 838.7097 | 4 | Discovery Center Project - Reynolds East | 90.1-2004 | 4 | 1846 | 71 | 1121 | 43.1154 | 39.27% | 725 | [8 empty] | Discovery Center Project - Reynolds East | 30466 | 1.1718 | 19282 | 0.74162 | 36.71% | 11184 |  |  |  |  | Discovery Center Project - Reynolds East | 475929 | 15352.5484 | 18.305 | 337075 | 10873.3871 | 12.9644 | 29.18% | 138854 |  |  |  |  | Discovery Center Project - Reynolds East | [9 empty] | 90.1-2004
Greene Residence Hall Renovation | 116 | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 16-13051-01B | 2017-06-29 | DD |  |  | Residence Hall | 395 | 83462 | 211.2962 | 10 | Greene Residence Hall Renovation | 90.1-2010 | 3 | 5199 | 62.2918 | 5139 | 61.5729 | 1.154% | 60 |  |  |  | Dorm | 47 |  |  |  | Greene Residence Hall Renovation | 123606 | 1.481 | 119683 | 1.434 | 3.174% | 3923 |  |  |  |  | Greene Residence Hall Renovation | 2958825 | 7490.6962 | 35.4512 | 1891131 | 4787.6734 | 22.6586 | 36.09% | 1067694 |  |  |  |  | Greene Residence Hall Renovation | 19000000 | 227.6485 | 18868881 | 1750000 |  | 23400 | 89500 | 62.2021 | EDi | 90.1-2010
Note on AD3: Thagard, Leonard: No normalization factor or no table 7-3 multiplier.
Note on BI4: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on AA5: Thagard, Leonard: model was for addition and renovation. Meter is for entire building.
Note on AT5: Leonard Thagard: limited kitchen use and limited bathroom use. Number is extremely low.
Note on AW5: Leonard Thagard: limited kitchen and bathroom use. Number is low.
Note on BI5: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on U6: Leonard Thagard: highest residence hall baseline EUI to date.
Note on W6: Leonard Thagard: highest proposed EUI for residence halls.
Note on BI6: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on AF7: Thagard, Leonard: No steam meter data.
Note on AO7: Leonard Thagard: Does not include steam cost.
Note on BI7: Leonard Thagard: Calculated from original amount construction contract less increase noted in LCCA for envelope, plumb, chillers and lights.
Note on AF8: Thagard, Leonard: No steam meter data.
Note on AO8: Thagard, Leonard: Does not include steam cost.
Note on BI8: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on BK8: Leonard Thagard: SB 668 at $99800 and LEED at $73700
Note on BB10: Thagard, Leonard: shared water meter.
Note on BI10: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on N11: Leonard Thagard: size is for addition only
Note on T11: Leonard Thagard: energy use is for addition only
Note on U11: Thagard, Leonard: EUI is for addition and renovation only, not entire building.
Note on AA11: Thagard, Leonard: metered energy usage is for entire building; addition, renovation and existing building
Note on AB11: Thagard, Leonard: EUI is for entire building.
Note on AO11: Thagard, Leonard: metered energy cost is for entire building, not just addition and renovation.
Note on AP11: Thagard, Leonard: $/sqft is for entire building.
Note on BB11: Thagard, Leonard: metered water consumption is for entire facility.
Note on BI11: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on BG13: Leonard Thagard: Includes RUP?
Note on BI13: Leonard Thagard: Does not include RUP?
Note on BK13: Leonard Thagard: LEED fees of 180,000 plus design amend #1 for SB 668 for 41,084
Note on BB14: Thagard, Leonard: shared water meter.
Note on M17: Leonard Thagard: One model performed and applied to seven bldgs
Note on N17: Leonard Thagard: One model performed and applied to seven bldgs.
Note on T17: Leonard Thagard: One model performed and applied to seven bldgs
Note on AO17: Thagard, Leonard: Chilled water cost is not included.
Note on BG17: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BJ17: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BK17: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BM17: Leonard Thagard: Cx fee divided by 7 buildings.
Note on M18: Leonard Thagard: One model performed and applied to seven bldgs
Note on N18: Leonard Thagard: One model performed and applied to seven bldgs.
Note on T18: Leonard Thagard: One model performed and applied to seven bldgs
Note on AO18: Thagard, Leonard: Chilled water cost is not included.
Note on BG18: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BJ18: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BK18: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BM18: Leonard Thagard: Cx fee divided by 7 buildings.
Note on M19: Leonard Thagard: One model performed and applied to seven bldgs
Note on N19: Leonard Thagard: One model performed and applied to seven bldgs.
Note on T19: Leonard Thagard: One model performed and applied to seven bldgs
Note on AO19: Thagard, Leonard: Chilled water cost is not included.
Note on BG19: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BJ19: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BK19: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BM19: Leonard Thagard: Cx fee divided by 7 buildings.
Note on M20: Leonard Thagard: One model performed and applied to seven bldgs
Note on N20: Leonard Thagard: One model performed and applied to seven bldgs.
Note on T20: Leonard Thagard: One model performed and applied to seven bldgs
Note on AO20: Thagard, Leonard: Chilled water cost is not included.
Note on BG20: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BJ20: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BK20: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BM20: Leonard Thagard: Cx fee divided by 7 buildings.
Note on M21: Leonard Thagard: One model performed and applied to seven bldgs
Note on N21: Leonard Thagard: One model performed and applied to seven bldgs.
Note on T21: Leonard Thagard: One model performed and applied to seven bldgs
Note on AO21: Thagard, Leonard: Site lighting cost is included. Chilled water cost is not included.
Note on BG21: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BJ21: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BK21: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BM21: Leonard Thagard: Cx fee divided by 7 buildings.
Note on M22: Leonard Thagard: One model performed and applied to seven bldgs
Note on N22: Leonard Thagard: One model performed and applied to seven bldgs.
Note on T22: Leonard Thagard: One model performed and applied to seven bldgs
Note on AO22: Thagard, Leonard: Chilled water costs are not included.
Note on BG22: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BJ22: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BK22: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BM22: Leonard Thagard: Cx fee divided by 7 buildings.
Note on M23: Leonard Thagard: One model performed and applied to seven bldgs
Note on N23: Leonard Thagard: One model performed and applied to seven bldgs.
Note on T23: Leonard Thagard: One model performed and applied to seven bldgs
Note on AO23: Thagard, Leonard: Chilled water costs are not included.
Note on BG23: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BJ23: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BK23: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BM23: Leonard Thagard: Cx fee divided by 7 buildings.
Note on BK26: Leonard Thagard: LEED services added as design amendment. Add to OTDF.
Note on BJ28: Leonard Thagard: Combined design fee for original building design and revised building design.
Note on AF29: Thagard, Leonard: Chilled water and heating hot water use is not metered.
Note on AP29: Thagard, Leonard: chilled water and heating hot water is billed on a square footage basis, not energy use.
Note on BK29: Leonard Thagard: SB 668 at 17520 and LEED at 139300
Note on BB31: Thagard, Leonard: meter inoperable.
Note on BG33: Leonard Thagard: CMR bid packages, NCSU utility assessment, parking deck assessment, etc. make bid amount difficult to accurately calculate.
Note on BG35: Leonard Thagard: Amount is for entire football complex.
Note on BH35: Leonard Thagard: Error in calculation due to entire football complex in one bid package. Building was not broken out.
Note on BJ35: Leonard Thagard: Fee includes design for complete football stadium complex.
Note on BG37: Leonard Thagard: Best guess from multiple bid packages. Will revisit later.
Note on BJ37: Leonard Thagard: 27% of full design fee
Note on BG38: Leonard Thagard: 73 percent of bid package total for Plemmons and Summit
Note on BJ38: Leonard Thagard: 73 percent of full design fee.
Note on U39: Leonard Thagard: Baseline is high.
Note on W39: Leonard Thagard: Proposed is high.
Note on BI39: Leonard Thagard: Note in LCCA report: "*Initial Cost estimated to be 85% of Construction Budget."
Note on K40: Leonard Thagard: BO
Note on AA42: Thagard, Leonard: incomplete meter data
Note on AE42: Thagard, Leonard: incomplete meter data
Note on AO42: Thagard, Leonard: incomplete meter data
Note on AQ42: Thagard, Leonard: incomplete meter data
Note on BI44: Leonard Thagard: deduct for wall, roof, glaze, bid alt 3, plumb, daylighting, bid alt 1
Note on BG45: Leonard Thagard: Early site package plus building package.
Note on BI45: Leonard Thagard: Clark Nexsen analysis indicated baseline building cost more to build than the proposed building. Analysis not used here.
Note on BG47: Leonard Thagard: Early site plus site and building bid packages.
Note on O49: Thagard, Leonard: includes dining hall
Note on AC49: Thagard, Leonard: This building also contains a dining hall.
Note on BC49: Thagard, Leonard: Resident Hall and food service combined.
Note on K53: Leonard Thagard: Best guess.
Note on AA53: Leonard Thagard: Thermal utilities are metered on a square foot basis not on usage.
Note on BG53: Leonard Thagard: Designer's LCCA estimate.
Note on BI53: Leonard Thagard: Designer's LCCA estimate.
Note on K54: Leonard Thagard: BO per Jerry Rogers' handwritten notes in file.
Note on BI54: Leonard Thagard: LCCA cost estimate for proposed building was $46,642,869 while baseline was $46,128,762 for a difference of 514,107 which was deducted from the bid amount to arrive at the baseline building estimate.
Note on BK54: Leonard Thagard: LEED certification 110000 and article 15-1 fee 229250
Note on AA55: Thagard, Leonard: Does not include heating hot water consumption.
Note on AO55: Thagard, Leonard: does not include heating hot water cost. Does not include chilled water cost.
Note on BB55: Thagard, Leonard: No meter data.
Note on BI58: Leonard Thagard: baseline calculated from bid amount less delta of $1,012,000 between proposed and baseline estimates by designer.
Note on BG60: Leonard Thagard: Early site plus building package.
Note on BC62: Thagard, Leonard: Not possible: 871 gallons/student/year.
Note on BI63: Leonard Thagard: baseline and proposed building cost estimates exceeded the bid amount. Costs to implement energy legislation are negative.
Note on BK64: Leonard Thagard: Green Globes.
Note on BG68: Leonard Thagard: CMR bid packages and CO's through CO#10.
Note on BI68: Leonard Thagard: CD estimates for baseline and proposed buildings exceed CMR bids through CO #10. Baseline estimate is CMR contract amount through CO #10 less designer's delta between baseline and proposed buildings.
Note on AO69: Thagard, Leonard: partial meter data incomplete
Note on AQ69: Thagard, Leonard: Partial meter data. No chilled water. No heating hot water or steam.
Note on AZ71: Leonard Thagard: includes kitchen load and cooling tower make up at 3,600,000 gall/yr.
Note on BG74: Leonard Thagard: Captures most but not all bid packages.
Note on BJ74: Leonard Thagard: includes swing space, promotion support, bridge over RR tracks, etc.
Note on X78: Leonard Thagard: 27% improvement without plug and process loads.
Note on BK78: Leonard Thagard: Green Globes
Note on N80: Leonard Thagard: GSF does not include tempered un-occupied attic space of ~22,000 SF.
Note on AA80: Thagard, Leonard: Total does not include thermal utilities or chilled water and heating hot water
Note on AO80: Thagard, Leonard: Total does not include thermal utilities
Note on BG80: Leonard Thagard: Designer's proposed building estimate is $5,957,771. Early demo is not included. Contract may include CUP and distribution piping. Ear
Note on BI80: Leonard Thagard: does not include early demo, CEP, CEP distribution, etc.
Note on BM80: Leonard Thagard: There is no SCO contract for Cx.
Note on N81: Leonard Thagard: Listed now as two buildings East at 102,127 GSF and West at 105,950 GSF.
Note on AA81: Thagard, Leonard: does not include steam/condensate meter data
Note on AO81: Thagard, Leonard: does not include steam/condensate meter data
Note on BB81: Thagard, Leonard: does not include Aug 15 and July 16 meter data
Note on AU82: Leonard Thagard: Includes cooling tower make up and large laundry load.
Note on J84: Leonard Thagard: Private funding. No state contract.
Note on K84: Thagard, Leonard: ?
Note on O84: Thagard, Leonard: include conference center meeting rooms.
Note on K85: Thagard, Leonard: BO. Working through punch list and natatorium.
Note on N85: Leonard Thagard: 131,341 includes pool deck and pool lobby in GSF. M&L estimate at 105,000 GSF.
Note on T85: Leonard Thagard: Includes plug and process loads. Pool equipment and HVAC are considered process loads.
Note on X85: Leonard Thagard: 6% less energy than A90.1-2010.
Note on BN85: Leonard Thagard: Not correct since base is A90.1-2010 instead of A90.1-2004. Also window and roof replacement not analyzed based on LCCA.
Note on K86: Thagard, Leonard: BO
Note on BG87: Leonard Thagard: SB 668 bldg estimate from PDC. BCC DB GMP is $9,751,745
Note on BI87: Leonard Thagard: Proposed bldg estimate from PDC. BCC DB GMP is $9,751,745
Note on BK87: Leonard Thagard: PDC estimate from HB 628 study.
Note on BM87: Leonard Thagard: PDC estimate for Cx.
Note on N88: Leonard Thagard: GSF includes alternates for additional space and per email from Rebecca dated 12.19.13.
Note on T88: Leonard Thagard: Includes process loads.
Note on V88: Leonard Thagard: Includes process loads.
Note on P89: Leonard Thagard: base=57,963 1st=70,579 mez=37,042 Need to verify GSF.
Note on K91: Thagard, Leonard: BO.
Note on X91: Leonard Thagard: 25% improvement w/o plug load
Note on AH91: Leonard Thagard: energy dollars include plug and process loads
Note on BI91: Leonard Thagard: baseline estimate from energy model report. Proposed estimate si $36,334,998 compared to CM estimate of
Note on BK92: Thagard, Leonard: $154,488 for LEED Silver Certification
Note on K93: Thagard, Leonard: BO? Per Lipke's notes of 07/14/17. Cx not complete.
Note on N93: Leonard Thagard: Building Area including overhang.
Note on BI93: Leonard Thagard: Proposed building reconciled CRM cost estimate less delta for base building from LCCA.
Note on K94: Thagard, Leonard: BO
Note on BK94: Leonard Thagard: Not LEED per meeting minutes 04.09.14.
Note on K97: Thagard, Leonard: Interscope has final sometime in June 2017. Construction completion is two + months behind.
Note on BM97: Leonard Thagard: Current contract is for $22,000. $120,000 is commissioning reserve.
Note on BK98: Leonard Thagard: LEED certification design & documentation for $35,000. LEED Registration for $8,500.
Note on BI101: Leonard Thagard: Delta between proposed and baseline is $2,000,000 per AEI LCCA.
Note on T102: Leonard Thagard: Includes process load
Note on V102: Leonard Thagard: Includes process load.
Note on X102: Leonard Thagard: Savings are 46% with process load removed.
Note on AI102: Leonard Thagard: Includes process load.
Note on AK102: Leonard Thagard: Includes process load.
Note on AT102: Leonard Thagard: Includes cooling tower consumption.
Note on AW102: Leonard Thagard: Includes cooling tower consumption that is reduced due to smaller cooling load.
Note on BI102: Leonard Thagard: Baseline whole building estimate from LCCA.
Note on BJ102: Leonard Thagard: Includes fee for swing space and others.
Note on A104: Leonard Thagard: Courtesy review only of energy model and LCCA per Greg Driver & Joe Bace discussion (SCO Director & AB Tech Fac/Oper Director)
Note on W104: Leonard Thagard: second lowest proposed EUI, second only to a warehouse/storage facility.
Note on X104: Leonard Thagard: Highest percentage savings to date.
Note on T106: Leonard Thagard: No data provided with SD or DD submission.
Note on V106: Leonard Thagard: No data provided with SD or DD submission.
Note on BI107: Thagard, Leonard: Designer's proposed building cost estimate and energy consumption exceeded bid price and modeled energy consumption.
Note on BM107: Thagard, Leonard: estimated at .75% of proposed construction cost.
Note on T108: Leonard Thagard: Plug and process has not been included.
Note on V108: Leonard Thagard: Plug and process has not been included.
Note on AJ108: Leonard Thagard: Highest $/GSF to date.
Note on AL108: Leonard Thagard: Highest $/GSF to date.
Note on BM108: Leonard Thagard: $730,000 Cx reserve. Current Cx contract is $36,940.
Note on BK109: Leonard Thagard: Silver LEED Consulting & Certification.
Note on BL109: Leonard Thagard: 7500 for predicting energy and water use. 6000 for preliminary study for LEED Silver certification 10000 for potential energy and water conservation strategies.
Note on BJ111: Leonard Thagard: complicated fee structure due to multiple increases in scope and square footage of project.
Note on BK111: Leonard Thagard: complex due to multiple increases in scope and square footage
Note on BI112: Thagard, Leonard: delta is from B-1 less B-0 whole bldg LCCA.
Note on BJ112: Thagard, Leonard: No design contract. Estimated at 11% of construction cost.
Note on BK112: Thagard, Leonard: no design contract. Estimated at 0.5% of construction cost.
Note on BM112: Thagard, Leonard: estimated at 4% of construction costs until contract is written.
Note on J113: Thagard, Leonard: Approved for bids 06/06/2016.
Note on K113: Thagard, Leonard: Approved for bids 06/06/2016.
Note on BI113: Leonard Thagard: LED Lighting at $40,240 selected on LCCA. No other alternates selected for energy savings. Envelope improvements were not shown to reduce energy consumption.
Note on BJ114: Thagard, Leonard: Design contract is for two buildings and site work.
Note on BK114: Thagard, Leonard: Green Globes.
Note on BI116: Leonard Thagard: from page 89 of the energy model lcca report.
Note on BJ116: Leonard Thagard: contract not signed as of 09.02.14
Note on BK116: Leonard Thagard: from design contract: $43,200 for model and $10,100 for LEED
Note on BM116: Leonard Thagard: Cx reserve of $250,000
Note on T117: Leonard Thagard: Includes plug and process
Note on BM118: Leonard Thagard: Cx reserve. Design only Cx is for $44,680.
Note on K125: Thagard, Leonard: Phase one completion is 08/02/16,
Note on BK125: Leonard Thagard: Not LEED per meeting minutes 04.09.14.

## 16.17 Meter Data
2016/2017 Meter Data Summary
1 | ASU - Cone Residence Hall Renovation | [16 empty] | ASU - Cone Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 90183.92 | 75576.56 | 97576.4 | 83684.64 | 70809.12 | 57196 | 34628.4 | 60848.48 | 55911.6 | 67107.12 | 74650.32 | 51248 |  |  |  | 819420.56 | kwhs | 2796.6824 | MMbtu
| Steam (lbs) |  | 70907 | 87591 | 136808.8 | 139311.4 | 241918 | 150990.2 | 226902.4 | 146819.2 | 222731.4 | 121793.2 | 102606.6 | 73409.6 |  |  |  | 1721788.8 | lbs | 1721.7888 | MMbtu | 4518.4712 | MMbtu
| Water (gallons) |  | 146908 | 171372 | 218777 | 168072 | 159633 | 50000 | 112000 | 174000 | 155865 | 155975 | 94933 | 57452 |  |  |  | 1664987.0001 | gallons | 1664987.0001 | gallons
| Electricity Cost ($) |  | 7278.9497 | 6102.3156 | 7874.4201 | 6755.4264 | 5718.2861 | 4621.7522 | 2803.9183 | 5070.1961 | 4801.7408 | 5760.2983 | 6406.156 | 4402.4387 |  |  |  | 67595.8982 |  | 67595.8982
| Steam Costs ($) |  | 1489.2 | 1839.6 | 2873.28 | 2925.84 | 5080.8 | 3171.12 | 4765.44 | 3083.52 | 4677.84 | 2557.92 | 2154.96 | 1908.72 |  |  |  | 36528.24 |  | 36528.24
104124.1382
2 | UNCC - Prospector Hall Renovation Phase II | [16 empty] | UNCC - Prospector Hall Renovation Phase II
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water (MMBtu) | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | MMbtu
| Water Usage (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
0
3 | UNCC - Miltimore Residence Hall | [16 empty] | UNCC - Miltimore Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 0 | MMbtu
| Water Usage (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
[20 empty] | 0 |  |  | #REF!
4 | NCCU - Nursing Building | [16 empty] | NCCU - Nursing Building
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 101534 | 104360 | 88955 | 79901 | 57473 | 51047 | 53957 | 57291 | 60217 | 65740 | 68099 | 70935 |  |  |  | 859509 | kwhs | 2933.5042 | MMbtu
| Steam (lbs) | No data. | [15 empty] | 0 | lbs | 0 | MMbtu
| Natural Gas (Therms) |  | 39 | 41 | 47 | 39 | 40 | 47 | 51 | 48 | 51 | 44 | 46 | 50 |  |  |  | 543 | therms | 54.287 | MMbtu | 2987.7913 | MMbtu
| Water (CCF) |  | 29190 | 36174 | 26967 | 22047 | 20331 | 16553 | 16038 | 8982 | 5104 | 8580 | 8836 | 8359 |  |  |  | 207161 | CCF | 1549564.28 | gallons
| Electricity Cost ($) |  | 6315.67 | 6491.45 | 5533.22 | 4970.04 | 3637.17 | 3175.25 | 3356.26 | 3563.64 | 3745.65 | 4089.19 | 4235.93 | 4412.33 |  |  |  | 53525.8 |  | 53525.8
| Steam Costs ($) | No data. | [15 empty] | 0 |  | 0
| Natural Gas ( $) |  | 45.4 | 46.77 | 50.87 | 45.48 | 46.63 | 53.19 | 56.61 | 57.79 | 60.26 | 54.71 | 56.95 | 60.27 |  |  |  | 634.93 |  | 634.93
54160.73
5 | NCCU - Chidley Residence Hall | [16 empty] | NCCU - Chidley Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 147744 | 165784 | 358416 | 114416 | 80848 | 81512 | 115584 | 105168 | 109536 | 142384 | 133160 | 130944 |  |  |  | 1685496 | kwhs | 5752.5978 | MMbtu
| Steam (lbs) | No data. | [15 empty] | 0 | lbs | 0 | MMbtu
| Natural Gas (Therms) |  | 289 | 404 | 594 | 878 | 1277 | 1383 | 685 | 2155 | 2118 | 1658 | 1977 | 48 |  |  |  | 13466 | therms | 1346.2785 | MMbtu | 7098.8763 | MMbtu
| Water (CCF) |  | 36393 | 89259 | 91028 | 83333 | 77392 | 28849 | 86983 | 135056 | 119848 | 109228 | 78193 | 73540 |  |  |  | 1009102 | CCF | 7548082.96 | gallons
| Electricity Cost ($) |  | 9190.04 | 10312.18 | 22294.36 | 7179.16 | 5028.95 | 5070.25 | 7189.61 | 6541.71 | 6813.41 | 8856.64 | 8282.88 | 8145.04 |  |  |  | 104904.23 |  | 104904.23
| Steam Costs ($) | No data. | [15 empty] | 0 |  | 0
| Natural Gas ( $) |  | 216.39 | 295.03 | 418.92 | 597.94 | 870.45 | 985.72 | 522.2 | 1684.04 | 1657.57 | 1315.61 | 1582.56 | 58.61 |  |  |  | 10205.04 |  | 10205.04
115109.27
6 | UNC-CH - Loudermilk | [16 empty] | UNC-CH - Loudermilk
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 132497 | 190080 | 173794 | 197784 | 172425 | 169010 | 163677 | 151891 | 156752 | 144391 | 192321 | 147026 |  |  | 1991648 | kwhs | 6797.4946 | MMbtu
| Steam Usage (mlbs) |  |  | 638 | 567 | 660 | 408 | 407 | 721 | 581 | 356 | 474 | 383 | 468 | 477 |  |  | 6140 | mlbs | 7331.16 | MMbtu
| Chilled water (ton-hrs) |  |  | 181905 | 184835 | 155343 | 64925 | 14135 | 2139 | 2227 | 9867 | 14159 | 54300 | 87151 | 121876 |  |  | 892862 | ton-hrs | 10714.344 | MMbtu
| Natural Gas (therms) |  |  | 109 | 162 | 379 | 599 | 380 | 486 | 282 | 303 | 335 | 293 | 381 | 293 |  |  | 4002 | therms | 400.1045 | MMbtu | 25243.1031 | Mmbtu
| Water Usage (kgallons) |  |  | 107 | 201 | 278 | 234 | 215 | 140 | 161 | 131 | 151 | 107 | 122 | 69 |  |  | 1916 | kgallons | 1916000 | gallons
| Electricity Cost ($) |  |  | 9500.03 | 10416.38 | 11522.54 | 9374.96 | 9948.92 | 8484.3 | 8805.82 | 8186.92 | 9044.59 | 7999.26 | 9154.48 | 9644.91 |  |  | 112083.11 |  | 112083.11
| Steam Cost ($) |  |  | 7017.87 | 6236.89 | 7259.87 | 4487.92 | 4476.92 | 7930.86 | 6390.88 | 3915.93 | 5213.91 | 4212.92 | 5147.91 | 5245.04 |  |  | 67536.92 |  | 67536.92
| Chilled Water ($) |  |  | 16644.31 | 16912.4 | 14213.88 | 5940.64 | 1293.35 | 195.72 | 203.77 | 902.83 | 1295.55 | 4968.45 | 7974.32 | 11395.41 |  |  | 81940.63 |  | 81940.63
| Natural Gas ($) |  |  | 69.67 | 103.55 | 242.25 | 380.29 | 253.63 | 333.09 | 203.89 | 230.46 | 255.24 | 225.42 | 295.89 | 227.55 |  |  | 2820.93 |  | 2820.93
261560.66
7 | DACS - Davis Event Center | [16 empty] | DACS - Davis Event Center
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 46440 | 59080 | 67880 | 46840 | 36040 | 30840 | 33440 | 40120 | 41440 | 23400 | 50960 | 37800 |  |  |  | 514280 | kwhs | 1755.2376 | MMbtu
| Nat Gas (Therms) |  | 113 | 91 | 305 | 177 | 2117 | 1910 | 2421 | 3187 | 2779 | 174 | 197 | 142 |  |  |  | 13613 | therms | 1360.975 | MMbtu | 3116.2126 | Mmbtu
| Water Usage (gallons) |  | 21693.5 | 55355.8 | 87522.1 | 38898.6988 | 32914.2836 | 29174.0241 | 71064.9305 | 54607.7887 | 62088.3077 | 30670.1279 | 45631.1659 | 26181.8165 |  |  |  | 555802.5437 | gallons | 555802.5437 | gallons
| Electricity Cost ($) |  | 5015.84 | 5949.32 | 6783.01 | 4970.32 | 4030.41 | 3472.82 | 3666.52 | 4120.61 | 4210.38 | 3056.1 | 5015.35 | 4179.66 |  |  |  | 54470.34 |  | 54470.34
| Nat Gas Costs ($) |  | 89.73 | 75.67 | 212.99 | 132.92 | 1387.6 | 1273.49 | 1762.89 | 2308.67 | 2028.08 | 152.63 | 170.49 | 127.78 |  |  |  | 9722.94 |  | 9722.94
64193.28
8 | NCSU - Student Health Center Addition and Renovation | [16 empty] | NCSU - Student Health Center Addition and Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electric (kWh) |  |  | 56780 | 55389 | 56067 | 57167 | 56609 | 61875 | 56873 | 61004 | 57214 | 58426 | 56376 | 58950 |  |  | 692730 | kwhs | 2364.2875 | MMbtu
| Chilled Water (Dtherms) |  |  | 701.02 | 535.34 | 279.11 | 144.63 | 74.75 | 88.38 | 138.6 | 228.58 | 332.16 | 452.57 | 585.3 | 752.22 |  |  | 4312.66 | dthrms | 4312.66 | MMbtu
| Steam (1,000 lbs) |  |  | 248 | 433 | 477 | 516 | 420 | 432 | 566 | 570 | 499 | 502 | 484 | 483 |  |  | 5630 | 1000 lbs | 5630 | MMbtu | 12306.9475 | Mmbtu
| Water (CCF) |  |  | 49.476 | 53.1635 | 57.0876 | 51.1715 | 36.7692 | 41.3141 | 52.6771 | 61.2013 | 57.5034 | 45.05 | 37.5953 | 40.1266 |  |  | 583.1358 | CCF | 436185.5647 | gallons
| Electricity Cost ($) |  |  | 4939.86 | 4818.843 | 4877.829 | 4973.529 | 4924.983 | 5383.125 | 4947.951 | 5307.348 | 4977.618 | 5083.062 | 4904.712 | 4892.85 |  |  | 60031.71 |  | 60031.71
| Chilled Water Cost ($) |  |  | 9078.209 | 6932.653 | 3614.4745 | 1872.9585 | 968.0125 | 1144.521 | 1794.87 | 2960.111 | 4301.472 | 5860.7815 | 7579.635 | 9598.3272 |  |  | 55706.0252 |  | 55706.0252
| Steam Cost ($) |  |  | 2980.96 | 5204.66 | 5733.54 | 6202.32 | 5048.4 | 5192.64 | 6803.32 | 6851.4 | 5997.98 | 6034.04 | 5817.68 | 6670.23 |  |  | 68537.17 |  | 68537.17
184274.9052
9 | ECSU - Gilchrist Ed & Psych Bldg | [16 empty] | ECSU - Gilchrist Ed & Psych Bldg
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity Usage (KWhs) |  | 105600 | 103488 | 101952 | 76416 | 56064 | 53952 | 53760 | 57600 | 53951 | 63936 | 56832 | 76872 |  |  |  | 860423 | kwhs | 2936.6237 | MMbtu
| Water Usage (gallons) |  | 4236.25 | 4271 | 7092.43 | 9192.19 | 5542 | 2443.31 | 10161.6 | 6178.68 | 5091.22 | 6424.63 | 7074.19 | 5182.18 |  |  |  | 72889.68 | gallons | 72889.68 | gallons
| Electricity Cost ($) |  | 9189.16 | 8991.05 | 8993.77 | 7428.3 | 5775.37 | 5379.52 | 5367.51 | 5574.91 | 5379.52 | 5971.52 | 5658.66 | 7274.25 |  |  |  | 80983.54 |  | 80983.54
10 | UNCC - EPIC | [16 empty] | UNCC - EPIC
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled water (BTU*10^6) | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water (BTU*10^6) | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | MMbtu
| Water Usage (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water | [16 empty] | 0 |  | 0
| Hot Water | [16 empty] | 0 |  | 0
0
11 | DACS - SENC Ag Center | [16 empty] | DACS - SENC Ag Center
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 13600 | 16280 | 22560 | 11971 | 24720 | 22080 | 11060 | 16880 | 20140 | 1900 | 35420 | 21220 |  |  |  | 217831 | kwhs | 743.4572 | MMbtu
| Nat Gas (Therms) |  | 25 | 27 | 34 | 27 | 515 | 1125 | 1093 | 919 | 762 | 69 | 33 | 26 |  |  |  | 4655 | therms | 465.3889 | MMbtu | 1208.8461 | Mmbtu
| Water Usage (gallons) |  | 4790 | 2360 | 10000 | 10260 | 2930 | 9600 | 12330 | 1740 | 370 | 7420 | 4090 | 5100 |  |  |  | 70990 | gallons | 70990 | gallons
| Electricity Cost ($) |  | 2388.07 | 2637.87 | 3326.85 | 1624.82 | 3310.01 | 3086.48 | 1832.56 | 2524.59 | 2245.63 | 929.42 | 4356.75 | 3047.37 |  |  |  | 31310.42 |  | 31310.42
| Nat Gas Costs ($) |  | 40 | 41 | 46 | 41.31 | 429.89 | 965 | 936.43 | 790.76 | 627.81 | 77.85 | 48.75 | 43.29 |  |  |  | 4088.09 |  | 4088.09
35398.51
12 | MVA - NC State Veterans Home - Black Mountain | [16 empty] | MVA - NC State Veterans Home - Black Mountain
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 177800 | 186200 | 185800 | 177600 | 143747 | 153470 | 177613 | 148146 | 161500 | 149500 | 153253 | 193904 |  |  |  | 2008533 | kwhs | 6855.1231 | MMbtu
| Nat Gas (Therms) |  | 1947 | 1782 | 1852 | 1731 | 2073 | 2101 | 2195 | 2046 | 2170 | 2045 | 2199 | 1891 |  |  |  | 24032 | therms | 2402.6262 | MMbtu | 9257.7494 | Mmbtu
| Water Usage (CCF) |  | 394 | 394 | 419 | 419 | 419 | 500 | 504 | 428 | 438 | 422 | 358 | 435 |  |  |  | 5130 | CCF | 3837240 | gallons
| Electricity Cost ($) |  | 14147 | 14604 | 14512 | 13905.45 | 11441 | 11792 | 12827 | 10859.76 | 11848 | 10888 | 11228.29 | 13775 |  |  |  | 151827.5 |  | 151827.5
| Nat Gas Costs ($) |  | 1256.9 | 1154.7 | 1198 | 1142 | 1354 | 1356.71 | 1576 | 1490 | 1591 | 1523 | 1625 | 1407 |  |  |  | 16674.31 |  | 16674.31
168501.81
13 | PCC - Russell Classroom Building | [16 empty] | PCC - Russell Classroom Building
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Gas Usage (Therms) | [16 empty] | 0 | Therms | 0 | MMbtu | 0 | Mmbtu
| Water CCF | [16 empty] | 0 | CCF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Gas Cost ($) | [16 empty] | 0 |  | 0
0
14 | UNCG - Bailey Residence Hall Renovation | [16 empty] | UNCG - Bailey Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 19077 | 24682 | 25006 | 21386 | 24873 | 22911 | 21122 | 22868 | 26101 | 22533 | 22646 | 18070 |  |  |  | 271275 | kwhs | 925.8616 | MMbtu
| Steam Usage (lbs) |  | 5270 | 9860 | 13340 | 17520 | 43220 | 68250 | 74950 | 60780 | 54350 | 17190 | 9090 | 6360 |  |  |  | 380180 | lbs | 380.18 | MMbtu
| Chilled water (ton-hrs) |  | 22276 | 27099.3333 | 23967.3333 | 11504 | 10664.6667 | 7941 | 4767 | 4462 | 6798 | 7812 | 10861 | 12558 |  |  |  | 150710.3333 | ton-hrs | 1808.524 | MMbtu | 3114.5656 | Mmbtu
| Water (gallons) |  | 6700 | 51100 | 85600 | 67400 | 83000 | 48200 | 62200 | 86600 | 84200 | 77400 | 33700 | 14400 |  |  |  | 700500 | gallons | 700500 | gallons
| Electricity Cost ($) |  | 1329.6231 | 1691.6889 | 1663.991 | 1194.0055 | 1364.5018 | 1308.0226 | 1213.1635 | 1247.7806 | 1501.1923 | 1220.6933 | 1254.945 | 1119.712 |  |  |  | 16109.3196 |  | 16109.3196
| Steam Cost ($) |  | 41.1793 | 77.0451 | 104.2374 | 136.8995 | 337.7168 | 533.2987 | 585.6518 | 474.9288 | 424.6855 | 134.3209 | 71.0284 | 49.6964 |  |  |  | 2970.6885 |  | 2970.6885
| Chilled Water ($) | No data. | [15 empty] | 0 |  | 0
19080.0081
15 | UNCG - Coit Residence Hall Renovation | [16 empty] | UNCG - Coit Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 19440 | 25539.6667 | 26717.6667 | 20243 | 22933 | 21422 | 20113 | 21952 | 25056 | 21553 | 21798 | 17036 |  |  |  | 263803.3333 | kwhs | 900.3608 | MMbtu
| Steam Usage (lbs) | * | 4500 | 10190 | 10660 | 37200 | 28733.3333 | 54006.6667 | 63430 | 40763.3333 | 40293.3333 | 36110 | 6453.3333 | 4540 |  |  |  | 336880 | lbs | 336.88 | MMbtu
| Chilled water (ton-hrs) |  | 22627 | 29638 | 24518 | 15124 | 15778 | 14869 | 12368 | 13340 | 10425 | 11675 | 17875 | 18406 |  |  |  | 206643 | ton-hrs | 2479.716 | MMbtu | 3716.9568 | Mmbtu
| Water (gallons) |  | 49800 | 129100 | 267500 | 229900 | 282900 | 141700 | 44600 | 63500 | 62800 | 59100 | 29400 | 25200 |  |  |  | 1385500 | gallons | 1385500 | gallons
| Electricity Cost ($) |  | 1354.9234 | 1750.4728 | 1777.8916 | 1130.1905 | 1258.0759 | 1223.0134 | 1155.2106 | 1197.7995 | 1441.0894 | 1167.6032 | 1207.9524 | 1055.6399 |  |  |  | 15719.8626 |  | 15719.8626
| Steam Cost ($) |  | 35.1626 | No Data | 83.2962 | 290.6771 | 224.5194 | 422.0027 | 495.6357 | 318.5206 | 314.8481 | 282.1599 | 50.4257 | 35.4751 |  |  |  | 2552.723 |  | 2552.723
| Chilled Water ($) | No data. | [15 empty] | 0 |  | 0
|  | * Off reading / having the average of 3 similar buildings for the same month | [17 empty] | 18272.5856
16 | UNCG - Cotten Residence Hall Renovation | [16 empty] | UNCG - Cotten Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 19274 | 26563 | 28279 | 21878 | 24768 | 22791 | 20710 | 22501 | 24666 | 23585 | 22578 | 16574 |  |  |  | 274167 | kwhs | 935.732 | MMbtu
| Steam Usage (lbs) |  | 6680 | 17870 | 21720 | 15290 | 23904.4444 | 49258.8889 | 59590 | 34091.1111 | 35607.7778 | 23290 | 9260 | 6140 |  |  |  | 302702.2222 | lbs | 302.7022 | MMbtu
| Chilled water (ton-hrs) |  | 21484 | 25899 | 24306 | 12824 | 10780 | 7513 | 24748 | No Data | 10087 | 14413 | 14228 | 15570 |  |  |  | 181852 | ton-hrs | 2182.224 | MMbtu | 3420.6582 | Mmbtu
| Water (gallons) |  | 37100 | 117100 | 105500 | 94900 | 137600 | 91600 | 109100 | 93100 | 33100 | 57000 | 29000 | 1400 |  |  |  | 906500 | gallons | 906500 | gallons
| Electricity Cost ($) |  | 1343.3536 | 1820.6114 | 1881.7885 | 1221.4745 | 1358.7417 | 1301.1716 | 1189.4999 | 1227.7554 | 1418.6586 | 1277.6839 | 1251.1767 | 1027.012 |  |  |  | 16318.9277 |  | 16318.9277
| Steam Cost ($) |  | 52.1969 | 139.6344 | 169.7179 | 119.4745 | 186.7869 | 384.904 | 465.6303 | 266.3845 | 278.2356 | 181.9857 | 72.3567 | 47.9773 |  |  |  | 2365.2849 |  | 2365.2849
| Chilled Water ($) | No data. | [15 empty] | 0 |  | 0
|  | * Off reading / having the average of 3 similar buildings for the same month | [17 empty] | 18684.2126
17 | UNCG - Gray Residence Hall Renovation | [16 empty] | UNCG - Gray Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 19969 | 25374 | 26868 | 22056 | 25355 | 23119 | 21134 | 23134 | 26601 | 23753 | 24223 | 18849 |  |  |  | 280435 | kwhs | 957.1247 | MMbtu
| Steam Usage (lbs) |  | 2930 | 2840 | 10570 | 9710 | 25390 | 72570 | 75300 | 40940 | 49300 | 5340 | 1010 | 1120 |  |  |  | 297020 | lbs | 297.02 | MMbtu
| Chilled water (ton-hrs) |  | 22717 | 25761 | 23078 | 6564 | 5436 | 4947 | 5318 | 7817 | 9341 | 14442 | 16173 | 18973 |  |  |  | 160567 | ton-hrs | 1926.804 | MMbtu | 3180.9487 | Mmbtu
| Water (gallons) |  | 39400 | 75400 | 120000 | 112000 | 143900 | 129900 | 66800 | 57200 | 55400 | 53900 | 24100 | 9400 |  |  |  | 887400 | gallons | 887400 | gallons
| Electricity Cost ($) |  | 1391.7935 | 1739.1181 | 1787.8953 | 1231.4124 | 1390.9438 | 1319.8976 | 1213.8528 | 1262.2947 | 1529.9497 | 1286.7851 | 1342.3356 | 1167.9829 |  |  |  | 16664.2615 |  | 16664.2615
| Steam Cost ($) |  | 22.8947 | 22.1915 | 82.5929 | 75.873 | 198.3949 | 567.0547 | 588.3867 | 319.9011 | 385.2253 | 41.7262 | 7.892 | 8.7516 |  |  |  | 2320.8846 |  | 2320.8846
| Chilled Water ($) | No data. | [15 empty] | 0 |  | 0
18985.146
18 | UNCG - Hinshaw Residence Hall Renovation | [16 empty] | UNCG - Hinshaw Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 23243 | 31723 | 33831 | 26694 | 28058 | 28507 | 25550 | 27252 | 31964 | 28723 | 28894 | 23949 |  |  |  | 338388 | kwhs | 1154.9182 | MMbtu
| Deduct site lighting (KWhs) |  | 2841 | 2732 | 3101 | 3253 | 3928 | 3929 | 3878 | 3480 | 3040 | 2912 | 2644 | 2330 |  |  |  | 38068 | kwhs | 129.9261 | MMbtu
| Steam Usage (lbs) |  | 4960 | 5800 | 12680 | 15600 | 17590 | 21200 | 40040 | 20570 | 17230 | 13660 | 8500 | 2820 |  |  |  | 180650 | lbs | 180.65 | MMbtu
| Chilled water (ton-hrs) |  | 20598 | 26776 | 23608 | 11831 | 7988 | 5522 | 5299 | 7236 | 9076 | 14531 | 15171 | 18926 |  |  |  | 166562 | ton-hrs | 1998.744 | MMbtu | 3204.3862 | Mmbtu
| Water (gallons) |  | 16600 | 73500 | 104600 | 82700 | 122500 | 79200 | 57700 | 57400 | 56500 | 57300 | 41400 | 45500 |  |  |  | 794900 | gallons | 794900 | gallons
| Electricity Cost ($) |  | 1619.9838 | 2174.2746 | 2251.2389 | 1490.3574 | 1539.227 | 1627.5064 | 1467.4902 | 1486.9913 | 1838.4012 | 1556.0278 | 1601.1825 | 1484.0057 |  |  |  | 20136.6868 |  | 20136.6868
| Steam Cost ($) |  | 38.7569 | 45.3206 | 99.0803 | 121.8968 | 137.4465 | 165.6547 | 312.8686 | 160.7319 | 134.6335 | 106.7379 | 66.4181 | 22.0352 |  |  |  | 1411.581 |  | 1411.581
| Chilled Water ($) | No data. | [15 empty] | 0 |  | 0
21548.2678
19 | UNCG - Jamison Residence Hall Renovation | [16 empty] | UNCG - Jamison Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 17705 | 24833 | 26199 | 21474 | 25185 | 23084 | 21405 | 23213 | 26551 | 23018 | 23962 | 17281 |  |  |  | 273910 | kwhs | 934.8548 | MMbtu
| Steam Usage (lbs) |  | 4856.6667 | 8836.6667 | 14990 | 13533.3333 | 22294.8148 | 12760 | 10570 | 10270 | 6060 | 14096.6667 | 6256.6667 | 3360 |  |  |  | 127884.8148 | lbs | 127.8848 | MMbtu
| Chilled water (ton-hrs) |  | 20598 | 26776 | 23608 | 11831 | 7988 | 5522 | 5299 | 7236 | 9076 | 14531 | 15171 | 18926 |  |  |  | 166562 | ton-hrs | 1998.744 | MMbtu | 3061.4836 | Mmbtu
| Water (gallons) |  | 29000 | 78100 | 127200 | 94000 | 115200 | 101600 | 104200 | 105300 | 87900 | 59100 | 24900 | 2600 |  |  |  | 929100 | gallons | 929100 | gallons
| Electricity Cost ($) |  | 1233.9979 | 1702.0383 | 1743.3776 | 1198.9187 | 1381.6178 | 1317.8994 | 1229.4179 | 1266.6053 | 1527.0739 | 1246.9675 | 1327.8721 | 1070.8214 |  |  |  | 16246.6078 |  | 16246.6078
| Steam Cost ($) |  | 37.9495 | 69.0488 | 117.1304 | 105.7481 | 174.2095 | 99.7054 | 82.5929 | 80.2488 | 47.3522 | 110.1499 | 48.889 | 26.2547 |  |  |  | 999.2792 |  | 999.2792
| Chilled Water ($) | No data. | [15 empty] | 0 |  | 0
17245.887
20 | UNCG - Shaw Residence Hall Renovation | [16 empty] | UNCG - Shaw Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 39688 | 48238 | 48931 | 41121 | 47838 | 45675 | 41273 | 43974 | 50831 | 43055 | 45402 | 37916 |  |  |  | 533942 | kwhs | 1822.344 | MMbtu
| Steam Usage (lbs) |  | 13120 | 19970 | 25310 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | 28310 | Note 1 |  |  |  | 86710 | lbs | 86.71 | MMbtu
| Chilled water (ton-hrs) |  | 63820 | 69292 | 53151 | 31771 | 33290 | 32079 | 26360 | 28987 | 34651 | 34799 | 38465 | 43457 |  |  |  | 490122 | ton-hrs | 5881.464 | MMbtu | 7790.518 | Mmbtu
| Water (gallons) |  | 40600 | 119600 | 211600 | 214000 | 207500 | 111700 | 78300 | 80500 | 77500 | 75900 | 33900 | 18500 |  |  |  | 1269600 | gallons | 1269600 | gallons
| Electricity Cost ($) |  | 2766.1625 | 3306.2024 | 3256.0484 | 2295.8338 | 2624.3332 | 2607.6527 | 2370.5567 | 2399.4185 | 2923.5319 | 2332.4435 | 2515.9857 | 2349.4743 |  |  |  | 31747.6435 |  | 31747.6435
| Steam Cost ($) |  | 102.5184 | 156.0436 | 197.7698 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | 221.2115 | Note 1 |  |  |  | 677.5433 |  | 677.5433
| Chilled Water ($) | No data. | [15 empty] | 0 |  | 0
|  |  | Note 1: Inaccurate Steam Meter | [16 empty] | 32425.1868
21 | WCU - Harrill Residence Hall Renovation | [16 empty] | WCU - Harrill Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 61294 | 78216 | 83548 | 74633 | 72643 | 58499 | 73775 | 69477 | 73343 | 68334 | 52440 | 48997 |  |  |  | 815199 | kwhs | 2782.2742 | MMbtu
| Water (CCF) |  | 40.4786 | 148.5462 | 276.7328 | 233.086 | 236.0136 | 172.9162 | 219.7714 | 245.9461 | 211.8709 | 194.3319 | 62.9102 | 9.4111 |  |  |  | 2052.0152 | CCF | 1534907.3992 | gallons
| Electricity Cost ($) |  | 4433.6402 | 5719.9361 | 5815.275 | 4091.9035 | 4017.0853 | 3308.0015 | 4097.9061 | 3944.3482 | 4127.084 | 3802.8554 | 3112.0518 | 3561.4939 |  |  |  | 50031.581 |  | 50031.581
23 | FSU - Renaissance Residence Hall | [16 empty] | FSU - Renaissance Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
22 | UNCP Health Science Builidng | [16 empty] | UNCP Health Science Builidng
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 0 | MMBtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
0
24 | UNCA - Overlook Residence Hall | [16 empty] | UNCA - Overlook Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 1535525 | kwhs | 5240.7468 | MMbtu
| Water (CCF) | [16 empty] | 3951 | CCF | 2955348 | gallons
| Electricity Cost ($) | [16 empty] | 118312 |  | 118312
25 | ECSU - Viking Tower Residence Hall | [16 empty] | ECSU - Viking Tower Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity Usage (KWhs) |  | 40760 | 28119 | 58731 | 58222 | 56170 | 49151 | 53036 | 49265 | 52527 | 54793 | 48155 | 46501 |  |  |  | 595430 | kwhs | 2032.2026 | MMbtu
| Water (gallons) |  | 251089 | 496833 | 713301 | 156426 | 156426 | 332819 | 310871 | 332819 | 310871 | 316938 | 265914 | 229491 |  |  |  | 3873798 | gallons | 3873798 | gallons
| Electricity Cost ($) |  | 3680.63 | 2539.11 | 6025.8 | 5315.67 | 5178.86 | 4482.53 | 4815.69 | 4675.21 | 4795.72 | 4597.1 | 4468.76 | 4106 |  |  |  | 54681.08 |  | 54681.08
26 | UNCW - Teaching Lab | [16 empty] | UNCW Teaching Lab
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 69426 | 81658 | 90743 | 73005 | 101317 | 81558 | 106084 | 71258 | 107855 | 73703 | 75575 | 85670 |  |  |  | 1017852 | kwhs | 3473.9289 | MMbtu
| Heating Hot Water Usage (Mbtu) | [16 empty] | 0 | Mbtu | 0 | MMbtu
| Chilled water (ton-hrs) | [16 empty] | 0 | ton-hrs | 0 | MMbtu | 3473.9289 | MMbtu
| Water Usage (gallons) |  | 24840 | 45591 | 67564 | 50486 | 66784 | 23455 | 64719 | 51895 | 76540 | 76102 | 73498 | 49816 |  |  |  | 671290 | gallons | 671290 | gallons
| Electricity Cost ($) |  | 5595.74 | 6622.46 | 7105.18 | 5577.58 | 7406.27 | 5692.75 | 7256.15 | 4817.04 | 7301.78 | 5019.17 | 5358.27 | 6185.37 |  |  |  | 73937.76 |  | 73937.76
| Heating Hot Water (Gas $) |  | 2029.02 | 2046.76 | 2466.12 | 2550.69 | 3619.84 | 3622.22 | 4729.75 | 2381.03 | 3262.48 | 2140.16 | 2557.75 | 2890.63 |  |  |  | 34296.45 |  | 34296.45
| Chilled Water (Electric $) |  | 3320.36 | 3523.53 | 2983.44 | 2862.49 | 2378.34 | 1460.77 | 1968.23 | 1587.55 | 1831.34 | 2778.89 | 3555.53 | 5591.35 |  |  |  | 33841.82 |  | 33841.82
142076.03
27 | UNCA - Rhoades Hall Renovation | [16 empty] | UNCA - Rhoades Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 343680 | kwhs | 1172.9798 | MMbtu
| Water (CCF) | [16 empty] | 1409 | CCF | 1053932 | gallons
| Electricity Cost ($) | [16 empty] | 26480 |  | 26480
26480
28 | ECU - Ross Hall | [16 empty] | ECU - Ross Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 227631.31 | 231203.8 | 225802.7 | 224452.68 | 212062.71 | 201626.22 | 204314.04 | 189981.17 | 221699.66 | 206590.89 | 218031.41 | 215938.68 |  |  |  | 2579335.27 | kwhs | 8803.2713 | MMbtu
| Chilled water (ton-hrs) |  | 170787 | 190439 | 154143 | 91735 | 44754 | 27373 | 25083 | 33364 | 44943 | 80069 | 109605 | 140893 |  |  |  | 1113188 | ton-hrs | 13358.256 | MMbtu
| Natural Gas (CCF) |  | 1619 | 2286 | 2495 | 6096 | 5052 | 6423 | 7157 | 5764 | 7718 | 4029 | 3545 | 2500 |  |  |  | 54684 | CCF | 5635.0041 | MMbtu | 27796.5314 | MMbtu
| Water Usage (gallons) | No data. | [15 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) |  | 19974.6475 | 20288.1334 | 19814.1869 | 19695.7227 | 18608.5028 | 17692.7008 | 17928.557 | 16670.8477 | 19454.1452 | 18128.3506 | 19132.2562 | 18948.6192 |  |  |  | 226336.6699 |  | 226336.6699
| Chilled Water ($) |  | 9415.4873 | 10498.9021 | 8497.9036 | 5057.3506 | 2467.288 | 1509.0735 | 1382.8258 | 1839.3573 | 2477.7076 | 4414.204 | 6042.5237 | 7767.4311 |  |  |  | 61370.0544 |  | 61370.0544
| Nat Gas Costs ($) |  | 1433.45 | 1915.36 | 2079.61 | 4922.9 | 4408.44 | 5572.56 | 6206.22 | 5256.81 | 6998.61 | 3710.23 | 3278.79 | 2312.2638 |  |  |  | 48095.2438 |  | 48095.2438
287706.7244
29 | GC - Lena Sue Beam Renovation | [16 empty] | GC - Lena Sue Beam Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 23240 | 26680 | 28640 | 24480 | 24600 | 23400 | 19920 | 22720 | 21640 | 30880 | 28080 | 23160 |  |  | 297440 | kwhs | 1015.1627 | MMbtu
| Steam (lbs) |  |  | 0 | 0 | 0 | 146300 | 251550 | 130650 | 117700 | 86750 | 30100 | 1550 | 500 | 0 |  |  | 765100 | lbs | 765.1 | MMbtu
| Chilled water (dtherms) |  |  | 107 | 87 | 129 | 170 | 34 | 88 | 56 | 91 | 103 | 207 | 221 | 333 |  |  | 1626 | dtherm | 1625.6118 | MMbtu | 3405.8745 | MMbtu
| Water (gallons) |  |  | 19775 | 12756 | 11815 | 10801 | 6589 | 8199 | 5742 | 6154 | 9329 | 10700 | 2737 | 1726 |  |  | 106323 | gallons | 106323 | gallons
| Electricity Cost ($) |  |  | 1998.6738 | 2139.2879 | 1932.5045 | 1804.0006 | 1787.858 | 1590.3275 | 1531.0812 | 1568.6143 | 1505.1 | 3952.5862 | 2235.787 | 2061.0835 |  |  | 24106.9047 |  | 24106.9047
| Steam Cost ($) |  |  | 0 | 0 | 0 | 1461.07 | 2527.86 | 1487.07 | 1354.42 | 1037.45 | 428.85 | 103.28 | 91.3 | 0 |  |  | 8491.3 |  | 8491.3
| Chilled Water ($) |  |  | 859.21 | 698.61 | 1035.87 | 1365.1 | 273.02 | 706.64 | 449.68 | 730.73 | 827.09 | 1662.21 | 1774.63 | 2673.99 |  |  | 13056.78 |  | 13056.78
45654.9847
30 | NCSU - Hunt Library | [16 empty] | NCSU - Hunt Library
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (kWh) |  |  | 389879.8828 | 371120.1172 | 376119.1406 | 355480.4688 | 348480.4688 | 351609.375 | 321339.8438 | 359160.1562 | 351919.9219 | 363299.8047 | 345959.9609 | 358800.7812 |  |  | 4293169.9219 | kwh | 14652.5889 | MMbtu
| Chilled Water (Dtherms) |  |  | 1498.92 | 1163.152 | 647.624 | 311.992 | 148.496 | 192.608 | 278.592 | 313.104 | 650.4 | 814.8 | 1041.696 | 1385.104 |  |  | 8446.488 | dthrms | 8446.488 | MMbtu
| Steam (1,000 lbs) |  |  | 273.3802 | 277.0636 | 316.54 | 465.3086 | 697.3902 | 723.3824 | 436.3228 | 168.8075 | 325.2032 | 302.7122 | 274.89 | 279.6381 |  |  | 4540.6387 | 1000 lbs | 4540.6387 | MMbtu | 27639.7157 | MMbtu
| Water (CCF) |  |  | 41 | 137 | 171 | 150 | 123 | 61 | 42 | 39 | 38 | 30 | 29 | 39 |  |  | 900 | CCF | 673200 | gallons
| Electricity Cost ($) |  |  | 33919.5498 | 32287.4502 | 32722.3652 | 30926.8008 | 30317.8008 | 30590.0156 | 27956.5664 | 31246.9336 | 30617.0332 | 31607.083 | 30098.5166 | 29780.4648 |  |  | 372070.5801 |  | 372070.5801
| Chilled Water Cost ($) |  |  | 19411.014 | 15062.8184 | 8386.7308 | 4040.2964 | 1923.0232 | 2494.2736 | 3607.7664 | 4054.6968 | 8422.68 | 10551.66 | 13489.9632 | 17673.927 |  |  | 109118.8498 |  | 109118.8498
| Steam Cost ($) |  |  | 3286.0299 | 3330.3046 | 3804.8108 | 5593.0093 | 8382.6302 | 8695.0565 | 5244.6 | 2029.0655 | 3908.9425 | 3638.6006 | 3304.1778 | 3861.8022 |  |  | 55079.0299 |  | 55079.0299
536268.4599
31 | MVA - NC State Veterans Home - Kinston | [16 empty] | MVA - NC State Veterans Home - Kinston
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | 186400 | 228400 | 267200 | 259600 | 238600 | 185782 | 192800 | 164800 | 154000 | 187200 | 197200 | 205800 |  |  |  |  | 2467782 | kwhs | 8422.54 | MMbtu
| Nat Gas (Therms) | 1881 | 1541 | 1580 | 1726 | 1589 | 1727 | 1956 | 1816 | 1896 | 1771 | 1800 | 1664 |  |  |  |  | 20947 | therms | 2094.1999 | MMbtu | 10516.7398 | MMBtu
| Water Usage (gallons) | 318000 | 313300 | 287700 | 256200 | 271400 | 237900 | 264900 | 287500 | 243600 | 257300 | 253100 | 298800 |  |  |  |  | 3289700 | gallons | 3289700 | gallons
| Electricity Cost ($) | 16067.44 | 19309.93 | 22503.72 | 21965.9 | 20274.3 | 15431.87 | 15300.75 | 13473.58 | 12739.07 | 15124.01 | 16073.57 | 16367.9 |  |  |  |  | 204632.04 |  | 204632.04
| Nat Gas Costs ($) | 1402.88 | 1155.31 | 1183.96 | 1291.18 | 1190.55 | 1158.24 | 1741.61 | 1650.18 | 1720.6 | 1608.72 | 1573.33 | 1464.82 |  |  |  |  | 17141.38 |  | 17141.38
221773.42
32 | UNCC - Rose Football Center | [16 empty] | UNCC - Rose Football Center
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 0 | Mmbtu
| Water Usage (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
0
33 | RCC - Continuing Education Industrial Center | [16 empty] | RCC - Continuing Education Industrial Center
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 86300 | 76900 | 84500 | 70100 | 57800 | 52900 | 53100 | 53300 | 54700 | 70500 | 62000 | 72100 |  |  |  | 794200 | kwhs | 2710.6046 | MMbtu
| Nat Gas (Therms) |  | 465 | 577 | 513 | 695 | 1109 | 1311 | 1615 | 1156 | 1435 | 874 | 569 | 389 |  |  |  | 10708 | therms | 1070.5443 | MMbtu | 3781.1489 | MMbtu
| Water Usage (CF) |  | 184 | 27 | 3 | 146 | 10 | 0 | 0 | 150 | 215 | 209 | 142 | 152 |  |  |  | 1238 | CF | 9260.24 | gallons
| Electricity Cost ($) |  | 7593.88 | 6961.75 | 7542.38 | 6271.92 | 5303.76 | 4844.6 | 4404.47 | 4527.84 | 4586.82 | 5538.05 | 5392.25 | 6258.65 |  |  |  | 69226.37 |  | 69226.37
| Nat Gas Costs ($) |  | 365.05 | 447.31 | 400.31 | 561.36 | 973.34 | 1198.98 | 1469.09 | 1058.25 | 1247.97 | 780.55 | 517.38 | 364.34 |  |  |  | 9383.93 |  | 9383.93
78610.3
34 | ASU - Plemmons Student Union Addition | [16 empty] | ASU - Plemmons Student Union Addition
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 124302.36 | 136673.48 | 154241.2 | 154193.12 | 150620.96 | 124908 | 100757.2 | 142079.84 | 126422.8 | 146194.96 | 153701.56 | 92243 |  |  |  | 1606338.48 | kwhs | 5482.4332 | MMbtu
| Steam (lbs) |  | 292804.2 | 311990.8 | 263607.2 | 227736.5992 | 376224.2 | 459644.2 | 623981.6 | 372887.4 | 511364.6 | 386234.6 | 488007 | 330343.1992 |  |  |  | 4644825.5983 | lbs | 4644.8256 | MMbtu | 10127.2588 | MMbtu
| Water (gallons) |  | 347964.0001 | 386276 | 446391 | 292376 | 228639 | 69000 | 128000 | 213000 | 208295 | 298425.0001 | 287539 | 287916 |  |  |  | 3193821.0004 | gallons | 3193821.0004 | gallons
| Elecricity Cost ($) |  | 10055.6008 | 11052.1161 | 12467.197 | 12463.3377 | 12175.592 | 10104.3948 | 8159.0232 | 11847.9085 | 10867.3251 | 12560.2146 | 13202.9423 | 7940.8564 |  |  |  | 132896.5084 |  | 132896.5084
| Steam Costs ($) |  | 6149.52 | 6552.48 | 5536.32 | 4782.96 | 7901.52 | 9653.52 | 13104.96 | 7831.44 | 10739.76 | 8111.76 | 10249.2 | 8589.24 |  |  |  | 99202.68 |  | 99202.68
232099.1884
35 | ASU - Summit Residence Hall and Appalachian Hall | [16 empty] | ASU - Summit Residence Hall and Appalachian Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 86886.72 | 100976.96 | 121742.4 | 106562.24 | 94529.92 | 77896 | 67854.4 | 83151.68 | 77425.6 | 91417.92 | 88109.12 | 79328 |  |  |  | 1075880.96 | kwhs | 3671.9817 | MMbtu
| Steam (lbs) |  | 221897.2 | 250260 | 302814.6 | 260270.4 | 444628.6 | 537224.8 | 506359.4 | 471323 | 412929 | 266944 | 260270.4 | 253596.8 |  |  |  | 4188518.2 | lbs | 4188.5182 | MMbtu | 7860.4999 | MMbtu
| Water (gallons) |  | 117128 | 239352 | 362832 | 265552 | 246728 | 75000 | 173000 | 270000 | 245840 | 263600 | 157528 | 90632 |  |  |  | 2507192.0001 | gallons | 2507192.0001 | gallons
| Elecricity Cost ($) |  | 7028.1895 | 8163.1882 | 9835.853 | 8613.0759 | 7643.8719 | 6303.993 | 5495.1385 | 6938.1154 | 6658.6142 | 7856.6571 | 7573.3617 | 6821.5049 |  |  |  | 88931.5634 |  | 88931.5634
| Steam Costs ($) |  | 5426 | 6119.55 | 7404.66 | 6364.33 | 10872.4 | 13136.64 | 12381.89 | 11525.15 | 10097.26 | 6527.52 | 6364.33 | 7278.68 |  |  |  | 103498.41 |  | 103498.41
192429.9734
36 | UNCW - MARBIONC | [16 empty] | UNCW - MARBIONC
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 442200 | 397800 | 355800 | 275600 | 224600 | 246800 | 246800 | 214800 | 234600 | 276200 | 290200 | 384000 |  |  |  | 3589400 | kwhs | 12250.6222 | MMbtu
| Nat Gas (MCF) |  | 585.5 | 702.6 | 604.3 | 821.2 | 906 | 1117.1 | 1192.9 | 870.2 | 972 | 686.9 | 817.9 | 399 |  |  |  | 9675.6 | MCF | 9936.8412 | MMbtu | 22187.4634 | MMbtu
| Water Usage (CF) | No Meter | [15 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) |  | 30515.3 | 28286.59 | 25406.57 | 19075.83 | 15034.82 | 14797.45 | 14797.45 | 13593.9 | 14025.56 | 17104.86 | 18062.83 | 24481.15 |  |  |  | 235182.31 |  | 235182.31
| Nat Gas Costs ($) |  | 4061.98 | 4838.99 | 4197.25 | 5492.28 | 7641.91 | 9725.28 | 10328.96 | 7613.44 | 7878.41 | 5752.69 | 6796.48 | 3443.57 |  |  |  | 77771.24 |  | 77771.24 |  |  | MCF=1000CF
[20 empty] | 312953.55 |  |  | 1 cubic foot = 1,025 Btu
37 | DOA - NC State Bar HQ | [16 empty] | DOA - NC State Bar HQ
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 69200 | 71200 | 69400 | 79000 | 68200 | 94200 | 73400 | 81800 | 75000 | 72000 | 39200 | 102800 |  |  | 895400 | kwhs | 3056.0002 | MMbtu
| Water Usage (CCF) |  |  | 22 | 18 | 19 | 18 | 18 | 13 | 19 | 27 | 18 | 19 | 18 | 21 |  |  | 230 | CCF | 172040 | gallons
| Elecricity Cost ($) |  |  | 6227.6 | 6398.76 | 6359.65 | 6998.26 | 6082.92 | 7699.57 | 6181.56 | 6752.66 | 6325.78 | 6050.78 | 3773.09 | 8097.79 |  |  | 76948.42 |  | 76948.42
76948.42
38 | FSU - Science and Technology Building | [16 empty] | FSU - Science and Technology Building
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
39 | UNCW - Student Rec Facility Addition | [16 empty] | UNCW - Student Rec Facility Addition
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 135000 | 165000 | 179000 | 131000 | 158000 | 110000 | 153000 | 109000 | 154000 | 127000 | 134000 | 165000 |  |  |  | 1720000 | kwhs | 5870.36 | MMbtu
| Nat Gas (MCF) |  | 13 | 16 | 21 | 19 | 20 | 12 | 24 | 19 | 24 | 20 | 15 | 18 |  |  |  | 221 | MCF | 226.967 | MMbtu
| Heating Hot Water Usage (Mbtu) | No data | [15 empty] | 0 | Mbtu | 0 | MMbtu
| Chilled water (ton-hrs) | No data | [15 empty] | 0 | ton-hrs | 0 | MMbtu | 6097.327 | MMbtu
| Water Usage (gallons) | Incomplete data | 0 | 0 | 0 | 210600 | 93400 | 34100 | 131400 | 116000 | 148310 | 85290 | 71900 | 84900 |  |  |  | 975900 | gallons | 975900 | gallons
| Electricity Cost ($) |  | 10881 | 13381.5 | 14015.7 | 10008.4 | 11549.8 | 7678 | 10465.2 | 7368.4 | 10425.8 | 8648.7 | 9500.6 | 11913 |  |  |  | 125836.1 |  | 125836.1
| Nat Gas Costs ($) |  | 66.69 | 78.24 | 102.69 | 95.19 | 101 | 69.48 | 155.04 | 114.38 | 124.08 | 110 | 82.8 | 102.78 |  |  |  | 1202.37 |  | 1202.37 |  |  | MCF=1000CF
| Heating Hot Water ($) |  | 1648.58 | 1662.99 | 2003.73 | 2072.44 | 2941.12 | 2943.06 | 3842.92 | 1934.59 | 2650.76 | 1738.88 | 2078.17 | 2348.64 |  |  |  | 27865.88 |  | 27865.88
| Chilled Water ($) |  | 2697.79 | 2862.87 | 2424.05 | 2325.78 | 1932.4 | 1186.88 | 1599.19 | 1289.89 | 1487.97 | 2257.85 | 2888.87 | 4542.97 |  |  |  | 27496.51 |  | 27496.51
[20 empty] | 182400.86 |  |  | 1 cubic foot = 1,025 Btu
40 | WSSU - Reaves Student Activities Center | [16 empty] | WSSU - Reaves Student Activities Center
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 70789 | 90642 | 103653 | 106555 | 107163 | 90691 | 126671 | 75986 | 102972 | 100858 | 66790 | 61469 |  |  |  | 1104239 | kwhs | 3768.7677 | MMbtu
| Steam (Nat Gas in therms) |  | 0 | 0 | 0 | 0 | 0 | 9691.6796 | 9112.5576 | 7083.3684 | 7814.0575 | 5964.9739 | 0 | 0 |  |  |  | 39666.6371 | therms | 3965.7166 | MMbtu
| Chilled water (kwh) |  | 133783.6185 | 147811.3378 | 119652.9365 | 67415.1099 | 57316.9478 | 53033.1632 | 64641.8173 | 43003.3451 | 88241.4945 | 143721.8646 | 93238.2009 | 77154.5777 |  |  |  | 1089014.4139 | kwhs | 3716.8062 | MMbtu
| Nat Gas (Therms) |  | 1344 | 2163 | 2692 | 2679 | 3195 | 1314 | 874 | 827 | 783 | 2276 | 1834 | 1135 |  |  |  | 21116 | therms | 2111.0958 | MMbtu | 9845.5802 | Mmbtu
| Water (CCF) |  | 19.02 | 328.73 | 328.73 | 364.26 | 19.39 | 689.84 | 353.88 | 411.87 | 284.27 | 193.1 | 207.25 | 180.96 |  |  |  | 3381.3 | CCF | 2529212.4 | gallons
| Electricity Cost ($) |  | 5037.617 | 6450.4327 | 7376.3454 | 7582.8628 | 7626.1304 | 6453.9197 | 9014.3946 | 5407.4554 | 7327.8828 | 7177.4424 | 4753.0328 | 4374.37 |  |  |  | 78581.886 |  | 78581.886
| Steam Costs ($ Natural Gas) |  | 0 | 0 | 0 | 0 | 0 | 5540.6226 | 3951.6975 | 3750.1011 | 3182.6599 | 1587.1031 | 0 | 0 |  |  |  | 18012.1844 |  | 18012.1844
| Chilled water ($) |  | 9520.5558 | 10518.8222 | 8514.9623 | 4797.518 | 4078.894 | 3774.0435 | 4600.1599 | 3060.2831 | 6279.6035 | 10227.7996 | 6635.1883 | 5490.6159 |  |  |  | 77498.446 |  | 77498.446
| Nat Gas Costs ($) |  | 944.51 | 1506.66 | 1869.76 | 1945.33 | 2557.42 | 1123.22 | 753.12 | 713.8 | 644.51 | 1864.4 | 1506.6 | 951.29 |  |  |  | 16380.62 |  | 16380.62
190473.1364
41 | HCC - Creative Arts Building | [16 empty] | HCC - Creative Arts Building
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 27521 | 27735.53 | 20205 | 19726.83 | 16030.75 | 16441.895 | 18656.95 | 20884.188 | 22695.627 | 22662.143 | 21777.506 | 25951.064 |  |  | 260288.483 | kwhs | 888.3646 | MMbtu
| Nat Gas (therms) |  |  | 39 | 3 | 231 | 443 | 1612 | 1890 | 1376 | 1616 | 862 | 668 | 136 | 73 |  |  | 8949 | therms | 894.6863 | MMbtu | 1783.0509 | MMbtu
| Water Usage (CCF) |  |  | 2851 | 3109.74 | 1253.96 | 1083.29 | 373 | 567 | 3979 | 1159.79 | 1353.27 | 1630.825 | 1490.858 | 1881.7473 |  |  | 20733.4803 | CCF | 155086.4326 | gallons
| Elecricity Cost ($) |  |  | 2752 | 2773.553 | 2020.5 | 1972.68 | 1603.075 | 1644 | 1865.695 | 2088.4188 | 2269.56 | 2266.2143 | 2177.75 | 2595.11 |  |  | 26028.5561 |  | 26028.5561
| Nat Gas Costs ($) |  |  | 45.4 | 20.78 | 177.94 | 333.27 | 1141.4 | 1394 | 1091.72 | 1276.32 | 708.51 | 564.83 | 131.74 | 79.38 |  |  | 6965.29 |  | 6965.29
32993.8461
42 | UNCC - Belk Residence Hall | [16 empty] | UNCC - Belk Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
0
43 | NCSU - Cherry Building Renovation | [16 empty] | NCSU - Cherry Building Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 38320.0073 | 31811.0352 | 26853.0273 | 25903.9307 | 25402.9541 | 26928.1006 | 23670.8984 | 26217.041 | 25682.9834 | 28046.0205 | 26443.9697 | 30530.0293 |  |  | 335809.9976 | kwhs | 1146.1195 | MMbtu
| Nat Gas (Therms) |  |  | 99 | 181 | 264 | 731 | 1648 | 740 | 592 | 530 | 228 | 231 | 143 | 120 |  |  | 5507 | therms | 550.5685 | MMbtu | 1696.688 | Mmbtu
| Water (CCF) |  |  | 3.2 | 10.9 | 10.3 | 11 | 6.9 | 6.1 | 9.3 | 31.2 | 9.5 | 9.5 | 2.5 | 1.2 |  |  | 111.6 | CCF | 83476.8 | gallons
| Electricity Cost ($) |  |  | 3333.8406 | 2767.5601 | 2336.2134 | 2253.642 | 2210.057 | 2342.7448 | 2059.3682 | 2280.8826 | 2234.4196 | 2440.0038 | 2300.6254 | 2533.9924 |  |  | 29093.3497 |  | 29093.3497
| Nat Gas Costs ($) |  |  | 86.43 | 143.35 | 205.45 | 542.45 | 1210.1 | 608.15 | 496.23 | 452.59 | 208.19 | 210.68 | 137.56 | 118.44 |  |  | 4419.62 |  | 4419.62
33512.9697
44 | UNCC - Hunt Residence Hall | [16 empty] | UNCC - Hunt Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water (MMBtu) | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water (MMBtu) | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | MMbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0
45 | NCSU - Wolf Ridge at Centennial Bldg 6 - Lakeview Hall | [16 empty] | NCSU - Wolf Ridge 6 - Lakeview
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 36934.021 | 37820.9839 | 37377.9907 | 34983.0322 | 33385.0098 | 35828.0029 | 33076.9653 | 34573.9746 | 34918.0908 | 30459.9609 | 27027.9541 | 28284.0576 |  |  | 404670.0439 | kwhs | 1381.1389 | MMbtu
| Steam (1000lbs) |  |  | 108.1001 | 121.6302 | 165.3901 | 222.8598 | 285.8099 | 275.3096 | 266.2003 | 253.69 | 190.5697 | 158.2203 | 130.3501 | 129.51 |  |  | 2307.6401 | 1000lbs | 2307.6401 | MMbtu
| Chilled Water (Dtherms) |  |  | 444 | 391 | 291 | 226 | 202 | 196 | 196 | 218 | 281 | 291 | 320 | 386 |  |  | 3442 | dtherms | 3441.1782 | MMbtu | 7129.9572 | Mmbtu
| Water (CCF) |  |  | 56 | 97 | 90 | 89 | 59 | 66 | 87 | 79 | 85 | 51 | 20 | 22 |  |  | 801 | CCF | 599148 | gallons
| Electricity Cost ($) |  |  | 3213.2598 | 3290.4256 | 3251.8852 | 3043.5238 | 2904.4958 | 3117.0363 | 2877.696 | 3007.9358 | 3037.8739 | 2650.0166 | 2351.432 | 2347.5768 |  |  | 35093.1576 |  | 35093.1576
| Steam Costs ($) |  |  | 1299.3632 | 1461.9951 | 1987.9888 | 2678.7745 | 3435.4352 | 3309.221 | 3199.7278 | 3049.3544 | 2290.6481 | 1901.8079 | 1566.8087 | 1788.5324 |  |  | 27969.6572 |  | 27969.6572
| Chilled Water ($) |  |  | 5749.8 | 5063.45 | 3768.45 | 2926.7 | 2615.9 | 2538.2 | 2538.2 | 2823.1 | 3638.95 | 3768.45 | 4144 | 4925.36 |  |  | 44500.56 |  | 44500.56
107563.3747
46 | NCSU - Wolf Ridge at Centennial Bldg 1 - Tower Hall | [16 empty] | NCSU - Wolf Ridge 1 - Tower
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 142992.9199 | 143932.0068 | 142215.0269 | 134521.1182 | 124160.0342 | 137486.8164 | 128972.0459 | 139423.8892 | 138697.1436 | 131389.1602 | 121522.8271 | 128257.2021 |  |  | 1613570.1904 | kwhs | 5507.1151 | MMbtu
| Steam (1000lbs) |  |  | 162.8252 | 193.5514 | 301.3916 | 462.0068 | 580.332 | 551.7521 | 371.1479 | 423.6618 | 218.5204 | 201.6684 | 175.6435 | 144.4152 |  |  | 3786.9164 | 1000lbs | 3786.9164 | MMbtu
| Chilled water (Dtherms) |  |  | 1197.9766 | 958.9805 | 490.6992 | 235.0762 | 134.0469 | 145.0405 | 200.8418 | 227.7051 | 513.4692 | 629.501 | 831.2666 | 1107.5645 |  |  | 6672.168 | dtherms | 6670.575 | MMbtu
| Natural Gas (thms) |  |  | 956 | 1240 | 1441 | 1149 | 1184 | 695 | 1111 | 1251 | 1012 | 1348 | 914 | 761 |  |  | 13062 | therms | 1305.8881 | MMbtu | 15964.6064 | Mmbtu
| Water (CCF) |  |  | 250 | 460 | 450 | 455 | 290 | 315 | 480 | 420 | 455 | 235 | 75 | 80 |  |  | 3965 | CCF | 2965820 | gallons
| Electricity Cost ($) |  |  | 12440.384 | 12522.0846 | 12372.7073 | 11703.3373 | 10801.923 | 11961.353 | 11220.568 | 12129.8784 | 12066.6515 | 11430.8569 | 10572.486 | 10645.3478 |  |  | 139867.5778 |  | 139867.5778
| Steam Costs ($) |  |  | 1957.1587 | 2326.4877 | 3622.7269 | 5553.3218 | 6975.5908 | 6632.0608 | 4461.198 | 5092.4153 | 2626.6152 | 2424.0538 | 2111.2351 | 1994.3739 |  |  | 45777.238 |  | 45777.238
| Chilled Water ($) |  |  | 15513.7965 | 12418.7971 | 6354.5549 | 3044.2364 | 1735.907 | 1878.2748 | 2600.9013 | 2948.7808 | 6649.4266 | 8152.0376 | 10764.9025 | 14132.5224 |  |  | 86194.1379 |  | 86194.1379
| Natural Gas ($) |  |  | 643.12 | 819.01 | 945.49 | 777.17 | 850.43 | 523.06 | 890.23 | 997 | 817.59 | 1093.52 | 756.09 | 637.14 |  |  | 9749.85 |  | 9749.85
271838.9537
47 | UNCG - Spartan Village 1 - Lee | [16 empty] | UNCG - Spartan Village 1 - Lee
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 52947 | 62731 | 89755 | 64121 | 61865 | 77423 | 80723 | 67610 | 71297 | 67750 | 54725 | 44235 |  |  |  | 795182 | kwhs | 2713.9562 | MMbtu
| Nat Gas (Therms) |  | 143 | 166 | 414 | 481 | 582 | 579 | 385 | 693 | 633 | 698 | 522 | 132 |  |  |  | 5428 | therms | 542.6704 | MMbtu | 3256.6266 | Mmbtu
| Water (gallons) |  | 12716.884 | 65080.524 | 136145.464 | 207210.404 | 162327.284 | 184768.844 | 69568.836 | 181776.636 | 199729.884 | 185516.896 | 184020.792 | 24685.716 |  |  |  | 1613548.164 | gallons | 1613548.164 | gallons
| Electricity Cost ($) |  | 4985.53 | 5586.64 | 7013.41 | 5456.15 | 5325.55 | 5849.65 | 6323.85 | 5023 | 5420.92 | 4671.94 | 4136.38 | 3357.39 |  |  |  | 63150.41 |  | 63150.41
| Nat Gas Costs ($) |  | 128.56 | 145.46 | 327.6 | 380.08 | 420.41 | 531.77 | 373.82 | 643.83 | 590.13 | 622.72 | 475.67 | 138.5 |  |  |  | 4778.55 |  | 4778.55
67928.96
48 | UNCG - Spartan Village 3 - Haywood | [16 empty] | UNCG - Spartan Village 3 - Haywood
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 38381 | 42563 | 55986 | 39727 | 48595 | 53348 | 60364 | 49556 | 51700 | 47402 | 34815 | 29429 |  |  |  | 551866 | kwhs | 1883.5187 | MMbtu
| Nat Gas (Therms) |  | 83 | 92 | 187 | 228 | 284 | 298 | 201 | 369 | 323 | 382 | 302 | 101 |  |  |  | 2850 | therms | 284.932 | MMbtu | 2168.4506 | Mmbtu
| Water (gallons) |  | 12716.884 | 26929.872 | 156342.868 | 280519.5 | 249849.368 | 256581.836 | 195241.572 | 228903.912 | 253589.628 | 248353.264 | 235636.38 | 78545.46 |  |  |  | 2223210.544 | gallons | 2223210.544 | gallons
| Electricity Cost ($) |  | 3380.33 | 3637.76 | 4317.57 | 3330.67 | 4140.78 | 4119.22 | 4526.77 | 3722.68 | 3827.45 | 3331.68 | 2610.71 | 2230.32 |  |  |  | 43175.94 |  | 43175.94
| Nat Gas Costs ($) |  | 84.5 | 91.11 | 160.87 | 192.61 | 212.64 | 285.09 | 206.48 | 353.83 | 312.65 | 351.45 | 285.12 | 111.5 |  |  |  | 2647.85 |  | 2647.85
45823.79
49 | UNCG - Spartan Village 4 - Union | [16 empty] | UNCG - Spartan Village 4 - Union
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 43939 | 50401 | 73790 | 53290 | 54502 | 59046 | 62444 | 53789 | 54926 | 54353 | 43429 | 35593 |  |  |  | 639502 | kwhs | 2182.6203 | MMbtu
| Nat Gas (Therms) |  | 127 | 145 | 348 | 421 | 516 | 509 | 358 | 604 | 568 | 609 | 453 | 121 |  |  |  | 4779 | therms | 477.7859 | MMbtu | 2660.4062 | Mmbtu
| Water (gallons) |  | 13464.936 | 8228.572 | 176540.272 | 348592.232 | 290244.176 | 293984.436 | 175792.22 | 235636.38 | 200000 | 223667.548 | 308945.476 | 175044.168 |  |  |  | 2450140.416 | gallons | 2450140.416 | gallons
| Electricity Cost ($) |  | 4017.39 | 4414.69 | 5659.56 | 4412.58 | 4680.93 | 4374.92 | 4645.67 | 3997.57 | 4010.86 | 3744.26 | 3237.39 | 2694.88 |  |  |  | 49890.7 |  | 49890.7
| Nat Gas Costs ($) |  | 116.81 | 130.04 | 279.12 | 335.53 | 378.6 | 470.43 | 349 | 564.17 | 531.94 | 546.32 | 415.91 | 128.92 |  |  |  | 4246.79 |  | 4246.79
54137.49
50 | WSSU - Martin-Schexnider Residence Hall | [16 empty] | WSSU - Martin-Schexnider Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 22904 | 37807 | 41696 | 40968 | 38386 | 30267 | 46534 | 29068 | 36510 | 39913 | 23149 | 20963 |  |  |  | 408165 | kwhs | 1393.0671 | MMbtu
| Steam (Nat Gas in Therms) |  | 2251.6474 | 2144.8256 | 2506.0695 | 4199.5044 | 4670.3493 | 5628.5628 | 5292.2305 | 4113.7538 | 4538.1105 | 3464.2323 | 1683.5309 | 2042.0461 |  |  |  | 42534.8632 | therms | 4252.4708 | MMbtu
| Chilled Water (kwh) |  | 77696.4906 | 85843.262 | 69489.9223 | 39152.1586 | 33287.5261 | 30799.6653 | 37541.5346 | 24974.7244 | 51247.339 | 83468.2499 | 54149.238 | 44808.475 |  |  |  | 632458.5856 | kwhs | 2158.5812 | MMbtu | 7804.1191 | Mmbtu
| Water (CCF) |  | 143.48 | 510.775 | 510.78 | 604.97 | 787.16 | 296.82 | 642.41 | 1002.16 | 889.53 | 1178.67 | 633.14 | 246.55 |  |  |  | 7446.445 | CCF | 5569940.86 | gallons
| Electricity Cost ($) |  | 1629.9366 | 2690.4912 | 2967.2474 | 2915.4401 | 2731.6951 | 2153.9159 | 3311.5381 | 2068.5905 | 2598.1917 | 2840.3623 | 1647.3717 | 1491.8075 |  |  |  | 29046.5882 |  | 29046.5882
| Steam ($) |  | 1138.3255 | 1033.54 | 1244.1054 | 2083.0927 | 2141.6032 | 3025.9494 | 3217.7851 | 2294.9972 | 2177.9176 | 1848.3691 | 921.7298 | 1130.5024 |  |  |  | 22257.9175 |  | 22257.9175
| Chilled Water($) |  | 5529.1805 | 6108.936 | 4945.1696 | 2786.2179 | 2368.8681 | 2191.8224 | 2671.5997 | 1777.2973 | 3646.9574 | 5939.9211 | 3853.4676 | 3188.7431 |  |  |  | 45008.1807 |  | 45008.1807
96312.6864
51 | CFCC - Union Station | [16 empty] | CFCC - Union Station
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | 358325 | 412600 | 387225 | 391450 | 295050 | 267125 | 267975 | 275475 | 251800 | 251725 | 273475 | 285200 |  |  |  |  | 3717425 | kwhs | 12687.5715 | MMbtu
| Nat Gas (Therms) | 9294 | 9173 | 8819 | 11968 | 10121 | 15102 | 17226 | 17322 | 12271 | 9636 | 8277 | 8289 |  |  |  |  | 137498 | therms | 13746.5172 | MMbtu | 26434.0887 | MMbtu
| Water (1000 gallons) | 382 | 563 | 564 | 469 | 469 | 208 | 208 | 184 | 185 | 161 | 162 | 356 |  |  |  |  | 3911 | 1000 Gal | 3911000 | gallons
| Electricity Cost ($) | 25594.84 | 28494.25 | 27845.44 | 27784.41 | 20819.04 | 18751.48 | 17034.76 | 16432.48 | 15820.07 | 15903.67 | 17080.63 | 17983.59 |  |  |  |  | 249544.66 |  | 249544.66
| Nat Gas Costs ($) | 6157.23 | 6080.16 | 5853.21 | 7872.04 | 5003.6 | 12127.73 | 14433.17 | 14483.77 | 10335.53 | 7589.69 | 6592.82 | 6603.32 |  |  |  |  | 103132.27 |  | 103132.27
352676.93
52 | ECU - Smith-Williams Center | [16 empty] | ECU - Smith-Williams Center
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 38470 | 37733 | 40115 | 34543 | 33747 | 39909 | 39879 | 27881 | 38890 | 35070 | 24385 | 38838 |  |  |  | 429460 | kwhs | 1465.747 | MMbtu
| Hot Water (MMBtu) | No data | [15 empty] | 0 | lbs | 0 | MMbtu
| Chilled Water (ton-hrs) |  | 26921 | 26100 | 20524 | 13417 | 5214 | 5387 | 6074 | 7813 | 6248 | 16100 | 16920 | 14100 |  |  |  | 164818 | ton-hrs | 1977.816 | MMbtu | 3443.563 | MMbtu
| Water (gallons) | No data | [15 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) |  | 3375.7425 | 3311.0707 | 3520.0912 | 3031.1482 | 2961.2993 | 3502.0147 | 3499.3822 | 2446.5577 | 3412.5975 | 3077.3925 | 2139.7838 | 3408.0345 |  |  |  | 37685.115 |  | 37685.115
| Hot Water ($) | No data | [15 empty] | 0 |  | 0
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
37685.115
53 | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 44531.9824 | 51126.9531 | 50754.0283 | 45870.9717 | 41633.0566 | 45049.9268 | 40887.085 | 42773.9258 | 46723.999 | 38963.9893 | 33222.0459 | 35352.0508 |  |  | 516890.0146 | kwhs | 1764.1456 | MMbtu
| Steam (1000lbs) |  |  | 75.52 | 74.8204 | 133.7395 | 191.3306 | 259.5297 | 255.5003 | 175.7297 | 187.8799 | 101.5598 | 77.0104 | 60.3602 | 64.4398 |  |  | 1657.4203 | 1000lbs | 1657.4203 | MMbtu
| Chilled Water (Dtherms) |  |  | 615.8252 | 475.4399 | 325.6602 | 215.3662 | 149.8545 | 149.8066 | 157.9375 | 168.042 | 279.0283 | 296.7139 | 369.2588 | 503.9785 |  |  | 3706.9116 | dtherms | 3706.0266 | MMbtu | 7127.5925 | Mmbtu
| Water (CCF) |  |  | 95 | 176 | 145 | 147 | 87 | 94 | 122 | 105 | 117 | 65 | 19 | 22 |  |  | 1194 | CCF | 893112 | gallons
| Electricity Cost ($) |  |  | 3874.2825 | 4448.0449 | 4415.6005 | 3990.7745 | 3622.0759 | 3919.3436 | 3557.1764 | 3721.3315 | 4064.9879 | 3389.8671 | 2890.318 | 2934.2202 |  |  | 44828.0231 |  | 44828.0231
| Steam Costs ($) |  |  | 907.7504 | 899.3406 | 1607.549 | 2299.7933 | 3119.5473 | 3071.1135 | 2112.2706 | 2258.3168 | 1220.7489 | 925.6654 | 725.5295 | 889.9137 |  |  | 20037.5391 |  | 20037.5391
| Chilled Water ($) |  |  | 7974.9363 | 6156.9472 | 4217.299 | 2788.9924 | 1940.6157 | 1939.996 | 2045.2906 | 2176.1438 | 3613.4167 | 3842.4446 | 4781.9013 | 6430.7659 |  |  | 47908.7496 |  | 47908.7496
112774.3118
54 | UNCG - Spartan Village Building 2 - Highland | [16 empty] | UNCG - Spartan Village Building 2 - Highland
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 78871 | 71264 | 95727 | 68240 | 65326 | 73775 | 78216 | 68943 | 72435 | 70192 | 56867 | 45785 |  |  |  | 845641 | kwhs | 2886.1727 | MMbtu
| Nat Gas (Therms) |  | 262 | 176 | 298 | 377 | 482 | 504 | 326 | 617 | 563 | 581 | 418 | 67 |  |  |  | 4671 | therms | 466.9885 | MMbtu | 3353.1612 | Mmbtu
| Water (gallons) |  | 150358.452 | 119688.32 | 150358.452 | 249849.368 | 167563.648 | 185516.896 | 80041.564 | 173548.064 | 188509.104 | 169807.804 | 169059.752 | 18701.3 |  |  |  | 1823002.724 | gallons | 1823002.724 | gallons
| Electricity Cost ($) |  | 6609.37 | 6148.93 | 7393.57 | 5735.35 | 5622.78 | 6003 | 6301.18 | 5745.8 | 5945.03 | 4837.19 | 4218.07 | 3500.23 |  |  |  | 68060.5 |  | 68060.5
| Nat Gas Costs ($) |  | 215.96 | 152.8 | 242.4 | 302.84 | 342.66 | 465.71 | 320.29 | 575.8 | 527.47 | 522.28 | 385.6 | 81.9 |  |  |  | 4135.71 |  | 4135.71
72196.21
55 | UNCC - PORTAL | [16 empty] | UNCC - PORTAL
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0
56 | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 47737.0605 | 48851.9287 | 48113.0371 | 44437.0117 | 40192.0166 | 44413.9404 | 41614.0137 | 43414.0625 | 45354.0039 | 38745.9717 | 33611.9385 | 35868.042 |  |  | 512353.0273 | kwhs | 1748.6609 | MMbtu
| Steam (1000lbs) |  |  | 37.7999 | 43.7102 | 52.6697 | 135.8205 | 225.0798 | 225.2698 | 146.3698 | 157.9397 | 74.5011 | 52.6597 | 36.8696 | 28.0003 |  |  | 1216.6902 | 1000lbs | 1216.6902 | MMbtu
| Chilled Water (Dtherms) |  |  | 477.0869 | 348.4141 | 160.1011 | 70.7358 | 39.1782 | 53.2642 | 72.9277 | 82.647 | 188.9062 | 212.5229 | 278.1338 | 382.1572 |  |  | 2366.0752 | dtherms | 2365.5103 | MMbtu | 5330.8613 | Mmbtu
| Water (CCF) |  |  | 75 | 135 | 127 | 121 | 80 | 81 | 113 | 105 | 117 | 70 | 25 | 28 |  |  | 1077 | CCF | 805596 | gallons
| Electricity Cost ($) |  |  | 4153.1243 | 4250.1178 | 4185.8342 | 3866.02 | 3496.7054 | 3864.0128 | 3620.4192 | 3777.0234 | 3945.7983 | 3370.8995 | 2924.2386 | 2977.0475 |  |  | 44431.2412 |  | 44431.2412
| Steam Costs ($) |  |  | 6178.2755 | 4511.9621 | 2073.3089 | 916.0291 | 507.358 | 689.7709 | 944.4142 | 1070.2783 | 2446.3359 | 2752.1722 | 3601.8326 | 4876.3262 |  |  | 30568.0639 |  | 30568.0639
| Chilled Water ($) |  |  | 454.3552 | 525.3967 | 633.0897 | 1632.5629 | 2705.4593 | 2707.7425 | 1759.3649 | 1898.4353 | 895.5035 | 632.9697 | 443.173 | 386.6835 |  |  | 14674.7364 |  | 14674.7364
89674.0415
57 | WSSU - Hill Hall Renovation | [16 empty] | WSSU - Hill Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 36532 | 44984 | 48514 | 49316 | 43061 | 43530 | 53204 | 34654 | 48669 | 51793 | 17160 | 48868 |  |  |  | 520285 | kwhs | 1775.7327 | MMbtu
| Steam (Nat Gas in therms) |  | 1534.0477 | 1461.2699 | 1707.3854 | 2861.1228 | 3181.9095 | 3834.7404 | 3605.5972 | 2802.7009 | 3091.8152 | 2360.1819 | 1146.9898 | 1391.2463 |  |  |  | 28979.007 | therms | 2897.2088 | MMbtu
| Chilled Water (kwh) |  | 52934.6277 | 58485.0239 | 47343.4918 | 26674.37 | 22678.7952 | 20983.8154 | 25577.0517 | 17015.2825 | 34914.8178 | 56866.9279 | 36891.8819 | 30528.019 |  |  |  | 430894.1049 | kwhs | 1470.6416 | MMbtu | 6143.5831 | Mmbtu
| Water (CCF) |  | 10.9 | 24.05 | 24.05 | 25 | 24.5 | 6.3 | 18.8 | 27.6 | 16.9 | 18.5 | 9.8 | 7.2 |  |  |  | 213.6 | CCF | 159772.8 | gallons
| Electricity Cost ($) |  | 2599.7574 | 3201.2341 | 3452.4425 | 3509.5159 | 3064.3861 | 3097.7619 | 3786.2009 | 2466.1117 | 3463.4729 | 3685.7887 | 1221.1715 | 3477.6345 |  |  |  | 37025.4778 |  | 37025.4778
| Steam ($) |  | 775.5413 | 704.1509 | 847.6092 | 1419.2113 | 1459.0745 | 2061.5796 | 2192.2773 | 1563.5819 | 1483.8155 | 1259.2941 | 627.9746 | 770.2114 |  |  |  | 15164.3216 |  | 15164.3216
| Chilled Water ($) |  | 3767.0313 | 4162.0188 | 3369.1446 | 1898.2506 | 1613.9101 | 1493.2889 | 1820.1612 | 1210.8728 | 2484.6725 | 4046.8689 | 2625.3679 | 2172.491 |  |  |  | 30664.0786 |  | 30664.0786
82853.878
58 | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 33242.0044 | 37013.0005 | 37297.9736 | 35138.0005 | 31933.0444 | 32115.9668 | 33400.0244 | 34113.9526 | 36401.001 | 32186.0352 | 28921.9971 | 28945.9839 |  |  | 400708.9844 | kwhs | 1367.6198 | MMbtu
| Steam (1000lbs) |  |  | 45.59 | 52.26 | 79.4701 | 131.4097 | 190.9903 | 160.5796 | 128.2406 | 127.8392 | 70.0408 | 57.2795 | 45.4902 | 42.55 |  |  | 1131.74 | 1000lbs | 1131.74 | MMbtu
| Chilled Water (Dtherms) |  |  | 312.1362 | 271.3101 | 131.5796 | 62.5332 | 37.3799 | 39.79 | 57.541 | 67.498 | 151.6182 | 177.2759 | 240.0439 | 323.9009 |  |  | 1872.6069 | dtherms | 1872.1598 | MMbtu | 4371.5196 | Mmbtu
| Water (CCF) |  |  | 48 | 94 | 87 | 81 | 53 | 58 | 77 | 74 | 82 | 53 | 28 | 26 |  |  | 761 | CCF | 569228 | gallons
| Electricity Cost ($) |  |  | 2892.0544 | 3220.131 | 3244.9237 | 3057.006 | 2778.1749 | 2794.0891 | 2905.8021 | 2967.9139 | 3166.8871 | 2800.1851 | 2516.2137 | 2402.5167 |  |  | 34745.8977 |  | 34745.8977
| Steam Costs ($) |  |  | 547.992 | 628.1648 | 955.2304 | 1579.5442 | 2295.7038 | 1930.1666 | 1541.4525 | 1536.6276 | 841.8908 | 688.4994 | 546.7919 | 587.6157 |  |  | 13679.6797 |  | 13679.6797
| Chilled Water ($) |  |  | 4042.1642 | 3513.4653 | 1703.9557 | 809.805 | 484.0695 | 515.281 | 745.1562 | 874.0997 | 1963.4552 | 2295.7226 | 3108.5691 | 4132.9752 |  |  | 24188.7186 |  | 24188.7186
72614.296
59 | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 35022.995 | 31261.0016 | 31486.9995 | 32717.9871 | 30886.0168 | 31885.9863 | 27928.009 | 33164.0015 | 32671.9971 | 35393.0054 | 32484.9854 | 33314.0259 |  |  | 388217.0105 | kwhs | 1324.9847 | MMbtu
| Steam (1000lbs) |  |  | 36.17 | 37.0602 | 63.3096 | 115.83 | 180.1999 | 141.3499 | 103.3603 | 50.58 | 66.9002 | 59.5697 | 47.9603 | 44.8899 |  |  | 947.18 | 1000lbs | 947.18 | MMbtu
| Chilled Water (Dtherms) |  |  | 383.1421 | 244.333 | 101.498 | 36.834 | 23.3931 | 25.9316 | 42.4722 | 56.8818 | 118.1631 | 178.1411 | 251.377 | 360.3721 |  |  | 1822.5391 | dtherms | 1822.1039 | MMbtu | 4094.2685 | Mmbtu
| Water (CCF) |  |  | 33 | 24 | 15 | 12 | 13 | 15 | 12 | 20 | 29 | 35 | 22 | 25 |  |  | 255 | CCF | 190740 | gallons
| Electricity Cost ($) |  |  | 3047.0006 | 2719.7071 | 2739.369 | 2846.4649 | 2687.0835 | 2774.0808 | 2429.7368 | 2885.2681 | 2842.4637 | 3079.1915 | 2826.1937 | 2765.0641 |  |  | 33641.6238 |  | 33641.6238
| Steam Costs ($) |  |  | 434.7632 | 445.4639 | 760.981 | 1392.2768 | 2166.0032 | 1699.0257 | 1242.3903 | 607.972 | 804.1407 | 716.0274 | 576.483 | 619.9289 |  |  | 11465.4561 |  | 11465.4561
| Chilled Water ($) |  |  | 4961.6901 | 3164.1125 | 1314.3997 | 477.0001 | 302.9402 | 335.8147 | 550.0146 | 736.6198 | 1530.212 | 2306.9274 | 3255.3315 | 4598.3476 |  |  | 23533.4102 |  | 23533.4102
68640.49
60 | Guilford Technical Community College - Aviation Center III Building | [16 empty] | Guilford Technical Community College - Aviation Center III Building
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 36789 | 48745 | 49769 | 36478 | 27694 | 29813 | 24353 | 26324 | 25217 | 30467 | 31050 | 34929 |  |  |  | 401628 | kwhs | 1370.7564 | MMbtu
| Nat Gas (Therms) |  | 123 | 149 | 209 | 412 | 845 | 941 | 1367 | 683 | 944 | 482 | 428 | 245 |  |  |  | 6828 | therms | 682.637 | MMbtu | 2053.3933 | Mmbtu
| Water (gallons) |  | 2992 | 4488 | 3740 | 3740 | 3740 | 1496 | 5236 | 3740 | 5236 | 2244 | 2244 | 2992 |  |  |  | 41888 | gallons | 41888 | gallons
| Electricity Cost ($) |  | 3332.3 | 4151.88 | 4104.22 | 3048.37 | 2434.91 | 2545.69 | 2091.54 | 2248.39 | 2231.02 | 2556.94 | 2678.71 | 2953.76 |  |  |  | 34377.73 |  | 34377.73
| Nat Gas Costs ($) |  | 113.14 | 132.24 | 177.04 | 244.66 | 745.97 | 866.35 | 1247.11 | 635.77 | 829.16 | 441.02 | 395.02 | 238.18 |  |  |  | 6065.66 |  | 6065.66
40443.39
61 | UNCC - Martin Residence Hall | [16 empty] | UNCC - Martin Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
0
62 | UNCSA - New Library Building | [16 empty] | UNCSA - New Library Building
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
0
63 | NCAT - Student Health Center | [16 empty] | NCAT - Student Health Center
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 38354 | 36013 | 30552 | 24645 | 20004 | 19960 | 17068 | 18478 | 19754 | 24347 | 25448 | 28029 |  |  |  | 302652 | kwhs | 1032.9513 | MMbtu
| Nat Gas (Therms) |  | 804 | 856 | 477 | 185 | 660 | 1335 | 1278 | 988 | 1307 | 1195 | 1007 | 1043 |  |  |  | 11135 | therms | 1113.2341 | MMbtu | 2146.1854 | Mmbtu
| Water (CCF) |  | 11 | 13 | 13 | 15 | 14 | 12 | 11 | 15 | 11 | 14 | 14 | 12 |  |  |  | 155 | CCF | 115940 | gallons
| Electricity Cost ($) |  | 2763.55 | 2559.53 | 2113.44 | 1508.53 | 1130.82 | 1165.46 | 996.55 | 1053.79 | 1240.7 | 1412.01 | 1474.84 | 1838.68 |  |  |  | 19257.9 |  | 19257.9
| Nat Gas Costs ($) |  | 573.86 | 609.55 | 349.41 | 148.98 | 520.28 | 1110.19 | 1092.13 | 848.48 | 1115.33 | 980.96 | 857.16 | 871.3 |  |  |  | 9077.63 |  | 9077.63
28335.53
64 | UNCG - Campus Police Facility | [16 empty] | UNCG - Campus Police Facility
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 51957 | 55238 | 53913 | 37459 | 29984 | 28341 | 33966 | 28457 | 31311 | 37191 | 37503 | 45351 |  |  |  | 470671 | kwhs | 1606.4001 | MMbtu
| Nat Gas (Therms) |  | 375 | 298 | 270 | 410 | 736 | 1036 | 1672 | 1057 | 938 | 955 | 563 | 413 |  |  |  | 8723 | therms | 872.0917 | MMbtu | 2478.4919 | Mmbtu
| Water (gallons) |  | 9724.676 | 9724.676 | 6732.468 | 8976.624 | 5984.416 | 6732.468 | 6732.468 | 7480.52 | 8228.572 | 8228.572 | 6732.468 | 6732.468 |  |  |  | 92010.396 | gallons | 92010.396 | gallons
| Electricity Cost ($) |  | 4065.9718 | 4273.7967 | 4045.1559 | 3002.8622 | 2519.4901 | 2026.1696 | 1875.5295 | 1625.9667 | 1821.221 | 2111.0845 | 2162.2793 | 3292.7663 |  |  |  | 32822.2936 |  | 32822.2936
| Nat Gas Costs ($) |  | 298.96 | 242.4 | 221.84 | 326.88 | 479.59 | 930.21 | 1530.93 | 969.63 | 863.13 | 843.33 | 511.18 | 383.24 |  |  |  | 7601.32 |  | 7601.32
40423.6136
65 | UNCC - South Village Dining Facility | [16 empty] | UNCC - South Village Dining Facility
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0
66 | UNCG - Moran Commons (Dining Hall Renovation) | [16 empty] | UNCG - Dining Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 216777 | 319608 | 258955 | 251121 | 280913 | 242911 | 234010 | 224198 | 268037 | 250006 | 231619 | 239556 |  |  |  | 3017711 | kwhs | 10299.4476 | MMbtu
| Nat Gas (Therms) |  | 2029 | 1603 | 4667 | 5030 | 4692 | 3907 | 1124 | 4649 | 3727 | 4693 | 3835 | 1088 |  |  |  | 41044 | therms | 4103.4201 | MMbtu
| Chilled Water (ton-hrs) |  | 344459.4698 | 354704.8135 | 276951.1771 | 186594.8427 | 155201.2427 | 103429.1 | 119861.7125 | 134074.7813 | 157555.9917 | 191209.3385 | 182287.6865 | 216474.7177 |  |  |  | 2422804.874 | ton-hrs | 29073.6585 | MMbtu
| Steam Usage (lbs) |  | 1026165 | 1005300.5 | 1136883.25 | 1189969.25 | 1473502 | 1629467.5 | 1795423 | 1486412.5 | 1819200.75 | 1267029.75 | 853718 | 821074.5 |  |  |  | 15504146 | lbs | 16133.3465 | MMbtu | 59609.8727 | Mmbtu
| Water (gallons) |  | 280238.2 | 425357.68 | 514339.76 | 472870.64 | 504264.2 | 270439.4 | 382564.6 | 439988.56 | 467118.52 | 486080.32 | 247722.64 | 261014.6 |  |  |  | 4751999.12 | gallons | 4751999.12 | gallons
| Electricity Cost ($) |  | 15108.8595 | 21905.7328 | 17231.8162 | 14020.3807 | 15410.5378 | 13868.1452 | 13440.6021 | 12233.2476 | 15416.0789 | 13543.7202 | 12835.3395 | 14844.1466 |  |  |  | 179858.6072 |  | 179858.6072
| Nat Gas Costs ($) |  | 1513.72 | 1200.84 | 3451.16 | 3752.27 | 3290.46 | 3464.04 | 1065.24 | 4184.75 | 3359.49 | 4053.19 | 3345.24 | 971.5 |  |  |  | 33651.9 |  | 33651.9
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
| Steam ($) | No data | [15 empty] | 0 |  | 0
213510.5072
67 | WSSU - Center for Design Innovation | [16 empty] | WSSU - Center for Design Innovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 31878 | 35999 | 27423 | 26620 | 32395 | 38651 | 42743 | 32682 | 37539 | 32116 | 31687 | 36849 |  |  |  | 406582 | kwhs | 1387.6644 | MMbtu | 1387.6644 | Mmbtu
| Water (CCF) |  | 1.8 | 0.4 | 0.4 | 0.85 | 0.85 | 0.6 | 0.69 | 0.8 | 0.61 | 0.66 | 0.74 | 0.63 |  |  |  | 9.03 | CCF | 6754.44 | gallons
| Electricity Cost ($) |  | 3962.44 | 3230.87 | 2583.83 | 2531.2 | 2887.65 | 3370.79 | 3563.42 | 2916.97 | 3218.49 | 2881.84 | 2855.21 | 3175.65 |  |  |  | 37178.36 |  | 37178.36
37178.36
68 | FSU - Jones Student Center - Renovation and Addition | [16 empty] | FSU - Jones Student Center - Renovation and Addition
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
69 | UNCSA - Campus Police Facility | [16 empty] | UNCSA - Campus Police Facility
70 | UNCSA - Central Storage Facility | [16 empty] | UNCSA - Central Storage Facility
71 | NCSU - Talley Student Center Renovation and Addition | [16 empty] | NCSU - Talley Student Center Renovation and Addition
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 404388.9766 | 387783.457 | 399113.5586 | 365638.1406 | 330221.2891 | 364260.6328 | 371929.0781 | 383835.0391 | 391473.2578 | 364464.1953 | 339343.4531 | 347896.3516 |  |  | 4450347.4297 | kwhs | 15189.0358 | MMbtu
| Nat Gas (Therms) |  |  | 2029 | 3265 | 4100 | 3589 | 3582 | 2383 | 3400 | 4070 | 3136 | 4310 | 2363 | 1658 |  |  | 37885 | therms | 3787.5955 | MMbtu
| Steam (1000lbs) |  |  | 437.115 | 545.1245 | 805.2051 | 1150.8103 | 1472.5037 | 1587.8059 | 1080.0286 | 1222.5664 | 743.5703 | 526.125 | 423.4609 | 383.2227 |  |  | 10377.5384 | 1000lbs | 10377.5384 | MMbtu
| Chilled Water (Dtherms) |  |  | 3131.6562 | 2789.4726 | 1999.893 | 1008.9028 | 107.6955 | 260.2605 | 464.7735 | 463.487 | 1392.5475 | 1310.4055 | 2031.0383 | 2805.0373 |  |  | 17765.1696 | dtherms | 17760.9281 | MMbtu | 43327.5023 | Mmbtu
| Water (CCF) |  |  | 564.1713 | 698.6784 | 707.238 | 673.2015 | 412.7895 | 598.3575 | 687.2701 | 634.1773 | 798.9846 | 383.488 | 347.3044 | 414.109 |  |  | 6919.7695 | CCF | 5175987.5536 | gallons
| Electricity Cost ($) |  |  | 35181.841 | 33737.1608 | 34722.8796 | 31810.5182 | 28729.2521 | 31690.6751 | 32357.8298 | 33393.6484 | 34058.1734 | 31708.385 | 29522.8804 | 28875.3972 |  |  | 385788.641 |  | 385788.641
| Nat Gas Costs ($) |  |  | 1307.68 | 2073.19 | 2596.01 | 2309.57 | 2199.77 | 1534.7 | 2370.29 | 2806.77 | 2206.88 | 3001.02 | 1717.94 | 1253.34 |  |  | 25377.16 |  | 25377.16
| Steam Costs ($) |  |  | 5254.1223 | 6552.3969 | 9678.565 | 13832.74 | 17699.4941 | 19085.4274 | 12981.9437 | 14695.2482 | 8937.7152 | 6324.0225 | 5090.0005 | 5292.3049 |  |  | 125423.9806 |  | 125423.9806
| Chilled Water ($) |  |  | 40554.9484 | 36123.6705 | 25898.6143 | 13065.2906 | 1394.6567 | 3370.3735 | 6018.8168 | 6002.1566 | 18033.4901 | 16969.7512 | 26301.9453 | 35792.2753 |  |  | 229525.9896 |  | 229525.9896
766115.7711
72 | NCC - CE and BLET | [16 empty] | NCC - CE and BLET
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 104400 | 125200 | 89040 | 105360 | 65360 | 64880 | 51440 | 57200 | 56800 | 66960 | 66640 | 81440 |  |  |  | 934720 | kwhs | 3190.1994 | MMbtu
| Nat Gas (Therms) |  | 646 | 641 | 707 | 1114 | 1353 | 1353 | 2762 | 4384 | 3540 | 3232 | 1064 | 769 |  |  |  | 21565 | therms | 2155.9851 | MMbtu | 5346.1845 | MMbtu
| Water (CCF) |  | 128 | 121 | 118 | 29 | 29 | 29 | 25 | 9 | 27 | 32 | 25 | 17 |  |  |  | 589 | CCF | 440572 | gallons
| Electricity Cost ($) |  | 10646.43 | 12365.49 | 9174.33 | 10543.77 | 7371.11 | 7162.18 | 6046.74 | 6455.13 | 6427.83 | 7118.7 | 7096.93 | 8103.31 |  |  |  | 98511.95 |  | 98511.95
| Chilled Water Costs ($) |  | 155.16 | 933.58 | 910.96 | 239.9 | 239.9 | 209.74 | 89.1 | 224.82 | 262.52 | 247.44 | 209.74 | 149.42 |  |  |  | 3872.28 |  | 3872.28
| Nat Gas Costs ($) |  | 695.37 | 690.25 | 754.74 | 1167.02 | 1422.3 | 1422.39 | 2809.02 | 4404.34 | 3574.15 | 3701.75 | 1318.89 | 1030.93 |  |  |  | 22991.15 |  | 22991.15
125375.38
73 | UNCSA - Film School Production Design Facility | [16 empty] | UNCSA - Film School Production Design Facility
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 0 | MMbtu
| Water (CCF) | [16 empty] | 0 | CCF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
0
74 | UNCC - Holshouser Residence Hall Renovation | [16 empty] | UNCC - Holshouser Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0
75 | UNCC - Laurel Residence Hall | [16 empty] | UNCC - Laurel Residence Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0
76 | ASU - Belk Residence Hall Renovation | [16 empty] | ASU - Belk Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 51000 | 52560 | 65280 | 50280 | 38640 | 32280 | 27600 | 34440 | 34080 | 37320 | 36480 | 30480 |  |  |  | 490440 | kwhs | 1673.8717 | MMbtu
| Steam (lbs) |  | 33368 | 39207.4 | 55057.2 | 47549.4 | 68404.4 | 90927.8 | 95933 | 77580.6 | 94264.6 | 49217.8 | 38373.2 | 39207.4 |  |  |  | 729090.8 | lbs | 729.0908 | MMbtu | 2402.9625 | MMbtu
| Water (gallons) |  | 57000 | 113000 | 230000 | 126000 | 97000 | 32000 | 76000 | 108000 | 104000 | 111000 | 54000 | 48000 |  |  |  | 1156000 | gallons | 1156000 | gallons
| Electricity Cost ($) |  | 4120.51 | 4246.17 | 5270.77 | 4062.51 | 3124.9 | 2612.6 | 2235.63 | 2870.88 | 2930.37 | 3207.77 | 3135.85 | 2622.13 |  |  |  | 40440.09 |  | 40440.09
| Steam Costs ($) |  | 700.8 | 823.44 | 1156.32 | 998.64 | 1436.64 | 1909.68 | 2014.8 | 1629.36 | 1979.76 | 1033.68 | 805.92 | 1019.43 |  |  |  | 15508.47 |  | 15508.47
55948.56
77 | UNCW - Osprey Hall Renovation | [16 empty] | UNCW - Osprey Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 54389 | 66815 | 80130 | 61939 | 75690 | 55369 | 77533 | 55539 | 75659 | 62896 | 63463 | 74539 |  |  |  | 803961 | kwhs | 2743.9189 | MMbtu
| Nat Gas (MCF) |  | 264 | 327 | 405 | 348 | 466 | 360 | 523 | 333 | 499 | 340 | 358 | 408 |  |  |  | 4631 | MCF | 4756.037 | MMbtu
| Heating Hot Water Usage (Mbtu) | No data | [15 empty] | 0 | Mbtu | 0 | MMbtu
| Chilled water (ton-hrs) | No data | [15 empty] | 0 | ton-hrs | 0 | MMbtu | 7499.9559 | MMbtu
| Water Usage (gallons) |  | 3238 | 10823 | 22310 | 18243 | 22218 | 3499 | 17207 | 16199 | 18834 | 14669 | 6696 | 7792 |  |  |  | 161728 | gallons | 161728 | gallons
| Electricity Cost ($) |  | 4383.75 | 5418.7 | 6274.18 | 4732.14 | 5532.94 | 3864.76 | 5303.26 | 3754.44 | 5122.11 | 4283.22 | 4499.53 | 5381.72 |  |  |  | 58550.75 |  | 58550.75
| Nat Gas Costs ($) |  | 1354.32 | 1599.03 | 1980.45 | 1743.48 | 2353.3 | 2084.4 | 3378.58 | 2004.66 | 2579.83 | 1870 | 1976.16 | 2329.68 |  |  |  | 25253.89 |  | 25253.89 |  |  | MCF=1000CF
| Heating Hot Water ($) | No data | [15 empty] | 0 |  | 0
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
|  | S&BS (Osprey Hall) also receives its space heating and cooling from a central plant. Unfortunately, calculations were not done for this building. | [17 empty] | 83804.64
78 | ECU - Gateway Residence Hall (Belk Replacement) | [16 empty] | ECU - Gateway Residence Hall (Belk Replacement)
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Steam (lbs) | No data. | [15 empty] | 0 | lbs | 0 | MMbtu | 0 | MMbtu
| Water (kgallons) | [16 empty] | 0 | kgallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Steam Costs ($) | No data. | [15 empty] | 0 |  | 0
0
79 | UNCC - Oak Residence Hall Renovation | [16 empty] | UNCC - Oak Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water (MMBtu) | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water (MMBtu) | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | MMbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0
80 | WTCC - Holding Hall Renovation | [16 empty] | WTCC - Holding Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 62500 | 63700 | 49900 | 39700 | 36500 | 36100 | 38300 | 41900 | 46500 | 45200 | 59000 | 61800 |  |  | 581100 | kwhs | 1983.2943 | MMbtu
| Fuel Oil (gallons) |  |  | 0 | 706.9 | 667.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1374.2 | gallons | 190.8407 | MMbtu
| Nat Gas (Therms) |  |  | 0 | 0 | 0 | 1231 | 2199 | 2302 | 1665 | 1932 | 1240 | 1224 | 712 | 422 |  |  | 12927 | therms | 1292.3914 | MMbtu | 3466.5263 | MMbtu
| Water (CCF) |  |  | 56.1799 | 54.0114 | 40.1637 | 38.7525 | 32.2566 | 53.2577 | 48.3938 | 43.8185 | 34.37 | 29.2012 | 23.4864 | 28.1904 |  |  | 482.0822 | CCF | 360597.4548 | gallons
| Electricity Cost ($) |  |  | 5394.84 | 5494.94 | 4229.05 | 3420.85 | 3064.7 | 2725.59 | 2857.64 | 3201.74 | 3457.29 | 3566.12 | 4277.33 | 4636.35 |  |  | 46326.44 |  | 46326.44
| Fuel Oil Cost ($) |  |  | 0 | 1322.26 | 1357.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2679.82 |  | 2679.82
| Nat Gas Costs ($) |  |  |  |  | 18.73 | 877.19 | 1540.48 | 1784.24 | 1311.47 | 1519.33 | 1008.31 | 997.11 | 599.04 | 369.4 |  |  | 10025.3 |  | 10025.3
59031.56
81 | UNC-CH - McLean Hall Bell/Rizzo | [16 empty] | UNC-CH - McLean Hall Bell/Rizzo
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 93200 | 136470 | 96678 | 96014 | 83407 | 112233 | 102692 | 89845 | 101172 | 84080 | 117029 | 111222 |  |  | 1224042 | kwhs | 4177.6553 | MMbtu
| Natural Gas (therms) |  |  | 2429 | 2515 | 2700 | 3660.5 | 4521 | 5598.5 | 5927 | 4813 | 5189 | 3761 | 3507 | 2819.5 |  |  | 47440.5 | therms | 4742.9173 | MMbtu | 8920.5727 | Mmbtu
| Water Usage (kgallons) |  |  | 77 | 60 | 110 | 148 | 86 | 98 | 99 | 105 | 98 | 126 | 113 | 128 |  |  | 1248 | kgallons | 1248000 | gallons
| Electricity Cost ($) |  |  | 6682.44 | 7478.56 | 6409.75 | 4551.06 | 4812.58 | 5634.1 | 5524.83 | 4842.65 | 5837.62 | 4658.03 | 5570.58 | 7926.16 |  |  | 69928.36 |  | 69928.36
| Natural Gas ($) |  |  | 1018.19 | 1054.28 | 1131.72 | 1534.32 | 1925.16 | 2362.79 | 2943.99 | 2407.27 | 2591.985 | 1899.125 | 1770.715 | 1423.645 |  |  | 22063.19 |  | 22063.19
91991.55
82 | UNCC - Belk Gymnasium Renovation | [16 empty] | UNCC - Belk Gymnasium Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water (MMBtu) | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water (MMBtu) | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | MMbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0
83 | UNCG - Leonard J. Kaplan Center for Wellness | [16 empty] | UNCG - Leonard J. Kaplan Center for Wellness
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 472979 | 545332 | 503876 | 342687 | 323860 | 292633 | 295932 | 275150 | 333061 | 341723 | 370179 | 463630 |  |  |  | 4561042 | kwhs | 15566.8363 | MMbtu
| Nat Gas (Therms) |  | 8075 | 7697 | 9092 | 9912 | 14428 | 22001 | 24984 | 17582 | 16177 | 17143 | 11528 | 9437 |  |  |  | 168056 | therms | 16801.5876 | MMbtu | 32368.4239 | MMbtu
| Water (gallons) |  | Note 2 | 136136 | 846736 | 731544 | 425612 | 348568 | 232628 | 184756 | 267784 | 228140 | 303688 | 365772 |  |  |  | 4071364 | gallons | 4071364 | gallons
| Electricity Cost ($) |  | 35972.84 | 41213.34 | 35924 | 25630.78 | 23219.21 | 19651.36 | 16405.96 | 16179.25 | 19083.31 | 20252.48 | 21826.62 | 34676.43 |  |  |  | 310035.58 |  | 310035.58
| Nat Gas Costs ($) |  | 5954.12 | 5676.5 | 6701.05 | 7370.3 | 10877.12 | 19284.79 | 22601.42 | 15760.77 | 14503.19 | 14739.4 | 10008.57 | 7528.26 |  |  |  | 141005.49 |  | 141005.49
|  | Note 2: Missing Data | [17 empty] | 451041.07
84 | NCSU - Reynolds Coliseum Renovation | [16 empty] | NCSU - Reynolds Coliseum Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 120312.9883 | 156106.0181 | 150607.9712 | 145809.021 | 144721.9849 | 138762.0239 | 143576.0498 | 148554.9316 | 150557.9834 | 152450.0732 | 169554.9316 | 171994.0186 |  | 1793007.9956 | kwhs | 6119.5363 | MMbtu
| Steam (1000lbs) |  |  |  | 421.7251 | 564.1295 | 527.9221 | 550.0643 | 550.3773 | 235.4723 | 277.6578 | 147.1246 | 161.3724 | 45.3614 | 43.8373 | 77.8789 |  | 3602.9231 | 1000lbs | 3602.9231 | MMbtu
| Chilled Water (Dtherms) |  |  |  | 1185.791 | 675.2422 | 265.5713 | 182.5391 | 195.418 | 210.9014 | 225.2129 | 575.5078 | 768.9307 | 828.7598 | 1027.79 | 979.4297 |  | 7121.0938 | dtherms | 7119.3936 | MMbtu | 16841.8529 | Mmbtu
| Water (CCF) |  |  |  | 402.2595 | 382.5549 | 379.7209 | 123.2271 | 100.1672 | 104.7524 | 140.98 | 94.0847 | 123.5613 | 38.5269 | 117.412 | 111.891 |  | 2119.1379 | CCF | 1585115.1853 | gallons
| Electricity Cost ($) |  |  |  | 10467.23 | 13581.2236 | 13102.8935 | 12685.3848 | 12590.8127 | 12072.2961 | 12491.1163 | 12924.2791 | 13098.5446 | 13263.1564 | 14751.2791 | 14275.5035 |  | 155303.7195 |  | 155303.7195
| Steam Costs ($) |  |  |  | 5069.1362 | 6780.8371 | 6345.6237 | 6611.7734 | 6615.535 | 2830.3773 | 3337.4465 | 1768.4381 | 1939.696 | 545.2439 | 526.9241 | 1075.5077 |  | 43446.5389 |  | 43446.5389
| Chilled Water ($) |  |  |  | 15355.9937 | 8744.3863 | 3439.1482 | 2363.8809 | 2530.6627 | 2731.1727 | 2916.5069 | 7452.8262 | 9957.6521 | 10732.439 | 13309.881 | 12497.5228 |  | 92032.0724 |  | 92032.0724
290782.3309

## 16.17 Raw Meter
2015/2016 Meter Data Summary
1 | ASU - Cone Residence Hall Renovation | [17 empty] | ASU - Cone Residence Hall Renovation
ELECTRICITY
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 124302.36 | 136673.48 | 154241.2 | 154193.12 | 150620.96 | 124908 | 100757.2 | 142079.84 | 126422.8 | 146194.96 | 153701.56 | 92243
| 315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 90183.92 | 75576.56 | 97576.4 | 83684.64 | 70809.12 | 57196 | 34628.4 | 60848.48 | 55911.6 | 67107.12 | 74650.32 | 51248
| 452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 86886.72 | 100976.96 | 121742.4 | 106562.24 | 94529.92 | 77896 | 67854.4 | 83151.68 | 77425.6 | 91417.92 | 88109.12 | 79328
| 239 | Belk Residence Hall Total Electricity Use | 51000 | 52560 | 65280 | 50280 | 38640 | 32280 | 27600 | 34440 | 34080 | 37320 | 36480 | 30480
| 204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 10055.6008 | 11052.1161 | 12467.197 | 12463.3377 | 12175.592 | 10104.3948 | 8159.0232 | 11847.9085 | 10867.3251 | 12560.2146 | 13202.9423 | 7940.8564
| 315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 7278.9497 | 6102.3156 | 7874.4201 | 6755.4264 | 5718.2861 | 4621.7522 | 2803.9183 | 5070.1961 | 4801.7408 | 5760.2983 | 6406.156 | 4402.4387
| 452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 7028.1895 | 8163.1882 | 9835.853 | 8613.0759 | 7643.8719 | 6303.993 | 5495.1385 | 6938.1154 | 6658.6142 | 7856.6571 | 7573.3617 | 6821.5049
| 239 | Belk Residence Hall Total Electricity Cost | 4120.51 | 4246.17 | 5270.77 | 4062.51 | 3124.9 | 2612.6 | 2235.63 | 2870.88 | 2930.37 | 3207.77 | 3135.85 | 2622.13
STEAM
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 292804.2 | 311990.8 | 263607.2 | 227736.5992 | 376224.2 | 459644.2 | 623981.6 | 372887.4 | 511364.6 | 386234.6 | 488007 | 330343.1992
| 315 | Cone Residence Hall Steam Use in Lbs. | 70907 | 87591 | 136808.8 | 139311.4 | 241918 | 150990.2 | 226902.4 | 146819.2 | 222731.4 | 121793.2 | 102606.6 | 73409.6
| 452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 221897.2 | 250260 | 302814.6 | 260270.4 | 444628.6 | 537224.8 | 506359.4 | 471323 | 412929 | 266944 | 260270.4 | 253596.8
| 239 | Belk Residence Hall Steam Use in lbs. | 33368 | 39207.4 | 55057.2 | 47549.4 | 68404.4 | 90927.8 | 95933 | 77580.6 | 94264.6 | 49217.8 | 38373.2 | 39207.4
| 204 & 445 | Plemmons Student Union Total Steam Cost | 6149.52 | 6552.48 | 5536.32 | 4782.96 | 7901.52 | 9653.52 | 13104.96 | 7831.44 | 10739.76 | 8111.76 | 10249.2 | 8589.24
| 315 | Cone Residence Hall Steam Costs | 1489.2 | 1839.6 | 2873.28 | 2925.84 | 5080.8 | 3171.12 | 4765.44 | 3083.52 | 4677.84 | 2557.92 | 2154.96 | 1908.72
| 452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 5426 | 6119.55 | 7404.66 | 6364.33 | 10872.4 | 13136.64 | 12381.89 | 11525.15 | 10097.26 | 6527.52 | 6364.33 | 7278.68
| 239 | Belk Residence Hall Steam Cost | 700.8 | 823.44 | 1156.32 | 998.64 | 1436.64 | 1909.68 | 2014.8 | 1629.36 | 1979.76 | 1033.68 | 805.92 | 1019.43
WATER & SEWER
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 347964.0001 | 386276 | 446391 | 292376 | 228639 | 69000 | 128000 | 213000 | 208295 | 298425.0001 | 287539 | 287916
| 315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 146908 | 171372 | 218777 | 168072 | 159633 | 50000 | 112000 | 174000 | 155865 | 155975 | 94933 | 57452
| 452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 117128 | 239352 | 362832 | 265552 | 246728 | 75000 | 173000 | 270000 | 245840 | 263600 | 157528 | 90632
| 239 | Belk Residence Hall Water Use | 57000 | 113000 | 230000 | 126000 | 97000 | 32000 | 76000 | 108000 | 104000 | 111000 | 54000 | 48000
| 204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 3726.0804 | 2995.2108 | 3627.3685 | 3822.692 | 2974.6506 | 1984.5 | 1298.2 | 2999 | 2198.6915 | 2480.1725 | 4088.5659 | 3343.0792
| 315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 1530.6388 | 1330.0276 | 1725.2195 | 2040.824 | 1912.5182 | 1419 | 1071.8 | 2498 | 1737.7005 | 1614.6075 | 1728.4573 | 867.2024
| 452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 942.9808 | 1122.3616 | 2603.412 | 3106.984 | 2945.3312 | 2156 | 1634.7 | 3864.5 | 2704.608 | 2601.32 | 2849.9768 | 1336.4184
| 239 | Belk Residence Hall Water & Sewer Cost | 347.7 | 372.9 | 805 | 567 | 523.8 | 240 | 486.4 | 1080 | 384.8 | 410.7 | 437.4 | 297.6
2 | UNCC - Prospector Hall Renovation Phase II | [17 empty] | UNCC - Prospector Hall Renovation Phase II
No data
3 | UNCC - Miltimore Residence Hall | [17 empty] | UNCC - Miltimore Residence Hall
No data
4 | NCCU - Nursing Building | [17 empty] | NCCU - Nursing Building
Agency - Building Name: NCCU - Nursing Building
| Utility | Jun-16 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14
| Electricity (KWhs) | 85576 | 101534 | 104360 | 88955 | 79901 | 57473 | 51047 | 53957 | 57291 | 60217 | 65740 | 68099 | 70935 | 82428 | 65420
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) | 51 | 39 | 41 | 47 | 39 | 40 | 47 | 51 | 48 | 51 | 44 | 46 | 50 | 42 | 39
| Water (CCF) | 30042 | 29190 | 36174 | 26967 | 22047 | 20331 | 16553 | 16038 | 8982 | 5104 | 8580 | 8836 | 8359 | 14279
| Electricity Cost ($) | 5323.04 | 6315.67 | 6491.45 | 5533.22 | 4970.04 | 3637.17 | 3175.25 | 3356.26 | 3563.64 | 3745.65 | 4089.19 | 4235.93 | 4412.33 | 5127.23 | 4069.29
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 53.61 | 45.4 | 46.77 | 50.87 | 45.48 | 46.63 | 53.19 | 56.61 | 57.79 | 60.26 | 54.71 | 56.95 | 60.27 | 53.63 | 51.14
Note 1 : August 2017 is a partial bill (up to 08/24/2016) | bar: 2016-07-01
Note 2 : Natural Gas July and August 2017 readings for Chidley North show 0 (up to 08/24/2016) and they will be adjusted in September. | bar: 2016-07-01 to 2016-12-01
Note 3: Nursing Building steam meter has not been fixed and could not get any readings. | bar: 2016-07-01 to 2016-10-01
5 | NCCU - Chidley Residence Hall | [17 empty] | NCCU - Chidley Residence Hall
Agency - Building Name: NCCU - Chidley North
| Utility | Jun-16 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14
| Electricity (KWhs) | 53704 | 147744 | 165784 | 358416 | 114416 | 80848 | 81512 | 115584 | 105168 | 109536 | 142384 | 133160 | 130944 | 145640 | 117416
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) | 277 | 289 | 404 | 594 | 878 | 1277 | 1383 | 685 | 2155 | 2118 | 1658 | 1977 | 48 | 0 | 0
| Water (CCF) | 23436 | 36393 | 89259 | 91028 | 83333 | 77392 | 28849 | 86983 | 135056 | 119848 | 109228 | 78193 | 73540 | 78193
| Electricity Cost ($) | 3340.52 | 9190.04 | 10312.18 | 22294.36 | 7179.16 | 5028.95 | 5070.25 | 7189.61 | 6541.71 | 6813.41 | 8856.64 | 8282.88 | 8145.04 | 9059.17 | 7303.57
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 208.18 | 216.39 | 295.03 | 418.92 | 597.94 | 870.45 | 985.72 | 522.2 | 1684.04 | 1657.57 | 1315.61 | 1582.56 | 58.61 | 18.73 | 18.73
Note 1 : August 2017 is a partial bill (up to 08/24/2016) | bar: 2016-07-01
Note 2 : Natural Gas July and August 2017 readings for Chidley North show 0 (up to 08/24/2016) and they will be adjusted in September. | bar: 2016-07-01 to 2016-12-01
Note 3: Nursing Building steam meter has not been fixed and could not get any readings. | bar: 2016-07-01 to 2016-10-01
6 | UNC-CH - Loudermilk | [17 empty] | UNC-CH - Loudermilk
Energy and Water Usage (Acct. #01012081)
Annual Summary of Performance
| id | Period | name | total btu | Electric (Btu) | ng (Btu) | steam (Btu) | chw (Btu) | mgal water | gsf | mgal non-potable water | Site EUI
| Actual Performance | Aug 16 - Jul 17 | UNC Chapel Hill | 17573308120 | 6795502976 | 400200000 | 7331160000 | 3046445144 | 1916 | 195165 | 0 | 90043.3383
| Modeled Performance | NA | UNC Chapel Hill | 7001059000 | 3177664000 | 99432000 | 1747534000 | 1976429000 | NA | 170189 | NA | 41136.9654
Monthly Detail of Performance
| UTILITY | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01
Consumption:
| ELECTRIC (kWhs) | 132497 | 190080 | 173794 | 197784 | 172425 | 169010 | 163677 | 151891 | 156752 | 144391 | 192321 | 147026
| STEAM (MLBS) | 638 | 567 | 660 | 408 | 407 | 721 | 581 | 356 | 474 | 383 | 468 | 477
| CHILLED WATER (Ton-Hrs.) | 181905 | 184835 | 155343 | 64925 | 14135 | 2139 | 2227 | 9867 | 14159 | 54300 | 87151 | 121876
| NATURAL GAS (Therms) | 109 | 162 | 379 | 599 | 380 | 486 | 282 | 303 | 335 | 293 | 381 | 293
| WATER (kGal) | 107 | 201 | 278 | 234 | 215 | 140 | 161 | 131 | 151 | 107 | 122 | 69
| SEWER (kGal) | 107 | 201 | 278 | 234 | 215 | 140 | 161 | 131 | 151 | 174 | 122 | 69
| STORMWATER (ksf) | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
Costs:
| ELECTRIC ($) | 9500.03 | 10416.38 | 11522.54 | 9374.96 | 9948.92 | 8484.3 | 8805.82 | 8186.92 | 9044.59 | 7999.26 | 9154.48 | 9644.91
| STEAM ($) | 7017.87 | 6236.89 | 7259.87 | 4487.92 | 4476.92 | 7930.86 | 6390.88 | 3915.93 | 5213.91 | 4212.92 | 5147.91 | 5245.04
| CHILLED WATER ($) | 16644.31 | 16912.4 | 14213.88 | 5940.64 | 1293.35 | 195.72 | 203.77 | 902.83 | 1295.55 | 4968.45 | 7974.32 | 11395.41
| NATURAL GAS ($) | 69.67 | 103.55 | 242.25 | 380.29 | 253.63 | 333.09 | 203.89 | 230.46 | 255.24 | 225.42 | 295.89 | 227.55
| WATER ($) | 889.17 | 1670.31 | 1856.96 | 1022.58 | 939.55 | 611.8 | 703.57 | 572.47 | 659.87 | 1025.78 | 1013.82 | 573.39
| SEWER ($) | 727.6 | 1366.8 | 1890.4 | 1591.2 | 1462 | 952 | 1094.8 | 890.8 | 1026.8 | 1183.2 | 829.6 | 469.2
| STORMWATER ($) | 340.2 | 340.2 | 340.2 | 340.2 | 340.2 | 340.2 | 340.2 | 340.2 | 340.2 | 340.2 | 340.2 | 357.75
7 | DoAg&CS - Davis Event Center | [17 empty] | DoAg&CS - Davis Arena
NC Department of Agriculture & Consumer Services - Western Ag Center - Davis Events Center
| Utility | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | Annual Total
| Electricity Usage (KWhs) | 46440 | 59080 | 67880 | 46840 | 36040 | 30840 | 33440 | 40120 | 41440 | 23400 | 50960 | 37800 | 514280
| Water Usage (gallons) | 21693.5 | 55355.8 | 87522.1 | 38898.6988 | 32914.2836 | 29174.0241 | 71064.9305 | 54607.7887 | 62088.3077 | 30670.1279 | 45631.1659 | 26181.8165 | 555802.5437
| Natural Gas Therms | 113 | 91 | 305 | 177 | 2117 | 1910 | 2421 | 3187 | 2779 | 174 | 197 | 142 | 13613
| Elecricity Cost ($) | 5015.84 | 5949.32 | 6783.01 | 4970.32 | 4030.41 | 3472.82 | 3666.52 | 4120.61 | 4210.38 | 3056.1 | 5015.35 | 4179.66 | 54470.34
| Water-Sewer Costs ($) | 1012.34 | 1338.38 | 1665.14 | 1190.8 | 1128.72 | 1089.92 | 1524.48 | 1353.76 | 1431.36 | 1105.44 | 1260.64 | 1058.88 | 15159.86
| Natural Gas ($) | 89.73 | 75.67 | 212.99 | 132.92 | 1387.6 | 1273.49 | 1762.89 | 2308.67 | 2028.08 | 152.63 | 170.49 | 127.78 | 9722.94
Notes: Davis Arena & Virginia Boone Bldg on same water meter
8 | NCSU - Student Health Center Addition and Renovation | [17 empty] | NCSU - Student Health Center Addition and Renovation
NCSU - Student Health Center Addition and Renovation
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 56780 | 55389 | 56067 | 57167 | 56609 | 61875 | 56873 | 61004 | 57214 | 58426 | 56376 | 58950 | 692730 | kwh |  | 2361.8712 | MMbtu
| Chilled Water (Dtherms) |  | 701.02 | 535.34 | 279.11 | 144.63 | 74.75 | 88.38 | 138.6 | 228.58 | 332.16 | 452.57 | 585.3 | 752.22 | 4312.66 | dthrms |  | 4312.66 | MMbtu
| Steam (1,000 lbs) |  | 248 | 433 | 477 | 516 | 420 | 432 | 566 | 570 | 499 | 502 | 484 | 483 | 5630 | 1000 lbs |  | 5630 | MMbtu
| Water (CCF) |  | 49.476 | 53.1635 | 57.0876 | 51.1715 | 36.7692 | 41.3141 | 52.6771 | 61.2013 | 57.5034 | 45.05 | 37.5953 | 40.1266 | 583.1358 | CCF |  | 436185.5647 | gallons
| Electric Cost ($) |  | 4939.86 | 4818.843 | 4877.829 | 4973.529 | 4924.983 | 5383.125 | 4947.951 | 5307.348 | 4977.618 | 5083.062 | 4904.712 | 4892.85 | 60031.71 | $
| Chilled Water Cost ($) |  | 9078.209 | 6932.653 | 3614.4745 | 1872.9585 | 968.0125 | 1144.521 | 1794.87 | 2960.111 | 4301.472 | 5860.7815 | 7579.635 | 9598.3272 | 55706.0252 | $
| Steam Cost ($) |  | 2980.96 | 5204.66 | 5733.54 | 6202.32 | 5048.4 | 5192.64 | 6803.32 | 6851.4 | 5997.98 | 6034.04 | 5817.68 | 6670.23 | 68537.17 | $
| Water Cost ($) |  | 461.6114 | 496.0157 | 532.6275 | 477.43 | 343.057 | 385.4602 | 491.4773 | 571.0085 | 536.5071 | 420.3165 | 350.7645 | 376.7888 | 5443.0644 | $
9 | ECSU - Gilchrist Ed & Psych Bldg | [17 empty] | ECSU - Gilchrist Ed & Psych Bldg
UNC - ECSU - Gilchrist Education & Psychology Building
| Utility | Jun-16 | 2016-07-15 | 2016-08-15 | 2016-09-15 | 2016-10-15 | 2016-11-15 | 2016-12-15 | 2017-01-16 | 2017-02-16 | 2017-03-16 | 2017-04-16 | 2017-05-16 | 2017-06-16 | 2017-07-16 | 2017-08-16 | 2017-09-14
| Electricity (KWhs) |  | 105600 | 103488 | 101952 | 76416 | 56064 | 53952 | 53760 | 57600 | 53951 | 63936 | 56832 | 76872
| Steam (lbs) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water (Dtherms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas (Therms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) |  | 4236.25 | 4271 | 7092.43 | 9192.19 | 5542 | 2443.31 | 10161.6 | 6178.68 | 5091.22 | 6424.63 | 7074.19 | 5182.18
| Electricity Cost ($) |  | 9189.16 | 8991.05 | 8993.77 | 7428.3 | 5775.37 | 5379.52 | 5367.51 | 5574.91 | 5379.52 | 5971.52 | 5658.66 | 7274.25
| Steam Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Please Note:
The water data is in gallons of water not CCF.
10 | UNCC - EPIC | [17 empty] | UNCC - EPIC
No data
11 | DoAg&CS - SENC Ag Center | [17 empty] | DoAg&CS - SENC Ag Center
NC Department of Agriculture & Consumer Services - Southeastern Ag Center - Multi-purpose Pavilion
| Utility | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2016-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | Annual Total
| Electricity Usage (KWhs) | 13600 | 16280 | 22560 | 11971 | 24720 | 22080 | 11060 | 16880 | 20140 | 1900 | 35420 | 21220 | 217831
| Water Usage (gallons) | 4790 | 2360 | 10000 | 10260 | 2930 | 9600 | 12330 | 1740 | 370 | 7420 | 4090 | 5100 | 70990
| Natural Gas Therms | 25 | 27 | 34 | 27 | 515 | 1125 | 1093 | 919 | 762 | 69 | 33 | 26 | 4655
| Elecricity Cost ($) | 2388.07 | 2637.87 | 3326.85 | 1624.82 | 3310.01 | 3086.48 | 1832.56 | 2524.59 | 2245.63 | 929.42 | 4356.75 | 3047.37 | 31310.42
| Water-Sewer Costs ($) | 115.01 | 74.68 | 201.5 | 205.82 | 40.36 | 51.44 | 55.97 | 38.39 | 36.11 | 47.82 | 42.29 | 55.17 | 964.56
| Natural Gas ($) | 40 | 41 | 46 | 41.31 | 429.89 | 965 | 936.43 | 790.76 | 627.81 | 77.85 | 48.75 | 43.29 | 4088.09
NOTES:
Pavilion, Farmers Market Building and Meeting Center all on the same water meter.
Error has been identified with incorrectly read water meter bginning in 2014. Corrections and credits are currently being tracked.
12 | Military and Veterans Affairs - NC State Veterans Home - Black Mountain | [17 empty] | DOA - VA - VA Home Swananoa
| Utility | JUN-16 | 2016-07-01 | 2016-08-16 | 2016-09-16 | 2016-10-16 | 2016-11-16 | 2016-12-16 | 2017-01-17 | 2017-02-17 | 2017-03-17 | 2017-04-17 | 2017-05-17 | 2017-06-17 | 2017-07-17 | 2017-08-17 | 2017-09-17
| Electricity (KWhs) | 177422 | 177800 | 186200 | 185800 | 177600 | 143747 | 153470 | 177613 | 148146 | 161500 | 149500 | 153253 | 193904
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) | 2482 | 1947 | 1782 | 1852 | 1731 | 2073 | 2101 | 2195 | 2046 | 2170 | 2045 | 2199 | 1891
| Water (CCF) | 575 | 394 | 394 | 419 | 419 | 419 | 500 | 504 | 428 | 438 | 422 | 358 | 435 | 430
| Electricity Cost ($) | 13873 | 14147 | 14604 | 14512 | 13905.45 | 11441 | 11792 | 12827 | 10859.76 | 11848 | 10888 | 11228.29 | 13775
Steam Costs ($)
| Water Cost ($) | 5209.17 | 3790.55 | 3790.55 | 3920 | 3906.17 | 3984.55 | 4627 | 4644.5 | 4054.39 | 4139.75 | 4007.03 | 3511.19 | 4108.71 | 4069.91
| Natural Gas Costs ($) | 1588.24 | 1256.9 | 1154.7 | 1198 | 1142 | 1354 | 1356.71 | 1576 | 1490 | 1591 | 1523 | 1625 | 1407
13 | Pitt CC - Russell Classroom Building | [17 empty] | Pitt CC - Russell Classroom Building
No data
14 | UNCG - Bailey Residence Hall Renovation | [17 empty] | UNCG - Bailey Residence Hall Renovation
| Bailey Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
305 West Drive
| Electricity (kWhs) | 19077 | 24682 | 25006 | 21386 | 24873 | 22911 | 21122 | 22868 | 26101 | 22533 | 22646 | 18070
| Lighting submeter (kWhs) | 4052.34 | 5926.15 | 5597.27 | 6371.37 | 6332.09 | 5330.17 | 5361.23 | 5823.26 | 6571.59 | 5750.7 | 6078.81 | 3943.87
| Mechanical submeter (kWhs) | 12973.64 | 13978.6 | 10678.96 | 12712.91 | 12751.67 | 13141.7 | 11071.83 | 11467.44 | 13492.96 | 11486.31 | 13792.62 | 11893.41
| Calculated plug load (kWhs) | 2051.02 | 4777.25 | 8729.77 | 2301.72 | 5789.24 | 4439.13 | 4688.94 | 5577.3 | 6036.45 | 5295.99 | 2774.57 | 2232.72 |  |  | Nihal Ali Al Raees:
Off reading/
| Steam Usage (lbs)* | 5270 | 9860 | 13340 | 17520 | 43220 | 68250 | 74950 | 60780 | 54350 | 17190 | 9090 | 6360 |  |  | having the average of 3 similar buildings for the same month
| Water Usage (gallons) | 6700 | 51100 | 85600 | 67400 | 83000 | 48200 | 62200 | 86600 | 84200 | 77400 | 33700 | 14400
| Chilled water (ton-hrs) | 22276 | 27099.3333 | 23967.3333 | 11504 | 10664.6667 | 7941 | 4767 | 4462 | 6798 | 7812 | 10861 | 12558
| Electricity Cost ($) | 1329.6231 | 1691.6889 | 1663.991 | 1194.0055 | 1364.5018 | 1308.0226 | 1213.1635 | 1247.7806 | 1501.1923 | 1220.6933 | 1254.945 | 1119.712
| Water Cost ($) | 54.9346 | 429.7045 | 719.8182 | 566.7727 | 697.9545 | 405.3182 | 523.0455 | 728.2273 | 708.0455 | 650.8636 | 283.3864 | 121.0909
| Steam Cost ($)* | 41.1793 | 77.0451 | 104.2374 | 136.8995 | 337.7168 | 533.2987 | 585.6518 | 474.9288 | 424.6855 | 134.3209 | 71.0284 | 49.6964
*Nihal Ali Al Raees: Off reading/having the average of 3 similar buildings for the same month
15 | UNCG - Coit Residence Hall Renovation | [17 empty] | UNCG - Coit Residence Hall Renovation
| Coit Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
312 Gray Drive
| Electricity (kWhs) | 19440 | 25539.6667 | 26717.6667 | 20243 | 22933 | 21422 | 20113 | 21952 | 25056 | 21553 | 21798 | 17036
| Lighting submeter (kWhs) | 3344.16 | 5421.94 | 5461.43 | 6350.63 | 6081.33 | 4956.62 | 4959.11 | 5765.29 | 6236.59 | 5639.86 | 5632.01 | 3895.12
| Mechanical submeter (kWhs) | 11344.75 | 12557.32 | 9853.17 | 11779.01 | 11236.35 | 12154.75 | 10516.68 | 10793.17 | 13064.26 | 10778.39 | 13200.85 | 11229.6
| Calculated plug load (kWhs) | 4751.09 | 7560.4067 | 11403.0667 | 2113.36 | 5615.32 | 4310.63 | 4637.21 | 5393.54 | 5755.15 | 5134.75 | 2965.14 | 1911.28
| Steam Usage (lbs)* | 4500 | 10190 | 10660 | 37200 | 28733.3333 | 54006.6667 | 63430 | 40763.3333 | 40293.3333 | 36110 | 6453.3333 | 4540
| Water Usage (gallons) | 49800 | 129100 | 267500 | 229900 | 282900 | 141700 | 44600 | 63500 | 62800 | 59100 | 29400 | 25200
| Chilled water (ton-hrs) | 22627 | 29638 | 24518 | 15124 | 15778 | 14869 | 12368 | 13340 | 10425 | 11675 | 17875 | 18406
| Electricity Cost ($) | 1354.9234 | 1750.4728 | 1777.8916 | 1130.1905 | 1258.0759 | 1223.0134 | 1155.2106 | 1197.7995 | 1441.0894 | 1167.6032 | 1207.9524 | 1055.6399
| Water Costs ($) | 408.3201 | 1085.6136 | 2249.4318 | 1933.25 | 2378.9318 | 1191.5682 | 375.0455 | 533.9773 | 528.0909 | 496.9773 | 247.2273 | 211.9091
| Steam Cost ($)* | 35.1626 | No Data | 83.2962 | 290.6771 | 224.5194 | 422.0027 | 495.6357 | 318.5206 | 314.8481 | 282.1599 | 50.4257 | 35.4751
*Nihal Ali Al Raees: Off reading/having the average of 3 similar buildings for the same month
16 | UNCG - Cotten Residence Hall Renovation | [17 empty] | UNCG - Cotten Residence Hall Renovation
| Cotten Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
314 Gray Drive
| Electricity (kWhs) | 19274 | 26563 | 28279 | 21878 | 24768 | 22791 | 20710 | 22501 | 24666 | 23585 | 22578 | 16574
| Lighting submeter (kWhs) | 3648.43 | 5497.02 | 5041.53 | 6057.24 | 5741.24 | 4733.78 | 4701.49 | 5475.43 | 6186 | 5403.2 | 5181.69 | 3283.34
| Mechanical submeter (KWhs) | 13562.42 | 16225.66 | 11823.69 | 16285.82 | 12999.17 | 13335.63 | 11251.93 | 11431.86 | 12325.92 | 12891.25 | 13774.53 | 11479.09
| Calculated plug load (kWhs) | 2063.15 | 4840.32 | 11413.78 | -465.06 | 6027.59 | 4721.59 | 4756.58 | 5593.71 | 6154.08 | 5290.55 | 3621.78 | 1811.57
| Steam Usage (lbs) | 6680 | 17870 | 21720 | 15290 | 23904.4444 | 49258.8889 | 59590 | 34091.1111 | 35607.7778 | 23290 | 9260 | 6140
| Water Usage (gallons) | 37100 | 117100 | 105500 | 94900 | 137600 | 91600 | 109100 | 93100 | 33100 | 57000 | 29000 | 1400
| Chilled water (ton-hrs) | 21484 | 25899 | 24306 | 12824 | 10780 | 7513 | 24748 | No Data | 10087 | 14413 | 14228 | 15570
| Electricity Cost ($) | 1343.3536 | 1820.6114 | 1881.7885 | 1221.4745 | 1358.7417 | 1301.1716 | 1189.4999 | 1227.7554 | 1418.6586 | 1277.6839 | 1251.1767 | 1027.012
| Water Costs ($) | 304.1902 | 984.7045 | 887.1591 | 798.0227 | 1157.0909 | 770.2727 | 917.4318 | 782.8864 | 278.3409 | 479.3182 | 243.8636 | 11.7727
| Steam Cost ($) | 52.1969 | 139.6344 | 169.7179 | 119.4745 | 186.7869 | 384.904 | 465.6303 | 266.3845 | 278.2356 | 181.9857 | 72.3567 | 47.9773
*Nihal Ali Al Raees: Off reading/having the average of 3 similar buildings for the same month
17 | UNCG - Gray Residence Hall Renovation | [17 empty] | UNCG - Gray Residence Hall Renovation
| Gray Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
316 Gray Drive
| Electricity (kWhs) | 19969 | 25374 | 26868 | 22056 | 25355 | 23119 | 21134 | 23134 | 26601 | 23753 | 24223 | 18849
| Lighting submeter (kWhs) | 4487 | 5379 | 5447 | 6027 | 6218 | 5327 | 5279 | 5704 | 6431 | 5443 | 6129 | 4483
| Mechanical submeter (kWhs) | 13237.3 | 15304.5 | 11581.18 | 14806.26 | 13110.68 | 13217.68 | 11106.85 | 11772.99 | 13969.92 | 12864.23 | 14610.57 | 12152.5
| Calculated plug load (kWhs) | 2244.7 | 4690.5 | 9839.82 | 1222.74 | 6026.32 | 4574.32 | 4748.15 | 5657.01 | 6200.08 | 5445.77 | 3483.43 | 2213.5
| Steam Usage (lbs) | 2930 | 2840 | 10570 | 9710 | 25390 | 72570 | 75300 | 40940 | 49300 | 5340 | 1010 | 1120
| Water Usage (gallons) | 39400 | 75400 | 120000 | 112000 | 143900 | 129900 | 66800 | 57200 | 55400 | 53900 | 24100 | 9400
| Chilled water (ton-hrs) | 22717 | 25761 | 23078 | 6564 | 5436 | 4947 | 5318 | 7817 | 9341 | 14442 | 16173 | 18973
| Electricity Cost ($) | 1391.7935 | 1739.1181 | 1787.8953 | 1231.4124 | 1390.9438 | 1319.8976 | 1213.8528 | 1262.2947 | 1529.9497 | 1286.7851 | 1342.3356 | 1167.9829
| Water Costs ($) | 323.0484 | 634.0455 | 1009.0909 | 941.8182 | 1210.0682 | 1092.3409 | 561.7273 | 481 | 465.8636 | 453.25 | 202.6591 | 79.0455
| Steam Cost ($) | 22.8947 | 22.1915 | 82.5929 | 75.873 | 198.3949 | 567.0547 | 588.3867 | 319.9011 | 385.2253 | 41.7262 | 7.892 | 8.7516
18 | UNCG - Hinshaw Residence Hall Renovation | [17 empty] | UNCG - Hinshaw Residence Hall Renovation
| Hinshaw Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
309 West Drive
| Electricity (kWhs) | 23243 | 31723 | 33831 | 26694 | 28058 | 28507 | 25550 | 27252 | 31964 | 28723 | 28894 | 23949
| Lighting submeter (kWhs) | 3840.72 | 6013.01 | 5468.25 | 6469.64 | 5978.94 | 4970.17 | 5017.05 | 5637.51 | 6394.15 | 5574.43 | 5883.23 | 4784.2
| Mechanical submeter (kWhs) | Note 2 | 17442.92 | 13235.83 | 14294.92 | 12206.01 | 14374.72 | 12221 | 12727.7 | 15828.54 | 14486.19 | 16114.18 | 14080.68
| Site Lighting (kWh) | 2841 | 2732 | 3101 | 3253 | 3928 | 3929 | 3878 | 3480 | 3040 | 2912 | 2644 | 2330
| Calculated plug load (kWhs) | Note 2 | 8267.07 | 15126.92 | 5929.44 | 9873.05 | 9162.11 | 8311.95 | 8886.79 | 9741.31 | 8662.38 | 6896.59 | 5084.12
| Steam Usage (lbs) | 4960 | 5800 | 12680 | 15600 | 17590 | 21200 | 40040 | 20570 | 17230 | 13660 | 8500 | 2820
| Water Usage (gallons) | 16600 | 73500 | 104600 | 82700 | 122500 | 79200 | 57700 | 57400 | 56500 | 57300 | 41400 | 45500
| Chilled water (ton-hrs) | 20598 | 26776 | 23608 | 11831 | 7988 | 5522 | 5299 | 7236 | 9076 | 14531 | 15171 | 18926
| Electricity Cost ($) | 1619.9838 | 2174.2746 | 2251.2389 | 1490.3574 | 1539.227 | 1627.5064 | 1467.4902 | 1486.9913 | 1838.4012 | 1556.0278 | 1601.1825 | 1484.0057
| Water Costs ($) | 136.1067 | 618.0682 | 879.5909 | 695.4318 | 1030.1136 | 666 | 485.2045 | 482.6818 | 475.1136 | 481.8409 | 348.1364 | 382.6136
| Steam Cost ($) | 38.7569 | 45.3206 | 99.0803 | 121.8968 | 137.4465 | 165.6547 | 312.8686 | 160.7319 | 134.6335 | 106.7379 | 66.4181 | 22.0352
Note 2: Missing Data
19 | UNCG - Jamison Residence Hall Renovation | [17 empty] | UNCG - Jamison Residence Hall Renovation
| Jamison Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
301 West Drive
| Electricity (kWhs) | 17705 | 24833 | 26199 | 21474 | 25185 | 23084 | 21405 | 23213 | 26551 | 23018 | 23962 | 17281
| Lighting submeter (kWhs) | 2301.14 | 5514.01 | 5241.45 | 6356.57 | 6031.79 | 4790.25 | 5013.26 | 5542.36 | 6087.33 | 5367.39 | 5797.73 | 3450.98
| Mechanical submeter (kWhs) | 13349.83 | 14490.83 | 11137.58 | 13468.9 | 13067.83 | 13486.79 | 11566.09 | 11918.81 | 14256.08 | 12309.27 | 14274.5 | 12085.83
| Calculated plug load (kWhs) | 2054.03 | 4828.16 | 9819.97 | 1648.53 | 6085.38 | 4806.96 | 4825.65 | 5751.83 | 6207.59 | 5341.34 | 3889.77 | 1744.19
| Steam Usage (lbs) | 13105.6667 | 33087 | 42559.3333 | 29754.6667 | 42645.3333 | 12760 | 10570 | 10270 | 6060 | 23914 | 19191 | 21491
| Water Usage (gallons) | 29000 | 78100 | 127200 | 94000 | 115200 | 101600 | 104200 | 105300 | 87900 | 59100 | 24900 | 2600
| Chilled water (ton-hrs) | 20598 | 26776 | 23608 | 11831 | 7988 | 5522 | 5299 | 7236 | 9076 | 14531 | 15171 | 18926
| Electricity Cost ($) | 1233.9979 | 1702.0383 | 1743.3776 | 1198.9187 | 1381.6178 | 1317.8994 | 1229.4179 | 1266.6053 | 1527.0739 | 1246.9675 | 1327.8721 | 1070.8214
| Water Costs ($) | 237.7767 | 656.75 | 1069.6364 | 790.4545 | 968.7273 | 854.3636 | 876.2273 | 885.4773 | 739.1591 | 496.9773 | 209.3864 | 21.8636
| Steam Cost ($) | 102.4064 | 258.5385 | 332.5544 | 232.5 | 333.2264 | 99.7054 | 82.5929 | 80.2488 | 47.3522 | 186.8616 | 149.9566 | 167.9285
20 | UNCG - Shaw Residence Hall Renovation | [17 empty] | UNCG - Shaw Residence Hall Renovation
| Shaw Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
1310 Walker Ave
| Electricity (kWhs) | 39688 | 48238 | 48931 | 41121 | 47838 | 45675 | 41273 | 43974 | 50831 | 43055 | 45402 | 37916
| Lighting submeter (kWhs) | 10148.57 | 12423.21 | 10785.87 | 13184.44 | 12540.96 | 11514.5 | 10662.33 | 11258.65 | 12883.77 | 10929.02 | 11606.98 | 9210.32
| Mechanical submeter (kWhs) | 17296.3 | 18974.93 | 15096.58 | 17613.37 | 17491.39 | 18167.15 | 15383.39 | 15797.08 | 18786.22 | 15771.69 | 18378 | 16654.66
| Calculated plug load (kWhs) | 12243.13 | 16839.86 | 23048.55 | 10323.19 | 17805.65 | 15993.35 | 15227.28 | 16918.27 | 19161.01 | 16354.29 | 15417.02 | 12051.02
| Steam Usage (lbs) | 13120 | 19970 | 25310 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | 28310 | Note 1
| Water Usage (gallons) | 40600 | 119600 | 211600 | 214000 | 207500 | 111700 | 78300 | 80500 | 77500 | 75900 | 33900 | 18500
| Chilled water (ton-hrs) | 63820 | 69292 | 53151 | 31771 | 33290 | 32079 | 26360 | 28987 | 34651 | 34799 | 38465 | 43457
| Electricity Cost ($) | 2766.1625 | 3306.2024 | 3256.0484 | 2295.8338 | 2624.3332 | 2607.6527 | 2370.5567 | 2399.4185 | 2923.5319 | 2332.4435 | 2515.9857 | 2349.4743
| Water Costs ($) | 332.8874 | 1005.7273 | 1779.3636 | 1799.5455 | 1744.8864 | 939.2955 | 658.4318 | 676.9318 | 651.7045 | 638.25 | 285.0682 | 155.5682
| Steam Cost ($) | 102.5184 | 156.0436 | 197.7698 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | 221.2115 | Note 1
Note 1: Inaccurate Steam Meter
21 | WCU - Harrill Residence Hall Renovation | [17 empty] | WCU - Harrill Residence Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14
| Electricity (KWhs) | 52885 | 61294 | 78216 | 83548 | 74633 | 72643 | 58499 | 73775 | 69477 | 73343 | 68334 | 52440 | 48997
Steam (lbs)
Chilled Water (Dtherms)
Natural Gas (Therms)
| Water (CCF) | 12.1249 | 40.4786 | 148.5462 | 276.7328 | 233.086 | 236.0136 | 172.9162 | 219.7714 | 245.9461 | 211.8709 | 194.3319 | 62.9102 | 9.4111
| Electricity Cost ($) | 4009.5292 | 4433.6402 | 5719.9361 | 5815.275 | 4091.9035 | 4017.0853 | 3308.0015 | 4097.9061 | 3944.3482 | 4127.084 | 3802.8554 | 3112.0518 | 3561.4939
Steam Costs ($)
Chilled Water Costs ($)
Natural Gas Costs ($)
| $/kWh | 0.075816 | 0.072334 | 0.07313 | 0.069604 | 0.054827 | 0.055299 | 0.056548 | 0.055546 | 0.056772 | 0.056271 | 0.055651 | 0.059345 | 0.072688
22 | FSU - Renaissance Residence Hall | [17 empty] | FSU - Renaissance Residence Hall
No data
23 | UNCP Health Science Builidng | [17 empty] | UNCP Health Science Builidng
No data
24 | UNCA - Overlook Residence Hall | [17 empty] | UNCA - Overlook Residence Hall
UNC-Asheville Overlook Residence Hall
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
|  | Utility | Jun-16 | 2016-07-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total FY
| Duke | Electricity (KWhs) | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> |  |  |  |  | 1535525
Steam (lbs)
Chilled Water (Dtherms)
Natural Gas (Therms)
| City | Water (CCF) | 138 | 121 | 352 | 398 | 440 | 424 | 115 | 401 | 432 | 499 | 631 | [5 empty] | 3951
|  | Electricity Cost ($) | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> |  |  |  |  | 118312
Steam Costs ($)
|  | Water Costs ($) | 1803.99 | 1672.07 | 3396.97 | 3746.57 | 4245.1 | 4023.35 | 1625.51 | 3844.87 | 4073.33 | 4605.35 | 5629.67 | [5 empty] | 38666.78
Natural Gas Costs ($)
No PSNC bills paid on Overlook; no water bill paid in June of 2017 for May 2017
25 | ECSU - Viking Tower Residence Hall | [17 empty] | ECSU - Viking Tower Residence Hall
| Utility | Jun-16 | 2016-07-15 | 2016-08-15 | 2016-09-15 | 2016-10-15 | 2016-11-15 | 2016-12-15 | 2017-01-16 | 2017-02-16 | 2017-03-16 | 2017-04-16 | 2017-05-16 | 2017-06-16 | 2017-07-16 | 2017-08-16 | 2017-09-14
| Electricity (KWhs) |  | 40760 | 28119 | 58731 | 58222 | 56170 | 49151 | 53036 | 49265 | 52527 | 54793 | 48155 | 46501 | 46224
| Steam (lbs) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water (Dtherms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas (Therms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) |  | 251089 | 496833 | 713301 | 156426 | 156426 | 332819 | 310871 | 332819 | 310871 | 316938 | 265914 | 229491 | 229491
| Electricity Cost ($) |  | 3680.63 | 2539.11 | 6025.8 | 5315.67 | 5178.86 | 4482.53 | 4815.69 | 4675.21 | 4795.72 | 4597.1 | 4468.76 | 4106 | 4072.33
| Steam Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Please Note:
The water data is in gallons of water not CCF.
26 | UNCW - Teaching Lab | [17 empty] | UNCW Teaching Lab
| TEACHING LAB | 2016-07-09 | 2016-08-09 | 2016-09-09 | 2016-10-09 | 2016-11-09 | 2016-12-09 | 2017-01-09 | 2017-02-09 | 2017-03-09 | 2017-04-09 | 2017-05-09 | 2017-06-09 | TOTAL YTD
ELECTRIC
| METER READING | 4780556 | 4862214 | 4952957 | 5025962 | 5127279 | 5208837 | 5314921 | 5386179 | 5494034 | 5567737 | 5643312 | 5728982 | -----
| PREVIOUS READING | 4711130 | 4780556 | 4862214 | 4952957 | 5025962 | 5127279 | 5208837 | 5314921 | 5386179 | 5494034 | 5567737 | 5643312 | -----
| CHANGE | 69426 | 81658 | 90743 | 73005 | 101317 | 81558 | 106084 | 71258 | 107855 | 73703 | 75575 | 85670 | -----
| KWH | 69426 | 81658 | 90743 | 73005 | 101317 | 81558 | 106084 | 71258 | 107855 | 73703 | 75575 | 85670 | 1017852
| COST/KWH | 0.0806 | 0.0811 | 0.0783 | 0.0764 | 0.0731 | 0.0698 | 0.0684 | 0.0676 | 0.0677 | 0.0681 | 0.0709 | 0.0722 | 0.0726
| COST | 5595.74 | 6622.46 | 7105.18 | 5577.58 | 7406.27 | 5692.75 | 7256.15 | 4817.04 | 7301.78 | 5019.17 | 5358.27 | 6185.37 | 73937.76
WATER
| METER READING high | 1354956 | 1373867 | 1400970 | 1420283 | 1443915 | 1450409 | 1472909 | 1491142 | 1513468 | 1531355 | 1541723 | 1547258
| PREVIOUS READING | 1345346 | 1354956 | 1373867 | 1400970 | 1420283 | 1443915 | 1450409 | 1472909 | 1491142 | 1513468 | 1531355 | 1541723
| CHANGE - GAL | 9610 | 18911 | 27103 | 19313 | 23632 | 6494 | 22500 | 18233 | 22326 | 17887 | 10368 | 5535
| METER READING low | 1292530 | 1319210 | 1359671 | 1390844 | 1433996 | 1450957 | 1493176 | 1526838 | 1581052 | 1639267 | 1702397 | 1746678
| PREVIOUS READING | 1277300 | 1292530 | 1319210 | 1359671 | 1390844 | 1433996 | 1450957 | 1493176 | 1526838 | 1581052 | 1639267 | 1702397
| CHANGE - GAL | 15230 | 26680 | 40461 | 31173 | 43152 | 16961 | 42219 | 33662 | 54214 | 58215 | 63130 | 44281
| TOTAL GALLONS | 24840 | 45591 | 67564 | 50486 | 66784 | 23455 | 64719 | 51895 | 76540 | 76102 | 73498 | 49816 | 671290
| COST/GAL | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0041 | 0.0041 | 0.004 | 0.0041
| COST | 99.36 | 182.36 | 270.26 | 201.94 | 267.14 | 98.51 | 271.82 | 217.96 | 321.47 | 312.02 | 301.34 | 199.26 | 2743.44
SEWAGE
| COST/GAL | 0.0056 | 0.0047 | 0.0047 | 0.0041 | 0.0041 | 0.0044 | 0.0044 | 0.004 | 0.004 | 0.0039 | 0.0039 | 0.0031 | 0.0042
| COST | 139.1 | 214.28 | 317.55 | 206.99 | 273.81 | 103.2 | 284.76 | 207.58 | 306.16 | 296.8 | 286.64 | 154.43 | 2791.3
FUEL OIL
| GALLONS | 0 | 81.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1
| COST | 0 | 141.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.05
Wagoner Energy Plant - 32%
| ELECTRIC | 3320.36 | 3523.53 | 2983.44 | 2862.49 | 2378.34 | 1460.77 | 1968.23 | 1587.55 | 1831.34 | 2778.89 | 3555.53 | 5591.35 | 33841.82
| GAS | 2029.02 | 2046.76 | 2466.12 | 2550.69 | 3619.84 | 3622.22 | 4729.75 | 2381.03 | 3262.48 | 2140.16 | 2557.75 | 2890.63 | 34296.45
| WATER | 1130.11 | 1324.42 | 1110.14 | 545.02 | 402.43 | 135.74 | 239.1 | 220.01 | 222.03 | 575.18 | 752.83 | 1363.07 | 8020.08
- | bar: 2016-07-09 to 2017-06-09
| TOTAL UTILITIES | 12313.69 | 14054.86 | 14252.69 | 11944.71 | 14347.83 | 11113.19 | 14749.81 | 9431.17 | 13245.26 | 11122.22 | 12812.36 | 16384.11 | 155771.9
= | bar: 2016-07-09 to 2017-06-09
| TRASH | 157.84 | 177.57 | 177.57 | 177.57 | 157.84 | 118.38 | 157.84 | 157.84 | 177.57 | 157.84 | 157.84 | 78.92 | 1854.62
| Jul usage 7/6/16-8/1/16 | 2016-07-09: Sep usage 8/31/16-10/3/16; 2016-09-09: Nov usage 11/1/16-12/5/16; 2016-11-09: Jan usage 1/3/17-2/6/17; 2017-01-09: Mar usage 3/1/17-4/4/17; 2017-03-09: May usage 5/1/17-5/31/17
| Aug usage 8/1/16-8/31/16 | 2016-07-09: Oct usage 10/3/16-11/1/16; 2016-09-09: Dec usage 12/5/16-1/3/17; 2016-11-09: Feb usage 2/6/17-3/1/17; 2017-01-09: Apr usage 4/4/17-5/1/17; 2017-03-09: Jun usage 5/31/17-7/6/17
27 | UNCA - Rhoades Hall Renovation | [17 empty] | UNCA - Rhoades Hall Renovation
UNC-Asheville Rhoades Hall Renovation
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
|  | Utility | Jun-16 | 2016-07-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total FY
| Duke | Electricity (KWhs) | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> |  |  |  |  | 343680
Steam (lbs)
Chilled Water (Dtherms)
Natural Gas (Therms)
| City | Water (CCF) | 2: 322; 4: 472; 6: 42; 7: 6; 8: 146; 10: 187; 12: 234 |  |  |  |  | 1409
|  | Electricity Cost ($) | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> | >>>>>>>>> |  |  |  |  | 26480
Steam Costs ($)
|  | Water Costs ($) | 952.16 | 2257.28 | 1350.53 | 2926.89 | 73.07 | 2797.83 | 422.21 | 1621.82 | 1717.3 | 1849.52 | 577.92 | 1951.94 |  |  |  |  | 18498.47
Natural Gas Costs ($)
Renovated Rhoades Hall does not use any natural gas; Rhoades Hall is heated and cooled via ground source heat pump system which consumes electricity.
28 | ECU - Ross Hall | [17 empty] | ECU - Ross Hall
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14
| Electricity (KWhs) | 200415.37 | 227631.31 | 231203.8 | 225802.7 | 224452.68 | 212062.71 | 201626.22 | 204314.04 | 189981.17 | 221699.66 | 206590.89 | 218031.41 | 215938.68
| Steam Condensate (gal) | 12148 | 9716 | 9972 | 9564 | 11500 | 9976 | 11536 | 12440 | 9168 | 9696 | 9124 | 9256 | 9036
| Chilled Water (Tons) | 117328 | 170787 | 190439 | 154143 | 91735 | 44754 | 27373 | 25083 | 33364 | 44943 | 80069 | 109605 | 140893
| Natural Gas (CCF) | 1420 | 1619 | 2286 | 2495 | 6096 | 5052 | 6423 | 7157 | 5764 | 7718 | 4029 | 3545 | 2500
Water (kGal)
| Electricity Cost ($) | 17586.4487 | 19974.6475 | 20288.1334 | 19814.1869 | 19695.7227 | 18608.5028 | 17692.7008 | 17928.557 | 16670.8477 | 19454.1452 | 18128.3506 | 19132.2562 | 18948.6192
Steam Costs ($)
| Chilled Water Costs ($) | 6468.2926 | 9415.4873 | 10498.9021 | 8497.9036 | 5057.3506 | 2467.288 | 1509.0735 | 1382.8258 | 1839.3573 | 2477.7076 | 4414.204 | 6042.5237 | 7767.4311
| Natural Gas Costs ($) | 1267.24 | 1433.45 | 1915.36 | 2079.61 | 4922.9 | 4408.44 | 5572.56 | 6206.22 | 5256.81 | 6998.61 | 3710.23 | 3278.79 | 2312.2638
29 | Gaston College - Lena Sue Beam Renovation | [17 empty] | Gaston College - Lena Sue Beam Renovation
Gaston College - Lena Sue Beam Building
| Utility | Aug 16 | Sep 16 | Oct 16 | Nov 16 | Dec 16 | Jan 17 | Feb 17 | Mar 17 | Apr 17 | May 17 | Jun 17 | Jul 17
| Electricity (KWhs) | 23240 | 26680 | 28640 | 24480 | 24600 | 23400 | 19920 | 22720 | 21640 | 30880 | 28080 | 23160
| Steam (lbs) | 0 | 0 | 0 | 146300 | 251550 | 130650 | 117700 | 86750 | 30100 | 1550 | 500 | 0
| Chilled Water (Dtherms) | 107 | 87 | 129 | 170 | 34 | 88 | 56 | 91 | 103 | 207 | 221 | 333
| Natural Gas (Therms) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) | 19775 | 12756 | 11815 | 10801 | 6589 | 8199 | 5742 | 6154 | 9329 | 10700 | 2737 | 1726
| Electricity Cost ($) | 1998.6738 | 2139.2879 | 1932.5045 | 1804.0006 | 1787.858 | 1590.3275 | 1531.0812 | 1568.6143 | 1505.1 | 3952.5862 | 2235.787 | 2061.0835 | 0 | 0
| Steam Costs ($) | 0 | 0 | 0 | 1461.07 | 2527.86 | 1487.07 | 1354.42 | 1037.45 | 428.85 | 103.28 | 91.3 | 0 | 0 | 0
| Chilled Water Costs ($) | 859.21 | 698.61 | 1035.87 | 1365.1 | 273.02 | 706.64 | 449.68 | 730.73 | 827.09 | 1662.21 | 1774.63 | 2673.99
| Natural Gas Costs ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electricity cost per kwh | 0.086001 | 0.080183 | 0.067476 | 0.073693 | 0.072677 | 0.067963 | 0.076862 | 0.069041 | 0.069552 | 0.128 | 0.079622 | 0.088993 | 0 | 0
| Water cost per billed unit | 0.013437 | 0.013445 | 0.013438 | 0.013439 | 0.013435 | 0.013424 | 0.013433 | 0.013436 | 0.013435 | 0.013432 | 0.01343 | 0.014918
| Natural gas cost per therm | 0 | 0 | 6.3928 | 0.49198 | 0.46654 | 0.55115 | 0.5688 | 0.56715 | 0.62433 | 0.61876 | 0 | 0
30 | NCSU - Hunt Library | [17 empty] | NCSU - Hunt Library
NCSU - Hunt Library
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 389879.8828 | 371120.1172 | 376119.1406 | 355480.4688 | 348480.4688 | 351609.375 | 321339.8438 | 359160.1562 | 351919.9219 | 363299.8047 | 345959.9609 | 358800.7812 | 4293169.9219 | kwh |  | 14637.6144 | MMbtu
| Chilled Water (Dtherms) |  | 1498.92 | 1163.152 | 647.624 | 311.992 | 148.496 | 192.608 | 278.592 | 313.104 | 650.4 | 814.8 | 1041.696 | 1385.104 | 8446.488 | dthrms |  | 8446.488 | MMbtu
| Steam (1,000 lbs) |  | 273.3802 | 277.0636 | 316.54 | 465.3086 | 697.3902 | 723.3824 | 436.3228 | 168.8075 | 325.2032 | 302.7122 | 274.89 | 279.6381 | 4540.6387 | 1000 lbs |  | 4540.6387 | MMbtu
| Water (CCF) |  | 41 | 137 | 171 | 150 | 123 | 61 | 42 | 39 | 38 | 30 | 29 | 39 | 900 | CCF |  | 1401632.32 | gallons | *This includes water and reuse water.
| Reuse Water (CCF) |  | 93.72 | 92.24 | 92.24 | 0 | 0 | 0.01 | 147.31 | 149.56 | 144.06 | 123.94 | 73.4 | 57.36 | 973.84 | CCF
| Electric Cost ($) |  | 33919.5498 | 32287.4502 | 32722.3652 | 30926.8008 | 30317.8008 | 30590.0156 | 27956.5664 | 31246.9336 | 30617.0332 | 31607.083 | 30098.5166 | 29780.4648 | 372070.5801 | $
| Chilled Water Cost ($) |  | 19411.014 | 15062.8184 | 8386.7308 | 4040.2964 | 1923.0232 | 2494.2736 | 3607.7664 | 4054.6968 | 8422.68 | 10551.66 | 13489.9632 | 17673.927 | 109118.8498 | $
| Steam Cost ($) |  | 3286.0299 | 3330.3046 | 3804.8108 | 5593.0093 | 8382.6302 | 8695.0565 | 5244.6 | 2029.0655 | 3908.9425 | 3638.6006 | 3304.1778 | 3861.8022 | 55079.0299 | $
| Water Cost ($) |  | 382.53 | 1278.21 | 1595.43 | 1399.5 | 1147.59 | 569.13 | 391.86 | 363.87 | 354.54 | 279.9 | 270.57 | 366.21 | 8399.34 | $
| Reuse Water Cost ($) |  | 252.1068 | 248.1256 | 248.1256 | 0 | 0 | 0.0269 | 396.2639 | 402.3164 | 387.5214 | 333.3986 | 197.446 | 154.2984 | 2619.6296 | $
31 | Military and Veterans Affairs - NC State Veterans Home - Kinston | [17 empty] | Military and Veterans Affairs - NC State Veterans Home - Kinston
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | TOTAL
| Electricity (KWhs) | 186400 | 228400 | 267200 | 259600 | 238600 | 185782 | 192800 | 164800 | 154000 | 187200 | 197200 | 205800 | 245400
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) | 1881 | 1541 | 1580 | 1726 | 1589 | 1727 | 1956 | 1816 | 1896 | 1771 | 1800 | 1664
| Water (CCF) | 318000 | 313300 | 287700 | 256200 | 271400 | 237900 | 264900 | 287500 | 243600 | 257300 | 253100 | 298800 | 339600
| Electricity Cost ($) | 16067.44 | 19309.93 | 22503.72 | 21965.9 | 20274.3 | 15431.87 | 15300.75 | 13473.58 | 12739.07 | 15124.01 | 16073.57 | 16367.9 | 19484.67 |  |  | 224116.71
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 1402.88 | 1155.31 | 1183.96 | 1291.18 | 1190.55 | 1158.24 | 1741.61 | 1650.18 | 1720.6 | 1608.72 | 1573.33 | 1464.82 |  |  |  | 17141.38
| WATER $ COST | 2014.97 | 2053.2 | 1855.26 | 1682.99 | 1764.62 | 1652.86 | 1729.71 | 1851.08 | 1643.1 | 1688.9 | 1666.35 | 1911.76 | 2159.53 |  |  | 23674.33
| TOTAL: | 19485.29 | 22518.44 | 25542.94 | 24940.07 | 23229.47 | 18242.97 | 18772.07 | 16974.84 | 16102.77 | 18421.63 | 19313.25 | 19744.48 | 21644.2 |  |  | 264932.42
32 | UNCC - Rose Football Center | [17 empty] | UNCC - Rose Football Center
No data
33 | Randolph CC - Continuing Education Industrial Center | [17 empty] | Randolph CC - Klaussner Building Renovation
| Randolph | Community | 1: College; 3: 2016-2017; 5: Continuing; 6: Education; 7: Industrial; 8: Center
|  | July | August | September | October | November | December | January | February | March | April | May | June | Totals
| 053 029 3190 TJ9935 CEIC |  | 5: Power
| kWh Usage | 86300 | 76900 | 84500 | 70100 | 57800 | 52900 | 53100 | 53300 | 54700 | 70500 | 62000 | 72100 | 794200
| KW | 175 | 164 | 165 | 161 | 131 | 140 | 170 | 175 | 185 | 216 | 164 | 180 | 168.8333
| Days in period | 32 | 28 | 30 | 29 | 29 | 32 | 35 | 29 | 29 | 32 | 29 | 30
| Amount | 6354.08 | 5738.98 | 6286.45 | 5094.58 | 4189.74 | 3801.62 | 3418.71 | 3534.2 | 3589.32 | 4478.32 | 4345.68 | 5151.78 | 55983.46
| Lighting | 743 | 767.33 | 767.06 | 767.03 | 767.03 | 726.04 | 697.62 | 697.43 | 697.43 | 697.43 | 697.43 | 697.43 | 8722.26
| 7% Sales Tax | 496.8 | 455.44 | 488.87 | 410.31 | 346.99 | 316.94 | 288.14 | 296.21 | 300.07 | 362.3 | 349.14 | 409.44 | 4520.65
| Total Bill | 7593.88 | 6961.75 | 7542.38 | 6271.92 | 5303.76 | 4844.6 | 4404.47 | 4527.84 | 4586.82 | 5538.05 | 5392.25 | 6258.65 | 69226.37
| 1003287462001 859461 CEIC 413 Industrial Pk |  | 5: Natural Gas
| Therms Used | 465 | 577 | 513 | 695 | 1109 | 1311 | 1615 | 1156 | 1435 | 874 | 569 | 389 | 10708
| Amount | 341.17 | 418.05 | 374.12 | 524.64 | 909.66 | 1120.54 | 1372.98 | 989.02 | 1166.33 | 729.49 | 483.53 | 340.5 | 8770.03
| State Sales Tax | 23.88 | 29.26 | 26.19 | 36.72 | 63.68 | 78.44 | 96.11 | 69.23 | 81.64 | 51.06 | 33.85 | 23.84 | 613.9
| Total Bill | 365.05 | 447.31 | 400.31 | 561.36 | 973.34 | 1198.98 | 1469.09 | 1058.25 | 1247.97 | 780.55 | 517.38 | 364.34 | 9383.93
| 83301 1830392826 CEIC 413 Ind. Pk. Ave. |  | 5: Domestic Water
| Usage (CF) | 184 | 27 | 3 | 146 | 10 | 0 | 0 | 150 | 215 | 209 | 142 | 152 | 1238
| Days in Period | 29 | 33 | 29 | 30 | 32 | 28 | 35 | 27 | 30 | 27 | 28 | 35
| Water | 14.84 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 15.69 | 15.53 | 13.91 | 13.96 | 171.3
| Sewer | 18.14 | 17.18 | 17.18 | 17.18 | 17.18 | 17.18 | 17.18 | 17.18 | 19.01 | 18.84 | 17.18 | 17.24 | 210.67
| Total | 32.98 | 31.09 | 31.09 | 31.09 | 31.09 | 31.09 | 31.09 | 31.09 | 34.7 | 34.37 | 31.09 | 31.2 | 381.97
34 | ASU - Plemmons Student Union Addition | [17 empty] | ASU - Plemmons Student Union Addition
ELECTRICITY
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 124302.36 | 136673.48 | 154241.2 | 154193.12 | 150620.96 | 124908 | 100757.2 | 142079.84 | 126422.8 | 146194.96 | 153701.56 | 92243
| 315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 90183.92 | 75576.56 | 97576.4 | 83684.64 | 70809.12 | 57196 | 34628.4 | 60848.48 | 55911.6 | 67107.12 | 74650.32 | 51248
| 452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 86886.72 | 100976.96 | 121742.4 | 106562.24 | 94529.92 | 77896 | 67854.4 | 83151.68 | 77425.6 | 91417.92 | 88109.12 | 79328
| 239 | Belk Residence Hall Total Electricity Use | 51000 | 52560 | 65280 | 50280 | 38640 | 32280 | 27600 | 34440 | 34080 | 37320 | 36480 | 30480
| 204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 10055.6008 | 11052.1161 | 12467.197 | 12463.3377 | 12175.592 | 10104.3948 | 8159.0232 | 11847.9085 | 10867.3251 | 12560.2146 | 13202.9423 | 7940.8564
| 315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 7278.9497 | 6102.3156 | 7874.4201 | 6755.4264 | 5718.2861 | 4621.7522 | 2803.9183 | 5070.1961 | 4801.7408 | 5760.2983 | 6406.156 | 4402.4387
| 452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 7028.1895 | 8163.1882 | 9835.853 | 8613.0759 | 7643.8719 | 6303.993 | 5495.1385 | 6938.1154 | 6658.6142 | 7856.6571 | 7573.3617 | 6821.5049
| 239 | Belk Residence Hall Total Electricity Cost | 4120.51 | 4246.17 | 5270.77 | 4062.51 | 3124.9 | 2612.6 | 2235.63 | 2870.88 | 2930.37 | 3207.77 | 3135.85 | 2622.13
STEAM
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 292804.2 | 311990.8 | 263607.2 | 227736.5992 | 376224.2 | 459644.2 | 623981.6 | 372887.4 | 511364.6 | 386234.6 | 488007 | 330343.1992
| 315 | Cone Residence Hall Steam Use in Lbs. | 70907 | 87591 | 136808.8 | 139311.4 | 241918 | 150990.2 | 226902.4 | 146819.2 | 222731.4 | 121793.2 | 102606.6 | 73409.6
| 452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 221897.2 | 250260 | 302814.6 | 260270.4 | 444628.6 | 537224.8 | 506359.4 | 471323 | 412929 | 266944 | 260270.4 | 253596.8
| 239 | Belk Residence Hall Steam Use in lbs. | 33368 | 39207.4 | 55057.2 | 47549.4 | 68404.4 | 90927.8 | 95933 | 77580.6 | 94264.6 | 49217.8 | 38373.2 | 39207.4
| 204 & 445 | Plemmons Student Union Total Steam Cost | 6149.52 | 6552.48 | 5536.32 | 4782.96 | 7901.52 | 9653.52 | 13104.96 | 7831.44 | 10739.76 | 8111.76 | 10249.2 | 8589.24
| 315 | Cone Residence Hall Steam Costs | 1489.2 | 1839.6 | 2873.28 | 2925.84 | 5080.8 | 3171.12 | 4765.44 | 3083.52 | 4677.84 | 2557.92 | 2154.96 | 1908.72
| 452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 5426 | 6119.55 | 7404.66 | 6364.33 | 10872.4 | 13136.64 | 12381.89 | 11525.15 | 10097.26 | 6527.52 | 6364.33 | 7278.68
| 239 | Belk Residence Hall Steam Cost | 700.8 | 823.44 | 1156.32 | 998.64 | 1436.64 | 1909.68 | 2014.8 | 1629.36 | 1979.76 | 1033.68 | 805.92 | 1019.43
WATER & SEWER
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 347964.0001 | 386276 | 446391 | 292376 | 228639 | 69000 | 128000 | 213000 | 208295 | 298425.0001 | 287539 | 287916
| 315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 146908 | 171372 | 218777 | 168072 | 159633 | 50000 | 112000 | 174000 | 155865 | 155975 | 94933 | 57452
| 452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 117128 | 239352 | 362832 | 265552 | 246728 | 75000 | 173000 | 270000 | 245840 | 263600 | 157528 | 90632
| 239 | Belk Residence Hall Water Use | 57000 | 113000 | 230000 | 126000 | 97000 | 32000 | 76000 | 108000 | 104000 | 111000 | 54000 | 48000
| 204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 3726.0804 | 2995.2108 | 3627.3685 | 3822.692 | 2974.6506 | 1984.5 | 1298.2 | 2999 | 2198.6915 | 2480.1725 | 4088.5659 | 3343.0792
| 315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 1530.6388 | 1330.0276 | 1725.2195 | 2040.824 | 1912.5182 | 1419 | 1071.8 | 2498 | 1737.7005 | 1614.6075 | 1728.4573 | 867.2024
| 452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 942.9808 | 1122.3616 | 2603.412 | 3106.984 | 2945.3312 | 2156 | 1634.7 | 3864.5 | 2704.608 | 2601.32 | 2849.9768 | 1336.4184
| 239 | Belk Residence Hall Water & Sewer Cost | 347.7 | 372.9 | 805 | 567 | 523.8 | 240 | 486.4 | 1080 | 384.8 | 410.7 | 437.4 | 297.6
35 | ASU - Summit Residence Hall and Appalachian Hall | [17 empty] | ASU - Summit Residence Hall and Appalachian Hall
ELECTRICITY
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 124302.36 | 136673.48 | 154241.2 | 154193.12 | 150620.96 | 124908 | 100757.2 | 142079.84 | 126422.8 | 146194.96 | 153701.56 | 92243
| 315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 90183.92 | 75576.56 | 97576.4 | 83684.64 | 70809.12 | 57196 | 34628.4 | 60848.48 | 55911.6 | 67107.12 | 74650.32 | 51248
| 452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 86886.72 | 100976.96 | 121742.4 | 106562.24 | 94529.92 | 77896 | 67854.4 | 83151.68 | 77425.6 | 91417.92 | 88109.12 | 79328
| 239 | Belk Residence Hall Total Electricity Use | 51000 | 52560 | 65280 | 50280 | 38640 | 32280 | 27600 | 34440 | 34080 | 37320 | 36480 | 30480
| 204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 10055.6008 | 11052.1161 | 12467.197 | 12463.3377 | 12175.592 | 10104.3948 | 8159.0232 | 11847.9085 | 10867.3251 | 12560.2146 | 13202.9423 | 7940.8564
| 315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 7278.9497 | 6102.3156 | 7874.4201 | 6755.4264 | 5718.2861 | 4621.7522 | 2803.9183 | 5070.1961 | 4801.7408 | 5760.2983 | 6406.156 | 4402.4387
| 452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 7028.1895 | 8163.1882 | 9835.853 | 8613.0759 | 7643.8719 | 6303.993 | 5495.1385 | 6938.1154 | 6658.6142 | 7856.6571 | 7573.3617 | 6821.5049
| 239 | Belk Residence Hall Total Electricity Cost | 4120.51 | 4246.17 | 5270.77 | 4062.51 | 3124.9 | 2612.6 | 2235.63 | 2870.88 | 2930.37 | 3207.77 | 3135.85 | 2622.13
STEAM
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 292804.2 | 311990.8 | 263607.2 | 227736.5992 | 376224.2 | 459644.2 | 623981.6 | 372887.4 | 511364.6 | 386234.6 | 488007 | 330343.1992
| 315 | Cone Residence Hall Steam Use in Lbs. | 70907 | 87591 | 136808.8 | 139311.4 | 241918 | 150990.2 | 226902.4 | 146819.2 | 222731.4 | 121793.2 | 102606.6 | 73409.6
| 452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 221897.2 | 250260 | 302814.6 | 260270.4 | 444628.6 | 537224.8 | 506359.4 | 471323 | 412929 | 266944 | 260270.4 | 253596.8
| 239 | Belk Residence Hall Steam Use in lbs. | 33368 | 39207.4 | 55057.2 | 47549.4 | 68404.4 | 90927.8 | 95933 | 77580.6 | 94264.6 | 49217.8 | 38373.2 | 39207.4
| 204 & 445 | Plemmons Student Union Total Steam Cost | 6149.52 | 6552.48 | 5536.32 | 4782.96 | 7901.52 | 9653.52 | 13104.96 | 7831.44 | 10739.76 | 8111.76 | 10249.2 | 8589.24
| 315 | Cone Residence Hall Steam Costs | 1489.2 | 1839.6 | 2873.28 | 2925.84 | 5080.8 | 3171.12 | 4765.44 | 3083.52 | 4677.84 | 2557.92 | 2154.96 | 1908.72
| 452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 5426 | 6119.55 | 7404.66 | 6364.33 | 10872.4 | 13136.64 | 12381.89 | 11525.15 | 10097.26 | 6527.52 | 6364.33 | 7278.68
| 239 | Belk Residence Hall Steam Cost | 700.8 | 823.44 | 1156.32 | 998.64 | 1436.64 | 1909.68 | 2014.8 | 1629.36 | 1979.76 | 1033.68 | 805.92 | 1019.43
WATER & SEWER
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 347964.0001 | 386276 | 446391 | 292376 | 228639 | 69000 | 128000 | 213000 | 208295 | 298425.0001 | 287539 | 287916
| 315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 146908 | 171372 | 218777 | 168072 | 159633 | 50000 | 112000 | 174000 | 155865 | 155975 | 94933 | 57452
| 452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 117128 | 239352 | 362832 | 265552 | 246728 | 75000 | 173000 | 270000 | 245840 | 263600 | 157528 | 90632
| 239 | Belk Residence Hall Water Use | 57000 | 113000 | 230000 | 126000 | 97000 | 32000 | 76000 | 108000 | 104000 | 111000 | 54000 | 48000
| 204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 3726.0804 | 2995.2108 | 3627.3685 | 3822.692 | 2974.6506 | 1984.5 | 1298.2 | 2999 | 2198.6915 | 2480.1725 | 4088.5659 | 3343.0792
| 315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 1530.6388 | 1330.0276 | 1725.2195 | 2040.824 | 1912.5182 | 1419 | 1071.8 | 2498 | 1737.7005 | 1614.6075 | 1728.4573 | 867.2024
| 452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 942.9808 | 1122.3616 | 2603.412 | 3106.984 | 2945.3312 | 2156 | 1634.7 | 3864.5 | 2704.608 | 2601.32 | 2849.9768 | 1336.4184
| 239 | Belk Residence Hall Water & Sewer Cost | 347.7 | 372.9 | 805 | 567 | 523.8 | 240 | 486.4 | 1080 | 384.8 | 410.7 | 437.4 | 297.6
36 | UNCW - MARBIONC | [17 empty] | UNCW - MARBIONC
| BIOTECHNOLOGY FACILITY | 2016-07-09 | 2016-08-09 | 2016-09-09 | 2016-10-09 | 2016-11-09 | 2016-12-09 | 2017-01-09 | 2017-02-09 | 2017-03-09 | 2017-04-09 | 2017-05-09 | 2017-06-09 | TOTAL YTD
ELECTRIC
| ON PEAK KWH | 150000 | 154400 | 134200 | 103000 | 77800 | 82600 | 82600 | 81000 | 84000 | 102400 | 106000 | 133800 | 1291800
| OFF PEAK KWH | 292200 | 243400 | 221600 | 172600 | 146800 | 164200 | 164200 | 133800 | 150600 | 173800 | 184200 | 250200 | 2297600
| TOTAL KWH | 442200 | 397800 | 355800 | 275600 | 224600 | 246800 | 246800 | 214800 | 234600 | 276200 | 290200 | 384000 | 3589400
| DEMAND | 774 | 752 | 686 | 599 | 458 | 488 | 488 | 502 | 460 | 606 | 630 | 712 | 7155
| COST | 30515.3 | 28286.59 | 25406.57 | 19075.83 | 15034.82 | 14797.45 | 14797.45 | 13593.9 | 14025.56 | 17104.86 | 18062.83 | 24481.15 | 235182.31
GAS
| MCF | 585.5 | 702.6 | 604.3 | 821.2 | 906 | 1117.1 | 1192.9 | 870.2 | 972 | 686.9 | 817.9 | 399 | 9675.6
| COST | 4061.98 | 4838.99 | 4197.25 | 5492.28 | 7641.91 | 9725.28 | 10328.96 | 7613.44 | 7878.41 | 5752.69 | 6796.48 | 3443.57 | 77771.24
WATER
| METER READING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PREVIOUS READING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GAL CHANGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST/GAL | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0041 | 0.0041 | 0.004 | #DIV/0!
| COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEWAGE
| COST/GAL | 0.0056 | 0.0047 | 0.0047 | 0.0041 | 0.0041 | 0.0044 | 0.0044 | 0.004 | 0.004 | 0.0039 | 0.0039 | 0.0031 | #DIV/0!
| COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2016-07-09 to 2017-06-09
| TOTAL UTILITIES | 34577.28 | 33125.58 | 29603.82 | 24568.11 | 22676.73 | 24522.73 | 25126.41 | 21207.34 | 21903.97 | 22857.55 | 24859.31 | 27924.72 | 312953.55
= | bar: 2016-07-09 to 2017-06-09
| TOTAL TRASH | 256.49 | 276.22 | 256.49 | 256.49 | 256.49 | 256.49 | 256.49 | 236.76 | 276.22 | 236.76 | 256.49 | 256.49 | 3077.88
BIOTECHNOLOGY - 25%
| ELECTRIC | 7628.83 | 7071.65 | 6351.64 | 4768.96 | 3758.71 | 3699.36 | 3699.36 | 3398.48 | 3506.39 | 4276.22 | 4515.71 | 6120.29 | 58795.6
| GAS | 1015.5 | 1209.75 | 1049.31 | 1373.07 | 1910.48 | 2431.32 | 2582.24 | 1903.36 | 1969.6 | 1438.17 | 1699.12 | 860.89 | 19442.81
| WATER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SEWER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2016-07-09 to 2017-06-09
| TOTAL UTILITIES | 8644.33 | 8281.4 | 7400.95 | 6142.03 | 5669.19 | 6130.68 | 6281.6 | 5301.84 | 5475.99 | 5714.39 | 6214.83 | 6981.18 | 78238.41
= | bar: 2016-07-09 to 2017-06-09
| TRASH | 64.12 | 69.06 | 64.12 | 64.12 | 64.12 | 64.12 | 64.12 | 59.19 | 69.06 | 59.19 | 64.12 | 64.12 | 769.46
UNCW - 75%
| ELECTRIC | 22886.48 | 21214.94 | 19054.93 | 14306.87 | 11276.12 | 11098.09 | 11098.09 | 10195.43 | 10519.17 | 12828.65 | 13547.12 | 18360.86 | 176386.75
| GAS | 3046.49 | 3629.24 | 3147.94 | 4119.21 | 5731.43 | 7293.96 | 7746.72 | 5710.08 | 5908.81 | 4314.52 | 5097.36 | 2582.68 | 58328.44
| WATER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SEWER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2016-07-09 to 2017-06-09
| TOTAL UTILITIES | 25932.97 | 24844.18 | 22202.87 | 18426.08 | 17007.55 | 18392.05 | 18844.81 | 15905.51 | 16427.98 | 17143.17 | 18644.48 | 20943.54 | 234715.19
= | bar: 2016-07-09 to 2017-06-09
| TRASH | 192.37 | 207.17 | 192.37 | 192.37 | 192.37 | 192.37 | 192.37 | 177.57 | 207.17 | 177.57 | 192.37 | 192.37 | 2308.44
No water or sewer charges. No water meter at the facility and awaiting information about how to charge for water and sewer.
37 | DOA - NC State Bar HQ | [17 empty] | DOA - NC State Bar HQ
The North Carolina State Bar-Electricity and Water Usage 6/2016 thru 8/2017
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01
| Electricity Usage (KWhs) | 74800 | 69600 | 69200 | 71200 | 69400 | 79000 | 68200 | 94200 | 73400 | 81800 | 75000 | 72000 | 39200 | 102800 | 0
| Water Usage (CCF) | 32 | 28 | 22 | 18 | 19 | 18 | 18 | 13 | 19 | 27 | 18 | 19 | 18 | 21 | 0
0
| Elecricity Cost ($) | 6664.63 | 6292.33 | 6227.6 | 6398.76 | 6359.65 | 6998.26 | 6082.92 | 7699.57 | 6181.56 | 6752.66 | 6325.78 | 6050.78 | 3773.09 | 8097.79 | 0
| Water-Sewer Costs ($) | 513.21 | 535.55 | 489.76 | 459.23 | 540.86 | 533.23 | 533.23 | 495.07 | 540.86 | 601.92 | 533.23 | 540.86 | 533.23 | 569.38 | 0
38 | FSU - Science and Technology Building | [17 empty] | FSU - Science and Technology Building
No data
39 | UNCW - Student Rec Facility Addition | [17 empty] | UNCW - Student Rec Facility Addition
| RECREATION CENTER | 2016-07-09 | 2016-08-09 | 2016-09-09 | 2016-10-09 | 2016-11-09 | 2016-12-09 | 2017-01-09 | 2017-02-09 | 2017-03-09 | 2017-04-09 | 2017-05-09 | 2017-06-09 | TOTAL YTD
ELECTRIC
| METER READING | 29710 | 29875 | 30054 | 30185 | 30343 | 30453 | 30606 | 30715 | 30869 | 30996 | 31130 | 31295
| PREVIOUS READING | 29575 | 29710 | 29875 | 30054 | 30185 | 30343 | 30453 | 30606 | 30715 | 30869 | 30996 | 31130
| CHANGE | 135 | 165 | 179 | 131 | 158 | 110 | 153 | 109 | 154 | 127 | 134 | 165
| KWH (CHANGE X1000) | 135000 | 165000 | 179000 | 131000 | 158000 | 110000 | 153000 | 109000 | 154000 | 127000 | 134000 | 165000 | 1720000
| COST/KWH | 0.0806 | 0.0811 | 0.0783 | 0.0764 | 0.0731 | 0.0698 | 0.0684 | 0.0676 | 0.0677 | 0.0681 | 0.0709 | 0.0722 | 0.0732
| COST | 10881 | 13381.5 | 14015.7 | 10008.4 | 11549.8 | 7678 | 10465.2 | 7368.4 | 10425.8 | 8648.7 | 9500.6 | 11913 | 125836.1
GAS
| METER READING | 12209 | 12225 | 12246 | 12265 | 12285 | 12297 | 12321 | 12340 | 12364 | 12384 | 12399 | 12417
| PREVIOUS READING | 12196 | 12209 | 12225 | 12246 | 12265 | 12285 | 12297 | 12321 | 12340 | 12364 | 12384 | 12399
| MCF CHANGE | 13 | 16 | 21 | 19 | 20 | 12 | 24 | 19 | 24 | 20 | 15 | 18 | 221
| COST/MCF | 5.13 | 4.89 | 4.89 | 5.01 | 5.05 | 5.79 | 6.46 | 6.02 | 5.17 | 5.5 | 5.52 | 5.71 | 5.44
| COST | 66.69 | 78.24 | 102.69 | 95.19 | 101 | 69.48 | 155.04 | 114.38 | 124.08 | 110 | 82.8 | 102.78 | 1202.37
WATER
| METER READING | 35689000 | 35689000 | 35689000 | 35899600 | 35993000 | 36027100 | 36158500 | 36274500 | 36422810 | 36508100 | 36580000 | 36664900
| PREVIOUS READING | 35689000 | 35689000 | 35689000 | 35689000 | 35899600 | 35993000 | 36027100 | 36158500 | 36274500 | 36422810 | 36508100 | 36580000
| CHANGE IN GAL | 0 | 0 | 0 | 210600 | 93400 | 34100 | 131400 | 116000 | 148310 | 85290 | 71900 | 84900 | 975900
| COST/GAL | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0041 | 0.0041 | 0.004 | 0.0041
| COST | 0 | 0 | 0 | 842.4 | 373.6 | 143.22 | 551.88 | 487.2 | 622.9 | 349.69 | 294.79 | 339.6 | 4005.28
SEWAGE
| COST/GAL | 0.0056 | 0.0047 | 0.0047 | 0.0041 | 0.0041 | 0.0044 | 0.0044 | 0.004 | 0.004 | 0.0039 | 0.0039 | 0.0031 | 0.004
| COST | 0 | 0 | 0 | 863.46 | 382.94 | 150.04 | 578.16 | 464 | 593.24 | 332.63 | 280.41 | 263.19 | 3908.07
FUEL OIL
| GAL | 0 | 81.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1
| COST | 0 | 141.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.05
- | bar: 2016-07-09 to 2017-06-09
CAMPUS REC - 26%
| ELECTRIC | 2697.79 | 2862.87 | 2424.05 | 2325.78 | 1932.4 | 1186.88 | 1599.19 | 1289.89 | 1487.97 | 2257.85 | 2888.87 | 4542.97
| GAS | 1648.58 | 1662.99 | 2003.73 | 2072.44 | 2941.12 | 2943.06 | 3842.92 | 1934.59 | 2650.76 | 1738.88 | 2078.17 | 2348.64
| WATER | 918.22 | 1076.09 | 901.99 | 442.83 | 326.98 | 110.29 | 194.27 | 178.76 | 180.4 | 467.33 | 611.67 | 1107.5
| TOTAL UTILITIES | 10947.69 | 19202.74 | 19448.16 | 16650.5 | 17607.84 | 12280.97 | 17386.66 | 11837.22 | 16085.15 | 13905.08 | 15737.31 | 20617.68 | 191707
= | bar: 2016-07-09 to 2017-06-09
TRASH
| BASIC SERVICE | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 39.46 | 39.46 | 512.98
| EXTRA PICK UP | 0 | 0 | 0 | 19.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.73
- | bar: 2016-07-09 to 2017-06-09
| TOTAL TRASH | 39.46 | 59.19 | 39.46 | 59.19 | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 39.46 | 39.46 | 532.71
= | bar: 2016-07-09 to 2017-06-09
Gross Sqft: 69644
Net Sqft: 65721
Last fiscal year Jun-16 water - Documented wrong number causing very large usage total. Will enter same reading in fy16-17 until reading catches up with June's incorrect reading.
Oct - additional trash pickup in preperation of hurricane Matthew.
Nov water corrected. Charged .04 more than should have. Campus Rec billed 373.64 but should have been 373.60.
| Jul usage 7/6/16-8/1/16 | 2016-07-09: Sep usage 8/31/16-10/3/16; 2016-09-09: Nov usage 11/1/16-12/5/16; 2016-11-09: Jan usage 1/3/17-2/6/17; 2017-01-09: Mar usage 3/1/17-4/4/17; 2017-03-09: May usage 5/1/17-5/31/17
| Aug usage 8/1/16-8/31/16 | 2016-07-09: Oct usage 10/3/16-11/1/16; 2016-09-09: Dec usage 12/5/16-1/3/17; 2016-11-09: Feb usage 2/6/17-3/1/17; 2017-01-09: Apr usage 4/4/17-5/1/17; 2017-03-09: Jun usage 5/31/17-7/6/17
40 | WSSU - Reaves Student Activities Center | [17 empty] | WSSU - Reaves Student Activities Center
Winston-Salem State University
Donald J. Reaves Student Activities Center
| Utility | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| Electricity (KWH) building meter | 70789 | 90642 | 103653 | 106555 | 107163 | 90691 | 126671 | 75986 | 102972 | 100858 | 66790 | 61469
| Steam from Central Plant (lbs) - natural gas therms | 0 | 0 | 0 | 0 | 0 | 9691.6796 | 9112.5576 | 7083.3684 | 7814.0575 | 5964.9739 | 0 | 0
| Chilled Water from Central Plant (Dtherms) kwh | 133783.6185 | 147811.3378 | 119652.9365 | 67415.1099 | 57316.9478 | 53033.1632 | 64641.8173 | 43003.3451 | 88241.4945 | 143721.8646 | 93238.2009 | 77154.5777
| Natural Gas (Therms) other than from central steam plant | 1344 | 2163 | 2692 | 2679 | 3195 | 1314 | 874 | 827 | 783 | 2276 | 1834 | 1135
| Water (CCF) | 19.02 | 328.73 | 328.73 | 364.26 | 19.39 | 689.84 | 353.88 | 411.87 | 284.27 | 193.1 | 207.25 | 180.96
| Electricity Cost ($) building meter x blended rate ($.0712/kwh) | 5037.617 | 6450.4327 | 7376.3454 | 7582.8628 | 7626.1304 | 6453.9197 | 9014.3946 | 5407.4554 | 7327.8828 | 7177.4424 | 4753.0328 | 4374.37
| Steam from Central Plant Cost ($) for Natural Gas | 0 | 0 | 0 | 0 | 0 | 5540.6226 | 3951.6975 | 3750.1011 | 3182.6599 | 1587.1031 | 0 | 0
| Chilled Water from Central Plant Cost ($) kwh x $.0712/kwh | 9520.5558 | 10518.8222 | 8514.9623 | 4797.518 | 4078.894 | 3774.0435 | 4600.1599 | 3060.2831 | 6279.6035 | 10227.7996 | 6635.1883 | 5490.6159
| Natural Gas Costs ($) other than from central steam. | 944.51 | 1506.66 | 1869.76 | 1945.33 | 2557.42 | 1123.22 | 753.12 | 713.8 | 644.51 | 1864.4 | 1506.6 | 951.29
| Water Costs ($) | 258.36 | 1916.505 | 1916.505 | 2275.34 | 289.8 | 3954.02 | 2216.94 | 2540.29 | 1858.04 | 1378.92 | 1490.14 | 1300.43
41 | Haywood Community College - Creative Arts Building | [17 empty] | Haywood Community College - Creative Arts Building
Haywood Community College - Creative Arts Building
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01
| Electricity (KWhs) |  |  | 27521 | 27735.53 | 20205 | 19726.83 | 16030.75 | 16441.895 | 18656.95 | 20884.188 | 22695.627 | 22662.143 | 21777.506 | 25951.064
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) |  |  | 39 | 3 | 231 | 443 | 1612 | 1890 | 1376 | 1616 | 862 | 668 | 136 | 73
| Water (CCF) |  |  | 2851 | 3109.74 | 1253.96 | 1083.29 | 373 | 567 | 3979 | 1159.79 | 1353.27 | 1630.825 | 1490.858 | 1881.7473
| Electricity Cost ($) |  |  | 2752 | 2773.553 | 2020.5 | 1972.68 | 1603.075 | 1644 | 1865.695 | 2088.4188 | 2269.56 | 2266.2143 | 2177.75 | 2595.11
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) |  |  | 45.4 | 20.78 | 177.94 | 333.27 | 1141.4 | 1394 | 1091.72 | 1276.32 | 708.51 | 564.83 | 131.74 | 79.38
42 | UNCC - Belk Residence Hall | [17 empty] | UNCC - Belk Residence Hall
No data
43 | NCSU - Early College High School / Cherry Building Renovation | [17 empty] | NCSU - Early College High School / Cherry Building Renovation
NCSU - Early College High School/Cherry
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 38320.0073 | 31811.0352 | 26853.0273 | 25903.9307 | 25402.9541 | 26928.1006 | 23670.8984 | 26217.041 | 25682.9834 | 28046.0205 | 26443.9697 | 30530.0293 | 335809.9976 | kwh |  | 1144.9482 | MMbtu
| Water (CCF) |  | 3.2 | 10.9 | 10.3 | 11 | 6.9 | 6.1 | 9.3 | 31.2 | 9.5 | 9.5 | 2.5 | 1.2 | 111.6 | CCF |  | 83476.8 | gallons
| Natural Gas (therms) |  | 99 | 181 | 264 | 731 | 1648 | 740 | 592 | 530 | 228 | 231 | 143 | 120 | 5507 | therms |  | 5507 | thrms
| Electric Cost ($) |  | 3333.8406 | 2767.5601 | 2336.2134 | 2253.642 | 2210.057 | 2342.7448 | 2059.3682 | 2280.8826 | 2234.4196 | 2440.0038 | 2300.6254 | 2533.9924 | 29093.3497 | $
| Water Cost ($) |  | 29.856 | 101.697 | 96.099 | 102.63 | 64.377 | 56.913 | 86.769 | 291.096 | 88.635 | 88.635 | 23.325 | 11.268 | 1041.3 | $
| Natural Gas ($) |  | 86.43 | 143.35 | 205.45 | 542.45 | 1210.1 | 608.15 | 496.23 | 452.59 | 208.19 | 210.68 | 137.56 | 118.44 | 4419.62 | $
44 | UNCC - Hunt Residence Hall | [17 empty] | UNCC - Hunt Residence Hall
No data
45 | NCSU - Wolf Ridge at Centennial Bldg 6 - Lakeview Hall | [17 empty] | NCSU - Wolf Ridge 6
NCSU - Wolf Ridge Building 6
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 36934.021 | 37820.9839 | 37377.9907 | 34983.0322 | 33385.0098 | 35828.0029 | 33076.9653 | 34573.9746 | 34918.0908 | 30459.9609 | 27027.9541 | 28284.0576 | 404670.0439 | kwh |  | 1379.7274 | MMbtu
| Chilled Water (Dtherms) |  | 444 | 391 | 291 | 226 | 202 | 196 | 196 | 218 | 281 | 291 | 320 | 386 | 3442 | dthrms |  | 3442 | MMbtu
| Steam (1,000 lbs) |  | 108.1001 | 121.6302 | 165.3901 | 222.8598 | 285.8099 | 275.3096 | 266.2003 | 253.69 | 190.5697 | 158.2203 | 130.3501 | 129.51 | 2307.6401 | 1000 lbs |  | 2307.6401 | MMbtu
| Water (CCF) |  | 56 | 97 | 90 | 89 | 59 | 66 | 87 | 79 | 85 | 51 | 20 | 22 | 801 | CCF |  | 599148 | gallons
| Electric Cost ($) |  | 3213.2598 | 3290.4256 | 3251.8852 | 3043.5238 | 2904.4958 | 3117.0363 | 2877.696 | 3007.9358 | 3037.8739 | 2650.0166 | 2351.432 | 2347.5768 | 35093.1576 | $
| Chilled Water Cost ($) |  | 5749.8 | 5063.45 | 3768.45 | 2926.7 | 2615.9 | 2538.2 | 2538.2 | 2823.1 | 3638.95 | 3768.45 | 4144 | 4925.36 | 44500.56 | $
| Steam Cost ($) |  | 1299.3632 | 1461.9951 | 1987.9888 | 2678.7745 | 3435.4352 | 3309.221 | 3199.7278 | 3049.3544 | 2290.6481 | 1901.8079 | 1566.8087 | 1788.5324 | 27969.6572 | $
| Water Cost ($) |  | 522.48 | 905.01 | 839.7 | 830.37 | 550.47 | 615.78 | 811.71 | 737.07 | 793.05 | 475.83 | 186.6 | 206.58 | 7474.65 | $
46 | NCSU - Wolf Ridge at Centennial Bldg 1 - Tower Hall | [17 empty] | NCSU - Wolf Ridge 1
NCSU - Wolf Ridge Building 1
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 142992.9199 | 143932.0068 | 142215.0269 | 134521.1182 | 124160.0342 | 137486.8164 | 128972.0459 | 139423.8892 | 138697.1436 | 131389.1602 | 121522.8271 | 128257.2021 | 1613570.1904 | kwh |  | 5501.4869 | MMbtu
| Chilled Water (Dtherms) |  | 1197.9766 | 958.9805 | 490.6992 | 235.0762 | 134.0469 | 145.0405 | 200.8418 | 227.7051 | 513.4692 | 629.501 | 831.2666 | 1107.5645 | 6672.168 | dthrms |  | 6672.168 | MMbtu
| Steam (1,000 lbs) |  | 162.8252 | 193.5514 | 301.3916 | 462.0068 | 580.332 | 551.7521 | 371.1479 | 423.6618 | 218.5204 | 201.6684 | 175.6435 | 144.4152 | 3786.9164 | 1000 lbs |  | 3786.9164 | MMbtu
| Water (CCF) |  | 250 | 460 | 450 | 455 | 290 | 315 | 480 | 420 | 455 | 235 | 75 | 80 | 3965 | CCF |  | 2965820 | gallons
| Natural Gas (thms) |  | 956 | 1240 | 1441 | 1149 | 1184 | 695 | 1111 | 1251 | 1012 | 1348 | 914 | 761 | 13062 | thms |  | 13062 | thms
| Electric Cost ($) |  | 12440.384 | 12522.0846 | 12372.7073 | 11703.3373 | 10801.923 | 11961.353 | 11220.568 | 12129.8784 | 12066.6515 | 11430.8569 | 10572.486 | 10645.3478 | 139867.5778 | $
| Chilled Water Cost ($) |  | 15513.7965 | 12418.7971 | 6354.5549 | 3044.2364 | 1735.907 | 1878.2748 | 2600.9013 | 2948.7808 | 6649.4266 | 8152.0376 | 10764.9025 | 14132.5224 | 86194.1379 | $
| Steam Cost ($) |  | 1957.1587 | 2326.4877 | 3622.7269 | 5553.3218 | 6975.5908 | 6632.0608 | 4461.198 | 5092.4153 | 2626.6152 | 2424.0538 | 2111.2351 | 1994.3739 | 45777.238 | $
| Water Cost ($) |  | 2332.5 | 4291.8 | 4198.5 | 4245.15 | 2705.7 | 2938.95 | 4478.4 | 3918.6 | 4245.15 | 2192.55 | 699.75 | 751.2 | 36998.25 | $
| Natural Gas ($) |  | 643.12 | 819.01 | 945.49 | 777.17 | 850.43 | 523.06 | 890.23 | 997 | 817.59 | 1093.52 | 756.09 | 637.14 | 9749.85 | $
47 | UNCG - Spartan Village 1 - Lee | [17 empty] | UNCG - Spartan Village 1
Spartan Village # 1
| Lee Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
700 Highland Avenue
| Electricity (kWhs) | 52947 | 62731 | 89755 | 64121 | 61865 | 77423 | 80723 | 67610 | 71297 | 67750 | 54725 | 44235
| Water Usage (gallons) | 12716.884 | 65080.524 | 136145.464 | 207210.404 | 162327.284 | 184768.844 | 69568.836 | 181776.636 | 199729.884 | 185516.896 | 184020.792 | 24685.716
| Natural Gas (Therms) | 143 | 166 | 414 | 481 | 582 | 579 | 385 | 693 | 633 | 698 | 522 | 132
| Electricity Cost ($) | 4985.53 | 5586.64 | 7013.41 | 5456.15 | 5325.55 | 5849.65 | 6323.85 | 5023 | 5420.92 | 4671.94 | 4136.38 | 3357.39
| Water Costs ($) | 871.69 | 1315.23 | 1912.78 | 2510.33 | 2132.93 | 2321.63 | 1352.97 | 2296.47 | 2447.43 | 2327.92 | 2315.34 | 975.57
| Natural Gas Cost ($) | 128.56 | 145.46 | 327.6 | 380.08 | 420.41 | 531.77 | 373.82 | 643.83 | 590.13 | 622.72 | 475.67 | 138.5
48 | UNCG - Spartan Village 3 - Haywood | [17 empty] | UNCG - Spartan Village 3
Spartan Village # 2
| Highland Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
701 Highland Avenue
| Electricity (kWhs) | 78871 | 71264 | 95727 | 68240 | 65326 | 73775 | 78216 | 68943 | 72435 | 70192 | 56867 | 45785
| Water Usage (gallons) | 150358.452 | 119688.32 | 150358.452 | 249849.368 | 167563.648 | 185516.896 | 80041.564 | 173548.064 | 188509.104 | 169807.804 | 169059.752 | 18701.3
| Natural Gas (Therms) | 262 | 176 | 298 | 377 | 482 | 504 | 326 | 617 | 563 | 581 | 418 | 67
| Electricity Cost ($) | 6609.37 | 6148.93 | 7393.57 | 5735.35 | 5622.78 | 6003 | 6301.18 | 5745.8 | 5945.03 | 4837.19 | 4218.07 | 3500.23
| Water Costs ($) | 1992.87 | 1774.4 | 2032.29 | 2868.86 | 2176.96 | 2327.92 | 1441.03 | 2227.28 | 2353.08 | 2195.83 | 2189.54 | 925.25
| Natural Gas Cost ($) | 215.96 | 152.8 | 242.4 | 302.84 | 342.66 | 465.71 | 320.29 | 575.8 | 527.47 | 522.28 | 385.6 | 81.9
49 | UNCG - Spartan Village 4 - Union | [17 empty] | UNCG - Spartan Village 4
Spartan Village # 4
| Union Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
917 Union Street
| Electricity (kWhs) | 43939 | 50401 | 73790 | 53290 | 54502 | 59046 | 62444 | 53789 | 54926 | 54353 | 43429 | 35593
| Water Usage (gallons) | 13464.936 | 8228.572 | 176540.272 | 348592.232 | 290244.176 | 293984.436 | 175792.22 | 235636.38 | 200000 | 223667.548 | 308945.476 | 175044.168
| Natural Gas (Therms) | 127 | 145 | 348 | 421 | 516 | 509 | 358 | 604 | 568 | 609 | 453 | 121
| Electricity Cost ($) | 4017.39 | 4414.69 | 5659.56 | 4412.58 | 4680.93 | 4374.92 | 4645.67 | 3997.57 | 4010.86 | 3744.26 | 3237.39 | 2694.88
| Water Costs ($) | 877.71 | 837.19 | 2252.44 | 3699.14 | 3208.52 | 3239.97 | 2246.15 | 2749.35 | 2340 | 2648.7 | 3365.77 | 2239.86
| Natural Gas Cost ($) | 116.81 | 130.04 | 279.12 | 335.53 | 378.6 | 470.43 | 349 | 564.17 | 531.94 | 546.32 | 415.91 | 128.92
50 | WSSU - Martin-Schexnider Residence Hall | [17 empty] | WSSU - Martin-Schexnider Residence Hall
Winston-Salem State University
Martin-Schexnider Residence Hall
| Utility | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| Electricity (KWH) building meter | 22904 | 37807 | 41696 | 40968 | 38386 | 30267 | 46534 | 29068 | 36510 | 39913 | 23149 | 20963
| Steam from Central Plant (lbs) - natural gas therms | 2251.6474 | 2144.8256 | 2506.0695 | 4199.5044 | 4670.3493 | 5628.5628 | 5292.2305 | 4113.7538 | 4538.1105 | 3464.2323 | 1683.5309 | 2042.0461
| Chilled Water from Central Plant (Dtherms) kwh | 77696.4906 | 85843.262 | 69489.9223 | 39152.1586 | 33287.5261 | 30799.6653 | 37541.5346 | 24974.7244 | 51247.339 | 83468.2499 | 54149.238 | 44808.475
| Natural Gas (Therms) other than from central steam plant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) | 143.48 | 510.775 | 510.78 | 604.97 | 787.16 | 296.82 | 642.41 | 1002.16 | 889.53 | 1178.67 | 633.14 | 246.55
| Electricity Cost ($) building meter x blended rate ($.0712/kwh) | 1629.9366 | 2690.4912 | 2967.2474 | 2915.4401 | 2731.6951 | 2153.9159 | 3311.5381 | 2068.5905 | 2598.1917 | 2840.3623 | 1647.3717 | 1491.8075
| Steam from Central Plant Cost ($) for Natural Gas | 1138.3255 | 1033.54 | 1244.1054 | 2083.0927 | 2141.6032 | 3025.9494 | 3217.7851 | 2294.9972 | 2177.9176 | 1848.3691 | 921.7298 | 1130.5024
| Chilled Water from Central Plant Cost ($) kwh x $.0712/kwh | 5529.1805 | 6108.936 | 4945.1696 | 2786.2179 | 2368.8681 | 2191.8224 | 2671.5997 | 1777.2973 | 3646.9574 | 5939.9211 | 3853.4676 | 3188.7431
| Natural Gas Cost ($) other than from central steam. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Costs ($) | 1045.68 | 2834.525 | 2834.525 | 3516.44 | 4485.03 | 1927.62 | 3704.61 | 5583.83 | 4978.75 | 6469.57 | 3686.03 | 1663.55
51 | Cape Fear Community College - Union Station | [17 empty] | Cape Fear Community College - Union Station
52 | ECU - Smith-Williams Center | [17 empty] | ECU - Smith-Williams Center
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14
| Electricity (KWhs) | 36781 | 38470 | 37733 | 40115 | 34543 | 33747 | 39909 | 39879 | 27881 | 38890 | 35070 | 24385 | 38838
Steam (lbs)
| Chilled Water (Tons) | 22898 | 26921 | 26100 | 20524 | 13417 | 5214 | 5387 | 6074 | 7813 | 6248 | 16100 | 16920 | 14100
Natural Gas (CCF)
Water (CCF)
| Electricity Cost ($) | 3227.5327 | 3375.7425 | 3311.0707 | 3520.0912 | 3031.1482 | 2961.2993 | 3502.0147 | 3499.3822 | 2446.5577 | 3412.5975 | 3077.3925 | 2139.7838 | 3408.0345
Steam Costs ($)
Chilled Water Costs ($)
Natural Gas Costs ($)
53 | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall | [17 empty] | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall
NCSU - Wolf Ridge Building 2
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 44531.9824 | 51126.9531 | 50754.0283 | 45870.9717 | 41633.0566 | 45049.9268 | 40887.085 | 42773.9258 | 46723.999 | 38963.9893 | 33222.0459 | 35352.0508 | 516890.0146 | kwh |  | 1762.3427 | MMbtu
| Chilled Water (Dtherms) |  | 615.8252 | 475.4399 | 325.6602 | 215.3662 | 149.8545 | 149.8066 | 157.9375 | 168.042 | 279.0283 | 296.7139 | 369.2588 | 503.9785 | 3706.9116 | dthrms |  | 3706.9116 | MMbtu
| Steam (1,000 lbs) |  | 75.52 | 74.8204 | 133.7395 | 191.3306 | 259.5297 | 255.5003 | 175.7297 | 187.8799 | 101.5598 | 77.0104 | 60.3602 | 64.4398 | 1657.4203 | 1000 lbs |  | 1657.4203 | MMbtu
| Water (CCF) |  | 95 | 176 | 145 | 147 | 87 | 94 | 122 | 105 | 117 | 65 | 19 | 22 | 1194 | CCF |  | 893112 | gallons
| Electric Cost ($) |  | 3874.2825 | 4448.0449 | 4415.6005 | 3990.7745 | 3622.0759 | 3919.3436 | 3557.1764 | 3721.3315 | 4064.9879 | 3389.8671 | 2890.318 | 2934.2202 | 44828.0231 | $
| Chilled Water Cost ($) |  | 7974.9363 | 6156.9472 | 4217.299 | 2788.9924 | 1940.6157 | 1939.996 | 2045.2906 | 2176.1438 | 3613.4167 | 3842.4446 | 4781.9013 | 6430.7659 | 47908.7496 | $
| Steam Cost ($) |  | 907.7504 | 899.3406 | 1607.549 | 2299.7933 | 3119.5473 | 3071.1135 | 2112.2706 | 2258.3168 | 1220.7489 | 925.6654 | 725.5295 | 889.9137 | 20037.5391 | $
| Water Cost ($) |  | 886.35 | 1642.08 | 1352.85 | 1371.51 | 811.71 | 877.02 | 1138.26 | 979.65 | 1091.61 | 606.45 | 177.27 | 206.58 | 11141.34 | $
54 | UNCG - Spartan Village Building 2 - Highland | [17 empty] | UNCG - Spartan Village Building 2
Spartan Village # 4
| Union Residence Hall | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
917 Union Street
| Electricity (kWhs) | 43939 | 50401 | 73790 | 53290 | 54502 | 59046 | 62444 | 53789 | 54926 | 54353 | 43429 | 35593
| Water Usage (gallons) | 13464.936 | 8228.572 | 176540.272 | 348592.232 | 290244.176 | 293984.436 | 175792.22 | 235636.38 | 200000 | 223667.548 | 308945.476 | 175044.168
| Natural Gas (Therms) | 127 | 145 | 348 | 421 | 516 | 509 | 358 | 604 | 568 | 609 | 453 | 121
| Electricity Cost ($) | 4017.39 | 4414.69 | 5659.56 | 4412.58 | 4680.93 | 4374.92 | 4645.67 | 3997.57 | 4010.86 | 3744.26 | 3237.39 | 2694.88
| Water Costs ($) | 877.71 | 837.19 | 2252.44 | 3699.14 | 3208.52 | 3239.97 | 2246.15 | 2749.35 | 2340 | 2648.7 | 3365.77 | 2239.86
| Natural Gas Cost ($) | 116.81 | 130.04 | 279.12 | 335.53 | 378.6 | 470.43 | 349 | 564.17 | 531.94 | 546.32 | 415.91 | 128.92
55 | UNCC - PORTAL | [17 empty] | UNCC - PORTAL
No data
56 | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall | [17 empty] | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall
NCSU - Wolf Ridge Building 3
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 47737.0605 | 48851.9287 | 48113.0371 | 44437.0117 | 40192.0166 | 44413.9404 | 41614.0137 | 43414.0625 | 45354.0039 | 38745.9717 | 33611.9385 | 35868.042 | 512353.0273 | kwh |  | 1746.8738 | MMbtu
| Chilled Water (Dtherms) |  | 477.0869 | 348.4141 | 160.1011 | 70.7358 | 39.1782 | 53.2642 | 72.9277 | 82.647 | 188.9062 | 212.5229 | 278.1338 | 382.1572 | 2366.0752 | dthrms |  | 2366.0752 | MMbtu
| Steam (1,000 lbs) |  | 37.7999 | 43.7102 | 52.6697 | 135.8205 | 225.0798 | 225.2698 | 146.3698 | 157.9397 | 74.5011 | 52.6597 | 36.8696 | 28.0003 | 1216.6902 | 1000 lbs |  | 1216.6902 | MMbtu
| Water (CCF) |  | 75 | 135 | 127 | 121 | 80 | 81 | 113 | 105 | 117 | 70 | 25 | 28 | 1077 | CCF |  | 805596 | gallons
| Electric Cost ($) |  | 4153.1243 | 4250.1178 | 4185.8342 | 3866.02 | 3496.7054 | 3864.0128 | 3620.4192 | 3777.0234 | 3945.7983 | 3370.8995 | 2924.2386 | 2977.0475 | 44431.2412 | $
| Chilled Water Cost ($) |  | 6178.2755 | 4511.9621 | 2073.3089 | 916.0291 | 507.358 | 689.7709 | 944.4142 | 1070.2783 | 2446.3359 | 2752.1722 | 3601.8326 | 4876.3262 | 30568.0639 | $
| Steam Cost ($) |  | 454.3552 | 525.3967 | 633.0897 | 1632.5629 | 2705.4593 | 2707.7425 | 1759.3649 | 1898.4353 | 895.5035 | 632.9697 | 443.173 | 386.6835 | 14674.7364 | $
| Water Cost ($) |  | 699.75 | 1259.55 | 1184.91 | 1128.93 | 746.4 | 755.73 | 1054.29 | 979.65 | 1091.61 | 653.1 | 233.25 | 262.92 | 10050.09 | $
57 | WSSU - Hill Hall Renovation | [17 empty] | WSSU - Hill Hall Renovation
Winston-Salem State University
Hill Hall Renovation - Student Success Center
| Utility | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| Electricity (KWhs) building meter | 36532 | 44984 | 48514 | 49316 | 43061 | 43530 | 53204 | 34654 | 48669 | 51793 | 17160 | 48868
| Steam from Central Plant (lbs) - natural gas therms | 1534.0477 | 1461.2699 | 1707.3854 | 2861.1228 | 3181.9095 | 3834.7404 | 3605.5972 | 2802.7009 | 3091.8152 | 2360.1819 | 1146.9898 | 1391.2463
| Chilled Water from Central Plant (Dtherms) kwh | 52934.6277 | 58485.0239 | 47343.4918 | 26674.37 | 22678.7952 | 20983.8154 | 25577.0517 | 17015.2825 | 34914.8178 | 56866.9279 | 36891.8819 | 30528.019
| Natural Gas (Therms) other than from central steam plant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) | 10.9 | 24.05 | 24.05 | 25 | 24.5 | 6.3 | 18.8 | 27.6 | 16.9 | 18.5 | 9.8 | 7.2
| Electricity Cost ($) building meter x blended rate ($.0712/kwh) | 2599.7574 | 3201.2341 | 3452.4425 | 3509.5159 | 3064.3861 | 3097.7619 | 3786.2009 | 2466.1117 | 3463.4729 | 3685.7887 | 1221.1715 | 3477.6345
| Steam from Central Plant Cost ($) for Natural Gas | 775.5413 | 704.1509 | 847.6092 | 1419.2113 | 1459.0745 | 2061.5796 | 2192.2773 | 1563.5819 | 1483.8155 | 1259.2941 | 627.9746 | 770.2114
| Chilled Water from Central Plant Cost ($) kwh x $.0712/kwh | 3767.0313 | 4162.0188 | 3369.1446 | 1898.2506 | 1613.9101 | 1493.2889 | 1820.1612 | 1210.8728 | 2484.6725 | 4046.8689 | 2625.3679 | 2172.491
| Natural Gas Cost ($) other than from central steam. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Costs ($) | 95.09 | 178.9 | 178.9 | 187.09 | 190.37 | 67.62 | 145.92 | 208.24 | 133.64 | 143.98 | 94.24 | 71.52
58 | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall | [17 empty] | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall
NCSU - Wolf Ridge Building 5
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 33242.0044 | 37013.0005 | 37297.9736 | 35138.0005 | 31933.0444 | 32115.9668 | 33400.0244 | 34113.9526 | 36401.001 | 32186.0352 | 28921.9971 | 28945.9839 | 400708.9844 | kwh |  | 1366.2221 | MMbtu
| Chilled Water (Dtherms) |  | 312.1362 | 271.3101 | 131.5796 | 62.5332 | 37.3799 | 39.79 | 57.541 | 67.498 | 151.6182 | 177.2759 | 240.0439 | 323.9009 | 1872.6069 | dthrms |  | 1872.6069 | MMbtu
| Steam (1,000 lbs) |  | 45.59 | 52.26 | 79.4701 | 131.4097 | 190.9903 | 160.5796 | 128.2406 | 127.8392 | 70.0408 | 57.2795 | 45.4902 | 42.55 | 1131.74 | 1000 lbs |  | 1131.74 | MMbtu
| Water (CCF) |  | 48 | 94 | 87 | 81 | 53 | 58 | 77 | 74 | 82 | 53 | 28 | 26 | 761 | CCF |  | 569228 | gallons
| Electric Cost ($) |  | 2892.0544 | 3220.131 | 3244.9237 | 3057.006 | 2778.1749 | 2794.0891 | 2905.8021 | 2967.9139 | 3166.8871 | 2800.1851 | 2516.2137 | 2402.5167 | 34745.8977 | $
| Chilled Water Cost ($) |  | 4042.1642 | 3513.4653 | 1703.9557 | 809.805 | 484.0695 | 515.281 | 745.1562 | 874.0997 | 1963.4552 | 2295.7226 | 3108.5691 | 4132.9752 | 24188.7186 | $
| Steam Cost ($) |  | 547.992 | 628.1648 | 955.2304 | 1579.5442 | 2295.7038 | 1930.1666 | 1541.4525 | 1536.6276 | 841.8908 | 688.4994 | 546.7919 | 587.6157 | 13679.6797 | $
| Water Cost ($) |  | 447.84 | 877.02 | 811.71 | 755.73 | 494.49 | 541.14 | 718.41 | 690.42 | 765.06 | 494.49 | 261.24 | 244.14 | 7101.69 | $
59 | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall | [17 empty] | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall
NCSU - Wolf Ridge Building 4
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 35022.995 | 31261.0016 | 31486.9995 | 32717.9871 | 30886.0168 | 31885.9863 | 27928.009 | 33164.0015 | 32671.9971 | 35393.0054 | 32484.9854 | 33314.0259 | 388217.0105 | kwh |  | 1323.6306 | MMbtu
| Chilled Water (Dtherms) |  | 383.1421 | 244.333 | 101.498 | 36.834 | 23.3931 | 25.9316 | 42.4722 | 56.8818 | 118.1631 | 178.1411 | 251.377 | 360.3721 | 1822.5391 | dthrms |  | 1822.5391 | MMbtu
| Steam (1,000 lbs) |  | 36.17 | 37.0602 | 63.3096 | 115.83 | 180.1999 | 141.3499 | 103.3603 | 50.58 | 66.9002 | 59.5697 | 47.9603 | 44.8899 | 947.18 | 1000 lbs |  | 947.18 | MMbtu
| Water (CCF) |  | 33 | 24 | 15 | 12 | 13 | 15 | 12 | 20 | 29 | 35 | 22 | 25 | 255 | CCF |  | 190740 | gallons
| Electric Cost ($) |  | 3047.0006 | 2719.7071 | 2739.369 | 2846.4649 | 2687.0835 | 2774.0808 | 2429.7368 | 2885.2681 | 2842.4637 | 3079.1915 | 2826.1937 | 2765.0641 | 33641.6238 | $
| Chilled Water Cost ($) |  | 4961.6901 | 3164.1125 | 1314.3997 | 477.0001 | 302.9402 | 335.8147 | 550.0146 | 736.6198 | 1530.212 | 2306.9274 | 3255.3315 | 4598.3476 | 23533.4102 | $
| Steam Cost ($) |  | 434.7632 | 445.4639 | 760.981 | 1392.2768 | 2166.0032 | 1699.0257 | 1242.3903 | 607.972 | 804.1407 | 716.0274 | 576.483 | 619.9289 | 11465.4561 | $
| Water Cost ($) |  | 307.89 | 223.92 | 139.95 | 111.96 | 121.29 | 139.95 | 111.96 | 186.6 | 270.57 | 326.55 | 205.26 | 234.75 | 2380.65 | $
60 | Guilford Technical Community College - Aviation Center III Building | [17 empty] | Guilford Technical Community College - Aviation Center III Building
|  |  | Electric | Elec | Nat Gas | Nat Gas | Water | Water
|  |  | KWH | Cost | Therms | Cost | Gallons | Cost
| 2016-07-01 | 2016-08-09: 36789; 2016-09-09: 3332.3; 2016-10-09: 123; 2016-11-09: 113.14; 2016-12-09: 2992; 2017-01-09: 269.16
| 2016-08-01 | 2016-08-09: 48745; 2016-09-09: 4151.88; 2016-10-09: 149; 2016-11-09: 132.24; 2016-12-09: 4488; 2017-01-09: 281.74
| 2016-09-01 | 2016-08-09: 49769; 2016-09-09: 4104.22; 2016-10-09: 209; 2016-11-09: 177.04; 2016-12-09: 3740; 2017-01-09: 275.45
| 2016-10-01 | 2016-08-09: 36478; 2016-09-09: 3048.37; 2016-10-09: 412; 2016-11-09: 244.66; 2016-12-09: 3740; 2017-01-09: 274.45
| 2016-11-01 | 2016-08-09: 27694; 2016-09-09: 2434.91; 2016-10-09: 845; 2016-11-09: 745.97; 2016-12-09: 3740; 2017-01-09: 275.45
| 2016-12-01 | 2016-08-09: 29813; 2016-09-09: 2545.69; 2016-10-09: 941; 2016-11-09: 866.35; 2016-12-09: 1496; 2017-01-09: 256.58
| 2017-01-01 | 2016-08-09: 24353; 2016-09-09: 2091.54; 2016-10-09: 1367; 2016-11-09: 1247.11; 2016-12-09: 5236; 2017-01-09: 288.03
| 2017-02-01 | 2016-08-09: 26324; 2016-09-09: 2248.39; 2016-10-09: 683; 2016-11-09: 635.77; 2016-12-09: 3740; 2017-01-09: 275.45
| 2017-03-01 | 2016-08-09: 25217; 2016-09-09: 2231.02; 2016-10-09: 944; 2016-11-09: 829.16; 2016-12-09: 5236; 2017-01-09: 288.03
| 2017-04-01 | 2016-08-09: 30467; 2016-09-09: 2556.94; 2016-10-09: 482; 2016-11-09: 441.02; 2016-12-09: 2244; 2017-01-09: 262.87
| 2017-05-01 | 2016-08-09: 31050; 2016-09-09: 2678.71; 2016-10-09: 428; 2016-11-09: 395.02; 2016-12-09: 2244; 2017-01-09: 262.87
| 2017-06-01 | 2016-08-09: 34929; 2016-09-09: 2953.76; 2016-10-09: 245; 2016-11-09: 238.18; 2016-12-09: 2992; 2017-01-09: 277.56
|  | Totals | 401628 | 34377.73 | 6828 | 6065.66 | 41888 | 3287.64
61 | UNCC - Martin Residence Hall | [17 empty] | UNCC - Martin Residence Hall
No data
62 | UNCSA - New Library Building | [17 empty] | UNCSA - New Library Building
No data
63 | NCA&T - Student Health Center | [17 empty] | NCA&T - Student Health Center
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14
| Electricity (KWhs) | 29474 | 38354 | 36013 | 30552 | 24645 | 20004 | 19960 | 17068 | 18478 | 19754 | 24347 | 25448 | 28029 | 32856
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) | 764 | 804 | 856 | 477 | 185 | 660 | 1335 | 1278 | 988 | 1307 | 1195 | 1007 | 1043 | 1263
| Water (CCF) | 13 | 11 | 13 | 13 | 15 | 14 | 12 | 11 | 15 | 11 | 14 | 14 | 12
| Electricity Cost ($) | 2012.97 | 2763.55 | 2559.53 | 2113.44 | 1508.53 | 1130.82 | 1165.46 | 996.55 | 1053.79 | 1240.7 | 1412.01 | 1474.84 | 1838.68 | 2319.15
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 545.32 | 573.86 | 609.55 | 349.41 | 148.98 | 520.28 | 1110.19 | 1092.13 | 848.48 | 1115.33 | 980.96 | 857.16 | 871.3 | 1056.09
64 | UNCG - Campus Police Facility | [17 empty] | UNCG - Campus Police Facility
| Campus Police Facility | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
1200 West Gate City Blvd
| Electricity (kWhs) | 51957 | 55238 | 53913 | 37459 | 29984 | 28341 | 33966 | 28457 | 31311 | 37191 | 37503 | 45351
| Water Usage (gallons) | 9724.676 | 9724.676 | 6732.468 | 8976.624 | 5984.416 | 6732.468 | 6732.468 | 7480.52 | 8228.572 | 8228.572 | 6732.468 | 6732.468
| Natural Gas (Therms) | 375 | 298 | 270 | 410 | 736 | 1036 | 1672 | 1057 | 938 | 955 | 563 | 413
| Electricity Cost ($) | 4065.9718 | 4273.7967 | 4045.1559 | 3002.8622 | 2519.4901 | 2026.1696 | 1875.5295 | 1625.9667 | 1821.221 | 2111.0845 | 2162.2793 | 3292.7663
| Water Costs ($) | 315.75 | 368.41 | 304.21 | 323.08 | 297 | 304 | 304.21 | 310.5 | 316.79 | 316.79 | 304.21 | 304.21
| Natural Gas Cost ($) | 298.96 | 242.4 | 221.84 | 326.88 | 479.59 | 930.21 | 1530.93 | 969.63 | 863.13 | 843.33 | 511.18 | 383.24
65 | UNCC - South Village Dining Facility | [17 empty] | UNCC - South Village Dining Facility
No data
66 | UNCG - Moran Commons (Dining Hall Renovation) | [17 empty] | UNCG - Dining Hall Renovation
| Dining Hall/ Moran Common | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
1209 North Drive
| Electricity (kWhs) | 216777 | 319608 | 258955 | 251121 | 280913 | 242911 | 234010 | 224198 | 268037 | 250006 | 231619 | 239556
| Lighting submeter (kWhs) | 16598 | 24158 | 19298 | 20093 | 21248 | 21118 | 20335 | 18934 | 22383 | 19692 | 17875 | 17429
| Mechanical submeter (kWhs) | 47147 | 63550 | 45874 | 47257 | 52908 | 50303 | 37400 | 30787 | 40207 | 33343 | 33981 | 45124
| Chilled water (ton-hrs) | 344459.4698 | 354704.8135 | 276951.1771 | 186594.8427 | 155201.2427 | 103429.1 | 119861.7125 | 134074.7813 | 157555.9917 | 191209.3385 | 182287.6865 | 216474.7177
| Steam Usage (lbs) | 1026165 | 1005300.5 | 1136883.25 | 1189969.25 | 1473502 | 1629467.5 | 1795423 | 1486412.5 | 1819200.75 | 1267029.75 | 853718 | 821074.5
| Water Usage (gallons) | 280238.2 | 425357.68 | 514339.76 | 472870.64 | 504264.2 | 270439.4 | 382564.6 | 439988.56 | 467118.52 | 486080.32 | 247722.64 | 261014.6
| Natural Gas (Therms) | 2029 | 1603 | 4667 | 5030 | 4692 | 3907 | 1124 | 4649 | 3727 | 4693 | 3835 | 1088
| Electricity Cost ($) | 15108.8595 | 21905.7328 | 17231.8162 | 14020.3807 | 15410.5378 | 13868.1452 | 13440.6021 | 12233.2476 | 15416.0789 | 13543.7202 | 12835.3395 | 14844.1466
| Water Costs ($) | 2297.7285 | 3576.8714 | 4325.1298 | 3976.4122 | 4240.4035 | 2274.1495 | 3217.0205 | 3699.9038 | 3928.0421 | 4087.4936 | 2083.1222 | 2194.8955
| Natural Gas Cost ($) | 1513.72 | 1200.84 | 3451.16 | 3752.27 | 3290.46 | 3464.04 | 1065.24 | 4184.75 | 3359.49 | 4053.19 | 3345.24 | 971.5
67 | WSSU - Center for Design Innovation | [17 empty] | WSSU - Center for Design Innovation
Winston-Salem State University
Center for Design Innovation
| Utility | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| Electricity (KWH) building utility meter | 31878 | 35999 | 27423 | 26620 | 32395 | 38651 | 42743 | 32682 | 37539 | 32116 | 31687 | 36849
Steam from Central Plant (lbs) - natural gas therms
Chilled Water from Central Plant (Dtherms) kwh
Natural Gas (Therms) other than from central steam plant
| Emergency Generator #2 Fuel Oil Use (Gallons-Estimated) | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6
| Water (CCF) | 1.8 | 0.4 | 0.4 | 0.85 | 0.85 | 0.6 | 0.69 | 0.8 | 0.61 | 0.66 | 0.74 | 0.63
| Electricity Cost ($) utility building meter invoice | 3962.44 | 3230.87 | 2583.83 | 2531.2 | 2887.65 | 3370.79 | 3563.42 | 2916.97 | 3218.49 | 2881.84 | 2855.21 | 3175.65
Steam from Central Plant Cost ($) for Natural Gas
Chilled Water from Central Plant Cost ($) kwh x $.071/wh
Natural Gas Cost ($) other than from central steam.
| Emergency Generator #2 Fuel Oil Cost (Estimated) | 42.56 | 39.2909 | 49.5345 | 42.5813 | 45.0444 | 43.4883 | 46.4064 | 44.9886 | 46.4197 | 42.8021 | 45.3503 | 45.7573
| Water Costs ($) | 42.04 | 30.97 | 30.97 | 33.62 | 35.78 | 35.05 | 33.91 | 39.9 | 33.5 | 33.75 | 38.51 | 33.6
Building is all electric and at an off-campus location. No central plant is available and no natural gas is delivered to the building or site.
68 | FSU - Jones Student Center - Renovation and Addition | [17 empty] | FSU - Jones Student Center - Renovation and Addition
No Data
69 | UNCSA - Campus Police Facility | [17 empty] | UNCSA - Campus Police Facility
No Data
70 | UNCSA - Central Storage Facility | [17 empty] | UNCSA - Central Storage Facility
No Data
71 | NCSU - Talley Student Center Renovation and Addition | [17 empty] | NCSU - Talley Student Center Renovation and Addition
NCSU - Talley Student Union
| Utility |  | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | Total | Units |  | Total | Units
| Electric (kWh) |  | 404388.9766 | 387783.457 | 399113.5586 | 365638.1406 | 330221.2891 | 364260.6328 | 371929.0781 | 383835.0391 | 391473.2578 | 364464.1953 | 339343.4531 | 347896.3516 | 4450347.4297 | kwh |  | 15173.513 | MMbtu
| Chilled Water (Dtherms) |  | 3131.6562 | 2789.4726 | 1999.893 | 1008.9028 | 107.6955 | 260.2605 | 464.7735 | 463.487 | 1392.5475 | 1310.4055 | 2031.0383 | 2805.0373 | 17765.1696 | dthrms |  | 17765.1696 | MMbtu
| Steam (1,000 lbs) |  | 437.115 | 545.1245 | 805.2051 | 1150.8103 | 1472.5037 | 1587.8059 | 1080.0286 | 1222.5664 | 743.5703 | 526.125 | 423.4609 | 383.2227 | 10377.5384 | 1000 lbs |  | 10377.5384 | MMbtu
| Water (CCF) |  | 564.1713 | 698.6784 | 707.238 | 673.2015 | 412.7895 | 598.3575 | 687.2701 | 634.1773 | 798.9846 | 383.488 | 347.3044 | 414.109 | 6919.7695 | CCF |  | 5175987.5536 | gallons
| Natural Gas (thms) |  | 2029 | 3265 | 4100 | 3589 | 3582 | 2383 | 3400 | 4070 | 3136 | 4310 | 2363 | 1658 | 37885 | thms |  | 37885 | thms
| Electric Cost ($) |  | 35181.841 | 33737.1608 | 34722.8796 | 31810.5182 | 28729.2521 | 31690.6751 | 32357.8298 | 33393.6484 | 34058.1734 | 31708.385 | 29522.8804 | 28875.3972 | 385788.641 | $
| Chilled Water Cost ($) |  | 40554.9484 | 36123.6705 | 25898.6143 | 13065.2906 | 1394.6567 | 3370.3735 | 6018.8168 | 6002.1566 | 18033.4901 | 16969.7512 | 26301.9453 | 35792.2753 | 229525.9896 | $
| Steam Cost ($) |  | 5254.1223 | 6552.3969 | 9678.565 | 13832.74 | 17699.4941 | 19085.4274 | 12981.9437 | 14695.2482 | 8937.7152 | 6324.0225 | 5090.0005 | 5292.3049 | 125423.9806 | $
| Water Cost ($) |  | 5263.7178 | 6518.6691 | 6598.5305 | 6280.9698 | 3851.3261 | 5582.6754 | 6412.2297 | 5916.8744 | 7454.5263 | 3577.9431 | 3240.3501 | 3888.4833 | 64586.2956 | $
| Natural Gas ($) |  | 1307.68 | 2073.19 | 2596.01 | 2309.57 | 2199.77 | 1534.7 | 2370.29 | 2806.77 | 2206.88 | 3001.02 | 1717.94 | 1253.34 | 25377.16 | $
72 | Nash CC - CE and BLET | [17 empty] | Nash CC - CE and BLET
Nash Community College - Continuing Education Building 2016-2017 (July 1, 2016 - June 30, 2017) | bar: 2016-07-09 to 2017-01-09
| Utility | Jun-16 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14
| Electricity (KWhs) |  | 104400 | 125200 | 89040 | 105360 | 65360 | 64880 | 51440 | 57200 | 56800 | 66960 | 66640 | 81440
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) |  | 646 | 641 | 707 | 1114 | 1353 | 1353 | 2762 | 4384 | 3540 | 3232 | 1064 | 769
| Water (CCF) |  | 128 | 121 | 118 | 29 | 29 | 29 | 25 | 9 | 27 | 32 | 25 | 17
| Electricity Cost ($) |  | 10646.43 | 12365.49 | 9174.33 | 10543.77 | 7371.11 | 7162.18 | 6046.74 | 6455.13 | 6427.83 | 7118.7 | 7096.93 | 8103.31
Steam Costs ($)
| Chilled Water Costs ($) |  | 155.16 | 933.58 | 910.96 | 239.9 | 239.9 | 209.74 | 89.1 | 224.82 | 262.52 | 247.44 | 209.74 | 149.42
| Natural Gas Costs ($) |  | 695.37 | 690.25 | 754.74 | 1167.02 | 1422.3 | 1422.39 | 2809.02 | 4404.34 | 3574.15 | 3701.75 | 1318.89 | 1030.93
Note: Electricity Cost Includes Steet Lights for Continuing Education Buildiing | bar: 2016-07-09 to 2016-10-09
Note: Chilled Water Cost Includes Water and Waste Water Expenses | bar: 2016-07-09 to 2016-10-09
73 | UNCSA - Film School Production Design Facility | [17 empty] | UNCSA - Film School Production Design Facility
No data
74 | UNCC - Holshouser Residence Hall Renovation | [17 empty] | UNCC - Holshouser Residence Hall Renovation
No data
75 | UNCC - Laurel Residence Hall | [17 empty] | UNCC - Laurel Residence Hall
No data
76 | ASU - Belk Residence Hall Renovation | [17 empty] | ASU - Belk Residence Hall Renovation
ELECTRICITY
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 124302.36 | 136673.48 | 154241.2 | 154193.12 | 150620.96 | 124908 | 100757.2 | 142079.84 | 126422.8 | 146194.96 | 153701.56 | 92243
| 315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 90183.92 | 75576.56 | 97576.4 | 83684.64 | 70809.12 | 57196 | 34628.4 | 60848.48 | 55911.6 | 67107.12 | 74650.32 | 51248
| 452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 86886.72 | 100976.96 | 121742.4 | 106562.24 | 94529.92 | 77896 | 67854.4 | 83151.68 | 77425.6 | 91417.92 | 88109.12 | 79328
| 239 | Belk Residence Hall Total Electricity Use | 51000 | 52560 | 65280 | 50280 | 38640 | 32280 | 27600 | 34440 | 34080 | 37320 | 36480 | 30480
| 204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 10055.6008 | 11052.1161 | 12467.197 | 12463.3377 | 12175.592 | 10104.3948 | 8159.0232 | 11847.9085 | 10867.3251 | 12560.2146 | 13202.9423 | 7940.8564
| 315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 7278.9497 | 6102.3156 | 7874.4201 | 6755.4264 | 5718.2861 | 4621.7522 | 2803.9183 | 5070.1961 | 4801.7408 | 5760.2983 | 6406.156 | 4402.4387
| 452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 7028.1895 | 8163.1882 | 9835.853 | 8613.0759 | 7643.8719 | 6303.993 | 5495.1385 | 6938.1154 | 6658.6142 | 7856.6571 | 7573.3617 | 6821.5049
| 239 | Belk Residence Hall Total Electricity Cost | 4120.51 | 4246.17 | 5270.77 | 4062.51 | 3124.9 | 2612.6 | 2235.63 | 2870.88 | 2930.37 | 3207.77 | 3135.85 | 2622.13
STEAM
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 292804.2 | 311990.8 | 263607.2 | 227736.5992 | 376224.2 | 459644.2 | 623981.6 | 372887.4 | 511364.6 | 386234.6 | 488007 | 330343.1992
| 315 | Cone Residence Hall Steam Use in Lbs. | 70907 | 87591 | 136808.8 | 139311.4 | 241918 | 150990.2 | 226902.4 | 146819.2 | 222731.4 | 121793.2 | 102606.6 | 73409.6
| 452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 221897.2 | 250260 | 302814.6 | 260270.4 | 444628.6 | 537224.8 | 506359.4 | 471323 | 412929 | 266944 | 260270.4 | 253596.8
| 239 | Belk Residence Hall Steam Use in lbs. | 33368 | 39207.4 | 55057.2 | 47549.4 | 68404.4 | 90927.8 | 95933 | 77580.6 | 94264.6 | 49217.8 | 38373.2 | 39207.4
| 204 & 445 | Plemmons Student Union Total Steam Cost | 6149.52 | 6552.48 | 5536.32 | 4782.96 | 7901.52 | 9653.52 | 13104.96 | 7831.44 | 10739.76 | 8111.76 | 10249.2 | 8589.24
| 315 | Cone Residence Hall Steam Costs | 1489.2 | 1839.6 | 2873.28 | 2925.84 | 5080.8 | 3171.12 | 4765.44 | 3083.52 | 4677.84 | 2557.92 | 2154.96 | 1908.72
| 452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 5426 | 6119.55 | 7404.66 | 6364.33 | 10872.4 | 13136.64 | 12381.89 | 11525.15 | 10097.26 | 6527.52 | 6364.33 | 7278.68
| 239 | Belk Residence Hall Steam Cost | 700.8 | 823.44 | 1156.32 | 998.64 | 1436.64 | 1909.68 | 2014.8 | 1629.36 | 1979.76 | 1033.68 | 805.92 | 1019.43
WATER & SEWER
| Bldg. # | Building Name | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
| 204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 347964.0001 | 386276 | 446391 | 292376 | 228639 | 69000 | 128000 | 213000 | 208295 | 298425.0001 | 287539 | 287916
| 315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 146908 | 171372 | 218777 | 168072 | 159633 | 50000 | 112000 | 174000 | 155865 | 155975 | 94933 | 57452
| 452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 117128 | 239352 | 362832 | 265552 | 246728 | 75000 | 173000 | 270000 | 245840 | 263600 | 157528 | 90632
| 239 | Belk Residence Hall Water Use | 57000 | 113000 | 230000 | 126000 | 97000 | 32000 | 76000 | 108000 | 104000 | 111000 | 54000 | 48000
| 204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 3726.0804 | 2995.2108 | 3627.3685 | 3822.692 | 2974.6506 | 1984.5 | 1298.2 | 2999 | 2198.6915 | 2480.1725 | 4088.5659 | 3343.0792
| 315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 1530.6388 | 1330.0276 | 1725.2195 | 2040.824 | 1912.5182 | 1419 | 1071.8 | 2498 | 1737.7005 | 1614.6075 | 1728.4573 | 867.2024
| 452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 942.9808 | 1122.3616 | 2603.412 | 3106.984 | 2945.3312 | 2156 | 1634.7 | 3864.5 | 2704.608 | 2601.32 | 2849.9768 | 1336.4184
| 239 | Belk Residence Hall Water & Sewer Cost | 347.7 | 372.9 | 805 | 567 | 523.8 | 240 | 486.4 | 1080 | 384.8 | 410.7 | 437.4 | 297.6
77 | UNCW - Osprey Hall Renovation | [17 empty] | UNCW - S & BS Building Renovation
| OSPREY HALL | 2016-07-09 | 2016-08-09 | 2016-09-09 | 2016-10-09 | 2016-11-09 | 2016-12-09 | 2017-01-09 | 2017-02-09 | 2017-03-09 | 2017-04-09 | 2017-05-09 | 2017-06-09 | TOTAL YTD
ELECTRIC
| METER READING | 527142 | 593957 | 674087 | 736026 | 811716 | 867085 | 944618 | 1000157 | 1075816 | 1138712 | 1202175 | 1276714 | -----
| PREVIOUS READING | 472753 | 527142 | 593957 | 674087 | 736026 | 811716 | 867085 | 944618 | 1000157 | 1075816 | 1138712 | 1202175 | -----
| CHANGE | 54389 | 66815 | 80130 | 61939 | 75690 | 55369 | 77533 | 55539 | 75659 | 62896 | 63463 | 74539 | 803961
| COST/KWH | 0.0806 | 0.0811 | 0.0783 | 0.0764 | 0.0731 | 0.0698 | 0.0684 | 0.0676 | 0.0677 | 0.0681 | 0.0709 | 0.0722 | 0.0728
| COST | 4383.75 | 5418.7 | 6274.18 | 4732.14 | 5532.94 | 3864.76 | 5303.26 | 3754.44 | 5122.11 | 4283.22 | 4499.53 | 5381.72 | 58550.75
GAS
| METER READING | 4643 | 4970 | 5375 | 5723 | 6189 | 6549 | 7072 | 7405 | 7904 | 8244 | 8602 | 9010 | -----
| PREVIOUS READING | 4379 | 4643 | 4970 | 5375 | 5723 | 6189 | 6549 | 7072 | 7405 | 7904 | 8244 | 8602 | -----
| MCF CHANGE | 264 | 327 | 405 | 348 | 466 | 360 | 523 | 333 | 499 | 340 | 358 | 408 | 4631
| COST/MCF | 5.13 | 4.89 | 4.89 | 5.01 | 5.05 | 5.79 | 6.46 | 6.02 | 5.17 | 5.5 | 5.52 | 5.71 | 5.45
| COST | 1354.32 | 1599.03 | 1980.45 | 1743.48 | 2353.3 | 2084.4 | 3378.58 | 2004.66 | 2579.83 | 1870 | 1976.16 | 2329.68 | 25253.89
WATER
| METER READING high | 174161 | 184984 | 207294 | 225537 | 247755 | 251254 | 268461 | 284660 | 303494 | 318163 | 324859 | 332651 | -----
| PREVIOUS READING | 170923 | 174161 | 184984 | 207294 | 225537 | 247755 | 251254 | 268461 | 284660 | 303494 | 318163 | 324859 | -----
| CHANGE - GAL | 3238 | 10823 | 22310 | 18243 | 22218 | 3499 | 17207 | 16199 | 18834 | 14669 | 6696 | 7792
| METER READING low | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | -----
| PREVIOUS READING | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | 58429 | -----
| CHANGE - GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL GALLONS | 3238 | 10823 | 22310 | 18243 | 22218 | 3499 | 17207 | 16199 | 18834 | 14669 | 6696 | 7792 | 161728
| COST/GAL | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0041 | 0.0041 | 0.004 | 0.0041
| COST | 12.95 | 43.29 | 89.24 | 72.97 | 88.87 | 14.7 | 72.27 | 68.04 | 79.1 | 60.14 | 27.45 | 31.17 | 660.19
SEWAGE
| COST/GAL | 0.0056 | 0.0047 | 0.0047 | 0.0041 | 0.0041 | 0.0044 | 0.0044 | 0.004 | 0.004 | 0.0039 | 0.0039 | 0.0031 | 0.0042
| COST | 18.13 | 50.87 | 104.86 | 74.8 | 91.09 | 15.4 | 75.71 | 64.8 | 75.34 | 57.21 | 26.11 | 24.16 | 678.48
FUEL OIL
| GALLONS | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95
| COST | 0 | 165.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.23
- | bar: 2016-07-09 to 2017-06-09
| TOTAL UTILITIES | 5769.15 | 7111.89 | 8448.73 | 6623.39 | 8066.2 | 5979.26 | 8829.82 | 5891.94 | 7856.38 | 6270.57 | 6529.25 | 7766.73 | 85143.31
= | bar: 2016-07-09 to 2017-06-09
| TRASH | 66.52 | 83.15 | 66.52 | 83.15 | 83.15 | 66.52 | 83.15 | 66.52 | 66.52 | 66.52 | 83.15 | 66.52 | 881.39
Gross Sqft: 46714
Net Sqft: 41759
Jul-Jun electric on line reading moved forward and backward. One digit less than meter in the field. Because rolled over now two digits less than meter in the field.
Jul-Jun low flow water reading not changing.
Oct - additional dump in preparation for Hurricane Matthew.
| Jul usage 7/6/16-8/1/16 | 2016-07-09: Sep usage 8/31/16-10/3/16; 2016-10-09: Nov usage 11/1/16-12/5/16; 2017-01-09: Jan usage 1/3/17-2/6/17; 2017-03-09: Mar usage 3/1/17-4/4/17; 2017-05-09: May usage 5/1/17-5/31/17
| Aug usage 8/1/16-8/31/16 | 2016-07-09: Oct usage 10/3/16-11/1/16; 2016-10-09: Dec usage 12/5/16-1/3/17; 2017-01-09: Feb usage 2/6/17-3/1/17; 2017-03-09: Apr usage 4/4/17-5/1/17; 2017-05-09: Jun usage 5/31/17-7/6/17
78 | ECU - Gateway Residence Hall (Belk Replacement) | [17 empty] | ECU - Gateway Residence Hall (Belk Replacement)
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14
| Electricity (KWhs) | 197344.59 | 271022.3 | 316583.31 | 305804.5 | 246148.93 | 187779.87 | 163839.26 | 184453.15 | 178029.61 | 187617.06 | 231861.02 | 201667.75 | 235149.06
| Steam Condensate (gal) | 2016-08-09: 166; 2017-06-09: 1251410 | 216350
Chilled Water (Tons)
Natural Gas (CCF)
| Water (kGal) | 82.28 | 314.91 | 374.75 | 1046.45 | 766.7 | 702.37 | 475.73 | 320.14 | 736.78 | 535.57 | 1469 | 561 | 638.6
| Electricity Cost ($) | 17316.9878 | 23782.2068 | 27780.1855 | 26834.3449 | 21599.5686 | 16477.6836 | 14376.8951 | 16185.7639 | 15622.0983 | 16463.397 | 20345.8045 | 17696.3451 | 20634.33
Steam Costs ($)
Chilled Water Costs ($)
Natural Gas Costs ($)
79 | UNCC - Oak Residence Hall Renovation | [17 empty] | UNCC - Oak Residence Hall Renovation
No data
80 | WTCC - Holding Hall Renovation | [17 empty] | WTCC - Holding Hall Renovation
| Utility | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-14
| Electricity (KWhs) | 53200 | 57000 | 62500 | 63700 | 49900 | 39700 | 36500 | 36100 | 38300 | 41900 | 46500 | 45200 | 59000 | 61800 | NA | NA
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) |  |  |  |  | 0 | 1231 | 2199 | 2302 | 1665 | 1932 | 1240 | 1224 | 712 | 422 | NA | NA
| Water (CCF) | 25.178 | 25.1625 | 56.1799 | 54.0114 | 40.1637 | 38.7525 | 32.2566 | 53.2577 | 48.3938 | 43.8185 | 34.37 | 29.2012 | 23.4864 | 28.1904 | NA | NA
| Fuel Oil (gallons) | 77.9 | NA | NA | 706.9 | 667.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| Electricity Cost ($) | 4442.5 | 4965.2 | 5394.84 | 5494.94 | 4229.05 | 3420.85 | 3064.7 | 2725.59 | 2857.64 | 3201.74 | 3457.29 | 3566.12 | 4277.33 | 4636.35 | NA | NA
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) |  |  |  |  | 18.73 | 877.19 | 1540.48 | 1784.24 | 1311.47 | 1519.33 | 1008.31 | 997.11 | 599.04 | 369.4 | NA | NA
| Fuel Oil Costs ($) | 353.29 | NA | NA | 1322.26 | 1357.56 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
GENERAL NOTES:
= "Dual fuel" boilers were configured for Fuel Oil at time of project completion; "duel fuel" boilers were converted to Natural Gas in the fall of 2016.
= BAS water submeter data was not totalizing water consumption properly, water use estimated as a percentage of entire campus water usage. Problem has been corrected for future reporting.
81 | UNC-CH - Rizzo Conference Center Phase III | [17 empty] | UNC-CH - Rizzo Conference Center Phase III
Energy and Water Usage (Acct. #01003891)
Annual Summary of Performance
| id | Period | name | total btu | Electric (Btu) | ng (Btu) | steam (Btu) | chw (Btu) | mgal water | gsf | mgal non-potable water | Site EUI
| Actual Performance | Aug 16 - Jul 17 | UNC Chapel Hill | 8920481304 | 4176431304 | 4744050000 | 0 | 0 | 1248 | 93576 | NA | 95328.7307
| Modeled Performance | NA | UNC Chapel Hill | 1176400000 | 1154200000 | 22200000 | 0 | 0 | 100.8 | 93576 | NA | 12571.5996
Monthly Detail of Performance
| UTILITY | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01
Consumption:
| ELECTRIC (kWhs) | 93200 | 136470 | 96678 | 96014 | 83407 | 112233 | 102692 | 89845 | 101172 | 84080 | 117029 | 111222
| STEAM (MLBS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHILLED WATER (Ton-Hrs.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NATURAL GAS (Therms) | 2429 | 2515 | 2700 | 3660.5 | 4521 | 5598.5 | 5927 | 4813 | 5189 | 3761 | 3507 | 2819.5
| WATER (kGal) | 77 | 60 | 110 | 148 | 86 | 98 | 99 | 105 | 98 | 126 | 113 | 128
| SEWER (kGal) | 77 | 60 | 110 | 148 | 86 | 98 | 99 | 105 | 98 | 126 | 113 | 128
Costs:
| ELECTRIC ($) | 6682.44 | 7478.56 | 6409.75 | 4551.06 | 4812.58 | 5634.1 | 5524.83 | 4842.65 | 5837.62 | 4658.03 | 5570.58 | 7926.16
| STEAM ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHILLED WATER ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NATURAL GAS ($) | 1018.19 | 1054.28 | 1131.72 | 1534.32 | 1925.16 | 2362.79 | 2943.99 | 2407.27 | 2591.985 | 1899.125 | 1770.715 | 1423.645
| WATER ($) | 639.87 | 498.6 | 734.75 | 646.76 | 375.82 | 428.26 | 432.63 | 458.85 | 428.26 | 742.78 | 939.03 | 1063.68
| SEWER ($) | 523.6 | 408 | 748 | 1006.4 | 584.8 | 666.4 | 673.2 | 714 | 666.4 | 856.8 | 768.4 | 870.4
82 | UNC-C - Belk Gymnasium Renovation | [17 empty] | UNC-C - Belk Gymnasium Renovation
No data
83 | UNCG - Leonard J. Kaplan Center for Wellness | [17 empty] | UNCG - Leonard J. Kaplan Center for Wellness
| Kaplan Center for Wellness | July-16 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01
1301 West Gate City Blvd
| Electricity (kWhs) | 472979 | 545332 | 503876 | 342687 | 323860 | 292633 | 295932 | 275150 | 333061 | 341723 | 370179 | 463630
| Water Usage (gallons) | Note 2 | 136136 | 846736 | 731544 | 425612 | 348568 | 232628 | 184756 | 267784 | 228140 | 303688 | 365772
| Natural Gas (Therms) | 8075 | 7697 | 9092 | 9912 | 14428 | 22001 | 24984 | 17582 | 16177 | 17143 | 11528 | 9437
| Electricity Cost ($) | 35972.84 | 41213.34 | 35924 | 25630.78 | 23219.21 | 19651.36 | 16405.96 | 16179.25 | 19083.31 | 20252.48 | 21826.62 | 34676.43
| Water Costs ($) | Note 2 | 1912.78 | 8671.28 | 6919.62 | 4347.01 | 3715.34 | 2740.39 | 2337.83 | 3036.02 | 2702.65 | 3321.74 | 3860.01
| Natural Gas Cost ($) | 5954.12 | 5676.5 | 6701.05 | 7370.3 | 10877.12 | 19284.79 | 22601.42 | 15760.77 | 14503.19 | 14739.4 | 10008.57 | 7528.26
Note 2: Missing Data
84 | NCSU - Reynolds Coliseum Renovation | [17 empty] | NCSU - Reynolds Coliseum Renovation
Reynolds Coliseum
| Utility |  |  | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | Total | Units |  | Total | Units
| Electric (kWh) |  |  | 120312.9883 | 156106.0181 | 150607.9712 | 145809.021 | 144721.9849 | 138762.0239 | 143576.0498 | 148554.9316 | 150557.9834 | 152450.0732 | 169554.9316 | 171994.0186 | 1793007.9956 | kwh |  | 6113.2823 | MMbtu
| Chilled Water (Dtherms) |  |  | 1185.791 | 675.2422 | 265.5713 | 182.5391 | 195.418 | 210.9014 | 225.2129 | 575.5078 | 768.9307 | 828.7598 | 1027.79 | 979.4297 | 7121.0938 | dthrms |  | 7121.0938 | MMbtu
| Steam (1,000 lbs) |  |  | 421.7251 | 564.1295 | 527.9221 | 550.0643 | 550.3773 | 235.4723 | 277.6578 | 147.1246 | 161.3724 | 45.3614 | 43.8373 | 77.8789 | 3602.9231 | 1000 lbs |  | 3602.9231 | MMbtu
| Water (CCF) |  |  | 402.2595 | 382.5549 | 379.7209 | 123.2271 | 100.1672 | 104.7524 | 140.98 | 94.0847 | 123.5613 | 38.5269 | 117.412 | 111.891 | 2119.1379 | CCF |  | 1585115.1853 | gallons
| Electric Cost ($) |  |  | 10467.23 | 13581.2236 | 13102.8935 | 12685.3848 | 12590.8127 | 12072.2961 | 12491.1163 | 12924.2791 | 13098.5446 | 13263.1564 | 14751.2791 | 14275.5035 | 155303.7195 | $
| Chilled Water Cost ($) |  |  | 15355.9937 | 8744.3863 | 3439.1482 | 2363.8809 | 2530.6627 | 2731.1727 | 2916.5069 | 7452.8262 | 9957.6521 | 10732.439 | 13309.881 | 12497.5228 | 92032.0724 | $
| Steam Cost ($) |  |  | 5069.1362 | 6780.8371 | 6345.6237 | 6611.7734 | 6615.535 | 2830.3773 | 3337.4465 | 1768.4381 | 1939.696 | 545.2439 | 526.9241 | 1075.5077 | 43446.5389 | $
| Water Cost ($) |  |  | 3753.0811 | 3569.2374 | 3542.7958 | 1149.7093 | 934.5597 | 977.3402 | 1315.3432 | 877.8101 | 1152.8274 | 359.4556 | 1095.4542 | 1050.6565 | 19778.2705 | $
Note on D218: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on G218: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on H218: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on I218: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on J218: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on K218: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on G235: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on H235: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on I235: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on J235: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on K235: Nihal Ali Al Raees: Off reading/ having the average of 3 similar buildings for the same month
Note on O672: Thagard, Leonard: manual input. Formula would not copy.
Note on C715: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on D715: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on E715: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on F715: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on G715: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on M715: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on N715: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on C720: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on D720: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on E720: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on F720: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on G720: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on M720: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on N720: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on G722: Summer boiler turned off week of 12/12/16.
Note on L722: summer boiler turned on
Note on D723: August and September billing came as one. Split costs and usage evenly.
Note on E723: August and September billing came as one. Split costs and usage evenly.
Note on F723: high usage from water running straight through walk-in cooler
Note on J827: running toilets
Note on D832: August and September billing came as one. Split costs and usage evenly.
Note on E832: August and September billing came as one. Split costs and usage evenly.
Note on D925: August and September billing came as one. Split costs and usage evenly.
Note on E925: August and September billing came as one. Split costs and usage evenly.
Note on F1028: faulty water meter
Note on G1028: faulty water meter
Note on D1034: August and September billing came as one. Split costs and usage evenly.
Note on E1034: August and September billing came as one. Split costs and usage evenly.

## 2016 Summary
|  | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [13 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [16 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [10 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [12 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project
2016-10-01 |  | PACKAGE DATA (Pages 1 - 6) | [12 empty] | 2016-10-01 | ANNUAL ENERGY USAGE (x1,000,000 BTU/YEAR) (Pages 7 -12) | [15 empty] | 2016-10-01 | ANNUAL ENERGY USAGE ($/YEAR) (pages 13-18) | [9 empty] | 2016-10-01 | ANNUAL INDOOR WATER USAGE (GALLONS/YEAR) (Pages 19 - 24) | [11 empty] | 2016-10-01 | Construction and Design Costs and Fees (Pages 25 - 30)
Project | LEED | Agency or Institution | County | Energy Contact | SCO ID# | Energy Model Report Date | Energy Model Report Phase | Construction Contract Award Date | Actual or Projected Acceptance Date | Principal Occupancy / Category / Use(s) | Number of Beds | Size (GSF from building code summary) | GSF/Bed | Floors (from building code summary) | Project | ASHRAE Standard | Climate Zone (3, 4 or 5) | Baseline | Site EUI Baseline (kBtu/Sq Ft/yr) | Proposed | Site EUI Proposed (kBtu/Sq Ft/yr) | Proposed improvement in energy efficiency | Proposed Energy Savings | Date of Meter Data | Metered Energy Usage | Site EUI Metered (kBtu/Sq Ft/yr) | ASHRAE 100 Bldg Type No. | ASHRAE 100 25th(kBtu/Sq Ft/yr) | Metered improvement in energy efficiency | Meets SB 668 (from unclean data) | Metered Energy Savings (from unclean data) | Project | Baseline | Baseline ($/Yr/Sq Ft) | Proposed | Proposed ($/Yr/Sq Ft) | Proposed % improvement in energy cost | Proposed Savings in Energy Cost | Metered | Metered ($/Yr/Sq Ft) | Metered % improvement in energy cost | Metered Savings in Energy Cost | Project | Baseline (Gallons/Year) | Baseline (Gal/Res/Yr) | WUI Baseline (Gal/Sq Ft/Yr) | Proposed (Gallons/Year) | Proposed (Gal/Res/Yr) | WUI Proposed (Gal/Sq Ft/Yr) | Proposed % improvement in water usage | Proposed Savings (Gallons/Year) | Metered (Gallons/Year) | Metered (Gal/Res/Yr) | WUI Metered (Gal/Sq Ft/Yr) | Metered improvement in water usage | Project | Cost Estimate or Original Amount Construction Contract | Construction Cost/SF | Designer's Baseline (non-SB668) Estimate | Original Total Design Fee (without amendments) | Additional Design Fees (LEED or SB 668 - included in OTDF) | Advance Planning Contract Item G | Commissioning Fee | Simple Payback in Years (Net Savings Required /HB 628) | Modeler | ASHRAE Standard
Cone Residence Hall Renovation | Gold | ASU | Watauga | Jerry Marshall | 08-07272-01A | 2009-01-20 | CD | 2009-09-14 | 2010-06-23 | Residence Hall | 278 | 58803 | 211.5216 | 8 | Cone Residence Hall Renovation | 90.1-2004 | 5 | 3467 | 58.9596 | 1993 | 33.8928 | 42.52% | 1474 | 2016-08-12 | 4786.0519 | 81.3913 | Dorm | 78 | -38.05% |  | -1319.0519 | Cone Residence Hall Renovation | 81830 | 1.3916 | 43969 | 0.74773 | 46.27% | 37861 | 112433.7297 | 1.912 | -37.4% | -30603.7297 | Cone Residence Hall Renovation | 2000376 | 7195.5971 | 34.0183 | 1397116 | 5025.5971 | 23.7593 | 30.16% | 603260 | 1709231 | 6148.3129 | 29.0671 | 14.55% | Cone Residence Hall Renovation | 7585100 | 128.9917 | 5965486 | 883660 | 0 |  | 62500 | 44.4287 | SKA | 90.1-2004
Prospector Hall Renovation Phase II | None | UNCC | Mecklenburg | Tony Schallert | 06-07223-01A | 2013-03-15 | LEED submit. | 2010-08-12 | 2011-05-30 | Food Service/Dining | NA | 22705 |  | 2 | Prospector Hall Renovation Phase II | 90.1-2004 | 3 | 2082 | 91.6979 | 1477 | 65.0518 | 29.06% | 605 | 2016-08-05 | 10571.8262 | 246.6825 | Fast food | 277 | -407.8% |  | -8489.8262 | Prospector Hall Renovation Phase II | 30538 | 1.345 | 21943 | 0.96644 | 28.15% | 8595 | 102256.9158 | 4.5037 | -234.9% | -71718.9158 | Prospector Hall Renovation Phase II | 48654 | NA | 2.1429 | 27934 | NA | 1.2303 | 42.59% | 20720 | 969063.92 | NA | 42.6806 | -1892% | Prospector Hall Renovation Phase II | 4029200 | 177.4587 | 3944812 | 295500 | 0 |  | 65100 | 17.3924 | M&C | 90.1-2004
Miltimore Residence Hall | Silver | UNCC | Mecklenburg | Tony Schallert | 05-06656-01A | 2009-06-10 | CD | 2009-07-22 | 2011-07-19 | Residence Hall | 431 | 173086 | 401.5916 | 5 | Miltimore Residence Hall | 90.1-2004 | 3 | 38283 | 221.1791 | 32882 | 189.9749 | 14.11% | 5401 | 2016-08-05 | 11395.7172 | 65.8385 | Dorm | 47 | 70.23% | ü | 26887.2828 | Miltimore Residence Hall | 478677 | 2.7655 | 411144 | 2.3754 | 14.11% | 67533 | 143088.6338 | 0.82669 | 70.11% | 335588.3662 | Miltimore Residence Hall | 6961135 | 16151.1253 | 40.2178 | 5188175 | 12037.529 | 29.9746 | 25.47% | 1772960 | 4889384.28 | 11344.2791 | 28.2483 | 29.76% | Miltimore Residence Hall | 32995620 | 190.6314 | 33000165 | 2747550 | 58700 |  | 177000 | 3.4228 | CN | 90.1-2004
Nursing Building | Silver | NCCU | Durham | Ondin Mihalcescu <o.mihalcescu@nccu.edu> | 07-07203-02A | 2009-12-22 | CD | 2010-01-25 | 2011-08-05 | Offices/Classrooms | NA | 69610 |  | 5 | Nursing Building | 90.1-2004 | 4 | 6048.6 | 86.8927 | 2596.2 | 37.2964 | 57.08% | 3452.4 | 2016-08-16 | 5209.1229 | 74.833 | Col/Univ | 72 | 13.88% |  | 839.4771 | Nursing Building | 148249 | 2.1297 | 61035 | 0.87681 | 58.83% | 87214 | 80478.11 | 1.1561 | 45.71% | 67770.89 | Nursing Building | 871150 | NA | 12.5147 | 601563 | NA | 8.6419 | 30.95% | 269587 | 1561671 | NA | 22.4346 | -79.27% | Nursing Building | 16198787 | 232.7078 | 16003466 | 1795875 | 82875 | 16175 | 265694 | 6.4217 | RMF | 90.1-2004
Chidley North Residence Hall | Gold | NCCU | Durham | Ondin Mihalcescu <o.mihalcescu@nccu.edu> | 05-07248-02A | 2012-03-23 | LEED submit. | 2009-08-03 | 2011-08-10 | Residence Hall | 528 | 133570 | 252.9735 | 4 | Chidley North Residence Hall | 90.1-2004 | 4 | 16482 | 123.396 | 10635 | 79.6212 | 35.48% | 5847 | 2016-08-16 | 2908.5997 | 21.7758 | Dorm | 58 | 82.35% |  | 13573.4003 | Chidley North Residence Hall | 292778 | 2.1919 | 198708 | 1.4877 | 32.13% | 94070 | 52638.59 | 0.39409 | 82.02% | 240139.41 | Chidley North Residence Hall | 6283057 | 11899.7292 | 47.0394 | 4373148 | 8282.4773 | 32.7405 | 30.4% | 1909909 | 1351127.36 | 2558.9533 | 10.1155 | 78.5% | Chidley North Residence Hall | 23276802 | 174.2667 | 21956196 | 2186050 | 173500 |  | 104934 | 16.9984 | SWA | 90.1-2004
The Loudermilk Center for Excellence | None | UNC-CH | Orange |  | 09-07851-01A | 2010-05-17 | CD | No Contract (Found. Proj) | 2011-08-18 | Offices/Locker rooms/Club | NA | 170189 |  | 6 | The Loudermilk Center for Excellence | 90.1-2004 | 4 | 10672 | 62.7068 | 7143 | 41.971 | 33.07% | 3529 | 2016-07-28 | 25526.7716 | 149.9907 | Col/Univ | 72 | -139.2% |  | -14854.7716 | The Loudermilk Center for Excellence | 116674 | 0.68556 | 78320 | 0.46019 | 32.87% | 38354 | 271145.11 | 1.5932 | -132.4% | -154471.11 | The Loudermilk Center for Excellence | 1518337 | NA | 8.9215 | 991995 | NA | 5.8288 | 34.67% | 526342 | 2683000 | NA | 15.7648 | -76.71% | The Loudermilk Center for Excellence | (Foundation Project) |  |  | (Foundation Project) |  | (Foundation Project) | (Foundation Project) |  | MSWG | 90.1-2004
Davis Event Center | In Progress | DoAG&CS | Buncombe | Debbie Robertson <debbie.robertson@ncagr.gov> | 08-07347-02A | 2010-05-06 | CD | 2010-10-26 | 2011-08-19 | Assembly | NA | 67904 |  | 1 | Davis Arena Add & Renov | 90.1-2004 | 4 | 2961 | 43.6057 | 1736 | 25.5655 | 41.37% | 1225 | 2016-08-23 | 3119.0466 | 45.9332 | Other Assembly | 31 | -5.338% |  | -158.0466 | Davis Arena Add & Renov | 72840 | 1.0727 | 42637 | 0.6279 | 41.46% | 30203 | 61509.57 | 0.90583 | 15.56% | 11330.43 | Davis Arena Add & Renov | 109500 | NA | 1.6126 | 87313 | NA | 1.2858 | 20.26% | 22187 |  |  |  |  | Davis Arena Add & Renov | 5507600 | 81.1086 | 5351000 | 484000 | 15000 |  | 43640 | 7.1264 |  | 90.1-2004
Student Health Center Add and Renovation | Gold | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 07-07345-02A | 2010-03-12 | CD | 2010-06-10 | 2011-09-12 | Offices/Clinics | NA | 24663 |  | 2 | Student Health Center Addition and Renovation | 90.1-2004 | 4 | 2746 | 111.3409 | 1547 | 62.7255 | 43.66% | 1199 | 2016-09-01 | 10036.0973 | 151.7677 | Clinic | 48 | -265.5% |  | -7290.0973 | Student Health Center Addition and Renovation | 69316 | 2.8105 | 38688 | 1.5687 | 44.19% | 30628 | 163637.7724 | 2.4746 | -136.1% | -94321.7724 | Student Health Center Addition and Renovation | 320198 | NA | 12.9829 | 230958 | NA | 9.3646 | 27.87% | 89240 | 427997.122 | NA | 17.3538 | -33.67% | Student Health Center Addition and Renovation | 6017900 | 244.0052 | 5778782 | 634045 | 65575 |  | 106438 | 13.4234 | RMF | 90.1-2004
Gilchrist Education and Psychology Complex | In Progress | ECSU | Pasquotank | Elizabeth Linney | 07-07081-02A | 2010-01-11 | CD | 2010-01-05 | 2012-02-01 | Office/Classroom | NA | 48112 |  | 3 | Gilchrist Education and Psychology Complex | 90.1-2004 | 3 | 3078 | 63.9757 | 1625 | 33.7754 | 47.21% | 1453 | 2016-09-22 | 2531.4084 | 75 | Col/Univ | 62 | 17.76% |  | 546.5916 | Gilchrist Education and Psychology Complex | 64655 | 1.3438 | 34128 | 0.70934 | 47.22% | 30527 | 76605.5 | 1.5922 | -18.48% | -11950.5 | Gilchrist Education and Psychology Complex | 1506938 | NA | 31.3215 | 1056525 | NA | 21.9597 | 29.89% | 450413 | No data |  |  |  | Gilchrist Education and Psychology Complex | 14394127 | 299.1796 | 13822099 | 1654600 | 35000 |  | 57000 | 21.7522 | AEI | 90.1-2004
EPIC | None | UNCC | Mecklenburg | Tony Schallert | 07-07078-02A | 2009-08-21 | CD | 2009-09-30 | 2012-04-12 | Offices/Labs/Classrooms | NA | 200164 |  | 4 | EPIC | 90.1-2004 | 3 | 30494.5 | 152.3476 | 18910.6 | 94.4755 | 37.99% | 11583.9 | 2016-08-05 | 42659.0535 | 213.1205 | Lab | 175 | -39.89% |  | -12164.5535 | EPIC | 284103 | 1.4194 | 165774 | 0.82819 | 41.65% | 118329 | 433639.9848 | 2.1664 | -52.63% | -149536.9848 | EPIC | 3172838 | NA | 15.8512 | 1985718 | NA | 9.9205 | 37.42% | 1187120 | 873972.924 | NA | 4.3663 | 72.45% | EPIC | 61500000 | 307.2481 | 51725930 | 5792635 | 221084 |  | 404815 | 87.8903 | M&L | 90.1-2004
SENC Ag Center | None | DoAG&CS | Robeson | Debbie Robertson <debbie.robertson@ncagr.gov> | 08-07348-02A | 2010-06-28 | DD | 2011-03-22 | 2012-04-12 | Equine & Livestock | NA | 55605 |  | 1 | SENC Ag Center | 90.1-2004 | 3 | 1743 | 31.3461 | 749 | 13.47 | 57.03% | 994 | 2016-08-23 | 2717.4964 | 48.8714 | Other Assembly | 28 | -55.91% |  | -974.4964 | SENC Ag Center | 42886 | 0.77126 | 28420 | 0.51111 | 33.73% | 14466 | 79111.91 | 1.4227 | -84.47% | -36225.91 | SENC Ag Center | 243256 | NA | 4.3747 | 171756 | NA | 3.0889 | 29.39% | 71500 |  |  |  |  | SENC Ag Center | 4072395 | 73.2379 | 3919435 | 363080 | 0 |  | 11870 | 11.3943 |  | 90.1-2004
NC Veterans Home - Black Mountain | None | NCDVA | Buncombe | diane.norris@doa.nc.gov | 06-06924-05A | 2009-12-22 | CD | 2010-05-24 | 2012-05-31 | Nursing Home /Assisted Living | 100 | 108770 |  | 1 | NC Veterans Home - Black Mountain | 90.1-2004 | 4 | 8495 | 78.1006 | 5163 | 47.4671 | 39.22% | 3332 | 2016-08-05 | 9408.4325 | 86.4984 | Nursing home | 91 | -10.75% |  | -913.4325 | NC Veterans Home - Black Mountain | 213106 | 1.9592 | 120807 | 1.1107 | 43.31% | 92299 | 174267.39 | 1.6022 | 18.23% | 38838.61 | NC Veterans Home - Black Mountain | 4378540 | 43785.4 | 40.255 | 3400982 | 34009.82 | 31.2676 | 22.33% | 977558 | 4190296 | 41902.96 | 38.5244 | 4.299% | NC Veterans Home - Black Mountain | 16135100 | 148.3415 | 15834228 | 1250000 | 0 |  | 96941 | 4.31 | MCBH | 90.1-2004
Russell Classroom Building | None | Pitt CC | Pitt | Don Heisey 'dheisey@email.pittcc.edu' | 08-07329-02A | 2010-04-12 | CD | 2010-12-06 | 2012-06-27 | Office/Classroom | NA | 50434 |  | 2 | Russell Classroom Building | 90.1-2004 | 3 | 3018 | 59.8406 | 1900 | 37.673 | 37.04% | 1118 | No data |  |  | Col/Univ | 62 |  |  |  | Russell Classroom Building | 91928 | 1.8227 | 56777 | 1.1258 | 38.24% | 35151 |  |  |  |  | Russell Classroom Building | 1217970 | NA | 24.1498 | 954495 | NA | 18.9256 | 21.63% | 263475 |  |  |  |  | Russell Classroom Building | 7393799 | 146.6035 | 7243287 | 943138 | 52150 |  | 42310 | 6.9691 | PDC | 90.1-2004
Bailey Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Bailey Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2016-08-30 | 2815.7656 | 91.6143 | Dorm | 58 | 30.58% | ü | 1240.2344 | Bailey Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 18623.7605 | 0.60595 | 68.76% | 40984.2395 | Bailey Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 912700 | 10612.7907 | 29.6958 | -178.4% | Bailey Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Coit Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Coit Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2016-08-30 | 3346.8665 | 108.8943 | Dorm | 58 | 17.48% | ü | 709.1335 | Coit Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 14952.1914 | 0.48649 | 74.92% | 44655.8086 | Coit Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 656500 | 7633.7209 | 21.36 | -100.2% | Coit Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Cotten Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Cotten Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2016-08-30 | 3213.3002 | 104.5486 | Dorm | 58 | 20.78% | ü | 842.6998 | Cotten Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 20169.0662 | 0.65622 | 66.16% | 39438.9338 | Cotten Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 978800 | 11381.3953 | 31.8464 | -198.5% | Cotten Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Gray Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Gray Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2016-08-30 | 3015.5114 | 98.1133 | Dorm | 58 | 25.65% | ü | 1040.4886 | Gray Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 19062.8062 | 0.62023 | 68.02% | 40545.1938 | Gray Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 756300 | 8794.186 | 24.6071 | -130.7% | Gray Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Hinshaw Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Hinshaw Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2016-08-30 | 3125.3206 | 101.686 | Dorm | 58 | 22.95% | ü | 930.6794 | Hinshaw Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 23084.4457 | 0.75108 | 61.27% | 36523.5543 | Hinshaw Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 659800 | 7672.093 | 21.4674 | -101.2% | Hinshaw Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Jamison Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 357.3837 | 4 | Jamison Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2016-08-30 | 2556.1476 | 83.1673 | Dorm | 58 | 36.98% | ü | 1499.8524 | Jamison Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 18248.3678 | 0.59373 | 69.39% | 41359.6322 | Jamison Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 835400 | 9713.9535 | 27.1807 | -154.8% | Jamison Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Shaw Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 118 | 54847 | 464.8051 | 4 | Shaw Residence Hall Renovation | 90.1-2004 | 4 | 4056 | 73.9512 | 3076 | 56.0833 | 24.16% | 980 | 2016-08-30 | 6727.3246 | 122.6562 | Dorm | 58 | -65.86% |  | -2671.3246 | Shaw Residence Hall Renovation | 59608 | 1.0868 | 46163 | 0.84167 | 22.56% | 13445 | 33127.2343 | 0.60399 | 44.42% | 26480.7657 | Shaw Residence Hall Renovation | 327880 | 2778.6441 | 5.9781 | 209536 | 1775.7288 | 3.8204 | 36.09% | 118344 | 1240811.7647 | 10515.3539 | 22.6231 | -278.4% | Shaw Residence Hall Renovation | 6196641.1429 | 112.9805 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Harrill Residence Hall Renovation | Gold | WCU | Jackson | David King <dbking@email.wcu.edu> | 03-07291-02A | 2011-01-07 | CD | 2011-08-03 | 2012-08-02 | Residence Hall | 350 | 71505 | 204.3 | 10 | Harrill Residence Hall Renovation | 90.1-2004 | 4 | 5122 | 71.6314 | 3189 | 44.5983 | 37.74% | 1933 | 2016-07-15 | 2231.7027 | 31.2104 | Dorm | 58 | 56.43% |  | 2890.2973 | Harrill Residence Hall Renovation | 114129 | 1.5961 | 82978 | 1.1605 | 27.29% | 31151 | 43374.1987 | 0.60659 | 62% | 70754.8013 | Harrill Residence Hall Renovation | 2675470 | 7644.2 | 37.4165 | 1801347 | 5146.7057 | 25.1919 | 32.67% | 874123 | 1419051.3494 | 4054.4324 | 19.8455 | 46.96% | Harrill Residence Hall Renovation | 13435000 | 187.889 | 11750000 | 998800 | 0 |  | 153235 | 59.0105 | Optima | 90.1-2004
Renaissance Residence Hall | Silver | FSU | Cumberland | Jon Parsons | 11-08594-01A | 2011-09-12 | CD | No Contract (Found. Proj) | 2012-08-07 | Residence Hall | 340 | 85000 | 250 | 3 | Renaissance Residence Hall | 90.1-2004 | 3 | 5499 | 64.6941 | 3624 | 42.6353 | 34.1% | 1875 | No data |  |  | Dorm | 47 |  |  |  | Renaissance Residence Hall | 174915 | 2.0578 | 88110 | 1.0366 | 49.63% | 86805 |  |  |  |  | Renaissance Residence Hall | 2636463 | 7754.3029 | 31.0172 | 1734140 | 5100.4118 | 20.4016 | 34.22% | 902323 |  |  |  |  | Renaissance Residence Hall | (Foundation Project) |  |  | (Foundation Project) | (Foundation Project) |  | (Foundation Project) |  | Optima | 90.1-2004
Health Science Building | Silver | UNCP | Robeson | Terry W. Divine <terry.divine@uncp.edu> | 06-06859-02A | 2009-11-17 | CD | 2010-07-16 | 2012-08-07 | Office/Classroom | NA | 87000 |  | 3 | Health Science Building | 90.1-2004 | 3 | 7163 | 82.3333 | 4954 | 56.9425 | 30.84% | 2209 | 2016-08-22 | 7385.2468 | 84.8879 | Col/Univ | 62 | -3.103% |  | -222.2468 | Health Science Building | 98379 | 1.1308 | 65154 | 0.7489 | 33.77% | 33225 | 131773.8643 | 1.5146 | -33.95% | -33394.8643 | Health Science Building | 2606625 | NA | 29.9612 | 1672375 | NA | 19.2227 | 35.84% | 934250 | No Data |  |  |  | Health Science Building | 14834300 | 170.5092 | 14419316 | 2004260 | 47460 |  | 0 | 13.9186 | MSWG | 90.1-2004
Overlook Residence Hall | None | UNCA | Buncombe | 'dtodd@unca.edu' | 09-07924-02B | 2011-02-28 | CD | 2011-07-14 | 2012-08-08 | Residence Hall | 300 | 91370 | 304.5667 | 6 | Overlook Residence Hall | 90.1-2004 | 4 | 5737 | 62.7887 | 3460 | 37.868 | 39.69% | 2277 | 2016-08-31 |  |  | Dorm | 58 |  |  |  | Overlook Residence Hall | 89281 | 0.97714 | 63609 | 0.69617 | 28.75% | 25672 |  |  |  |  | Overlook Residence Hall | 2888310 | 9627.7 | 31.6111 | 1728304 | 5761.0133 | 18.9154 | 40.16% | 1160006 | 4225452 | 14084.84 | 46.2455 | -46.29% | Overlook Residence Hall | 16467600 | 180.2298 | 14927082 | 1685000 | 0 |  | 85000 | 63.3187 | MSWG | 90.1-2004
Viking Tower Residence Hall | None | ECSU | Pasquotank | Elizabeth Linney | 00-06539-03A | 2010-09-03 | CD | 2011-01-25 | 2012-08-17 | Residence Hall | 210 | 53896 | 256.6476 | 3 | Viking Tower Residence Hall | 90.1-2004 | 3 | 9118 | 169.1777 | 6399 | 118.7287 | 29.82% | 2719 | 2016-09-22 | 2114.1583 | 39.2266 | Dorm | 47 | 76.81% | ü | 7003.8417 | Viking Tower Residence Hall | 217417 | 4.034 | 145256 | 2.6951 | 33.19% | 72161 | 56971.07 | 1.0571 | 73.8% | 160445.93 | Viking Tower Residence Hall | 1193460 | 5683.1429 | 22.1438 | 938250 | 4467.8571 | 17.4085 | 21.38% | 255210 | 2005449 | 9549.7571 | 37.2096 | -68.04% | Viking Tower Residence Hall | 12474496 | 231.455 | 12222788 | 1199950 | 40000 |  | 85000 | 5.2204 | RMF | 90.1-2004
Teaching Laboratory Building | Silver | UNCW | New Hanover | Steve Sharpe | 07-07129-02A | 2010-08-06 | CD | 2011-01-21 | 2012-08-24 | Office/Classroom/Labs | NA | 85000 |  | 3 | Teaching Laboratory Building | 90.1-2004 | 3 | 7739 | 91.0471 | 4808 | 56.5647 | 37.87% | 2931 | No data |  | 0 | Col/Univ | 62 |  |  |  | Teaching Laboratory Building | 142633 | 1.678 | 90792 | 1.0681 | 36.35% | 51841 |  |  |  |  | Teaching Laboratory Building | 751030 | NA | 8.8356 | 507514 | NA | 5.9708 | 32.42% | 243516 |  |  |  |  | Teaching Laboratory Building | 15645200 | 184.0612 | 15440699 | 2615450 | 156820 |  | 0 | 6.9698 | RMF | 90.1-2004
Rhoades Hall Renovation | None | UNCA | Buncombe | 'dtodd@unca.edu' | 06-06994-02B | 2009-05-11 | CD | 2010-04-26 | 2012-09-10 | Classroom/Lab/Offices | NA | 40434 |  | 3 and 4 | Rhoades Hall Renovation | 90.1-2004 | 4 | 3231 | 79.908 | 1185 | 29.307 | 63.32% | 2046 | 2016-08-31 |  |  | Col/Univ | 72 |  |  |  | Rhoades Hall Renovation | 98370 | 2.4329 | 43014 | 1.0638 | 56.27% | 55356 |  |  |  |  | Rhoades Hall Renovation | 957500 | NA | 23.6806 | 655500 | NA | 16.2116 | 31.54% | 302000 | 985864 | NA | 24.3821 | -2.962% | Rhoades Hall Renovation | 5996300 | 148.2985 | 5834600 | 859165 | 76500 |  | 0 |  | ESE | 90.1-2004
Ledyard E. Ross Hall | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 07-07054-02A | 2010-04-16 | CD | 2010-07-01 | 2012-09-14 | Offices/Classrooms/Labs | NA | 157410 |  | 5 | Ledyard E. Ross Hall | 90.1-2004 | 3 | 43253 | 274.7792 | 27864 | 177.0154 | 35.58% | 15389 | 2016-08-09 | 20265.3761 | 128.7426 | Lab | 175 | 53.15% | ü | 22987.6239 | Ledyard E. Ross Hall | 420065 | 2.6686 | 302543 | 1.922 | 27.98% | 117522 | 203551.275 | 1.2931 | 51.54% | 216513.725 | Ledyard E. Ross Hall | 1373584 | NA | 8.7262 | 905161 | NA | 5.7503 | 34.1% | 468423 | No Data |  |  |  | Ledyard E. Ross Hall | 33176057 | 210.7621 | 32922547 | 5394860 | 100000 |  | 346397 |  | BR+A | 90.1-2004
Lena Sue Beam Renovation | None | Gaston College | Gaston | Cynthia McCrory | 07-07395-02A | 2011-03-03 | CD | 2011-07-29 | 2012-10-03 | Office/Classroom | NA | 31418 |  | 2 | Lena Sue Beam Renovation | 90.1-2004 | 4 | 1732 | 55.1276 | 1161 | 36.9533 | 32.97% | 571 | 2016-08-30 | 1918.4008 | 61.0606 | Col/Univ | 72 | -10.76% |  | -186.4008 | Lena Sue Beam Renovation | 36406 | 1.1588 | 25403 | 0.80855 | 30.22% | 11003 | 33329.6249 | 1.0608 | 8.45% | 3076.3751 | Lena Sue Beam Renovation | 689715 | NA | 21.9529 | 403299 | NA | 12.8366 | 41.53% | 286416 | 130253 | NA | 4.1458 | 81.11% | Lena Sue Beam Renovation | 4701800 | 149.6531 | 4657494 | 474000 | 0 |  | 56984 | 9.2057 | M&L | 90.1-2004
Hunt Library | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 07-07171-02A | 2010-08-06 | CD-2 | 2009-08-25 | 2012-10-18 | Library/Offices/Lecture Hall/Meeting | NA | 253028 |  | 4 | Hunt Library | 90.1-2004 | 4 | 15191 | 60.0368 | 10342 | 40.8729 | 31.92% | 4849 | 2016-09-01 | 30208.4281 | 119.3877 | Library | 67 | -98.86% |  | -15017.4281 | Hunt Library | 268448 | 1.0609 | 184680 | 0.72988 | 31.2% | 83768 | 590039.253 | 2.3319 | -119.8% | -321591.253 | Hunt Library | 4536750 | NA | 17.9298 | 2948625 | NA | 11.6534 | 35.01% | 1588125 | 1765280 | NA | 6.9766 | 61.09% | Hunt Library | 81306000 | 321.332 | 80844228 | 9829956 | 200000 |  | 605005 |  | AEI | 90.1-2004
NC Veterans Home - Kinston | None | NCDVA | Lenoir | diane.norris@doa.nc.gov | 06-06924-05A | 2009-12-22 | CD | 2010-05-24 | 2012-10-31 | Nursing Home /Assisted Living | 100 | 108770 |  | 1 | NC Veterans Home - Kinston | 90.1-2004 | 3 | 8495 | 78.1006 | 5163 | 47.4671 | 39.22% | 3332 | 2016-08-01 | 15542.936 | 142.8973 | Nursing home | 83 | -82.97% |  | -7047.936 | NC Veterans Home - Kinston | 213106 | 1.9592 | 120807 | 1.1107 | 43.31% | 92299 | 200385.01 | 1.8423 | 5.969% | 12720.99 | NC Veterans Home - Kinston | 4378540 | 43785.4 | 40.255 | 3400982 | 34009.82 | 31.2676 | 22.33% | 977558 | 6710400 | 67104 | 61.6935 | -53.26% | NC Veterans Home - Kinston | 12903000 | 118.6265 | 12602128 | 1077600 | 0 |  | 107804 | 4.4277 | MCBH | 90.1-2004
Judy W. Rose Football Center | Certified | UNCC | Mecklenburg | Tony Schallert | 08-07833-02A | 2010-12-10 | CD | 2011-03-29 | 2012-10-31 | Lockerrooms/Offices | NA | 43290 |  | 2 | Judy W. Rose Football Center | 90.1-2004 | 3 | 8320 | 192.1922 | 5184 | 119.7505 | 37.69% | 3136 | 2016-08-05 | 9016.7796 | 208.2878 | Col/Univ | 62 | -8.375% |  | -696.7796 | Judy W. Rose Football Center | 65175 | 1.5055 | 44151 | 1.0199 | 32.26% | 21024 | 132230.9567 | 3.0545 | -102.9% | -67055.9567 | Judy W. Rose Football Center | 1349491 | NA | 31.1733 | 1113354 | NA | 25.7185 | 17.5% | 236137 | 2412382.28 | NA | 55.7261 | -78.76% | Judy W. Rose Football Center | 12987000 | 300 | 12521456 | 3448472 | 45000 |  | 99500 |  | M&C | 90.1-2004
Continuing Education and Industrial Center | Gold | Randolph CC | Randolph | Cindi Goodwin | 07-07252-03A | 2010-12-08 | CD | 2011-10-14 | 2012-11-27 | Office/Classroom/Labs | NA | 43967 |  | 1 | Continuing Education and Industrial Center | 90.1-2004 | 3 | 2940 | 66.8683 | 1839 | 41.8268 | 37.45% | 1101 | 2016-08-03 | 3543.0363 | 80.584 | Col/Univ | 72 | -20.51% |  | -603.0363 | Continuing Education and Industrial Center | 67485 | 1.5349 | 43675 | 0.99336 | 35.28% | 23810 | 78538.2 | 1.7863 | -16.38% | -11053.2 | Continuing Education and Industrial Center | 544858 | NA | 12.3924 | 436998 | NA | 9.9392 | 19.8% | 107860 | 27302 | NA | 0.62097 | 94.99% | Continuing Education and Industrial Center | 6361300 | 144.6835 | 6060565 | 363200 | 0 |  | 49800 | 14.7222 | PDC | 90.1-2004
Plemmons Student Union Addition | Gold | ASU | Watauga | Jerry Marshall | 08-07327-02A | 2010-08-19 | CD | 2010-06-08 | 2012-12-18 | Office/Classroom/Conference | NA | 50560 |  | 4 | Plemmons Student Union | 90.1-2004 | 5 | 2185 | 43.216 | 1346 | 26.6218 | 38.4% | 839 | 2016-08-12 | 10320.7015 | 204.1278 | Rest/Cafet | 179 | -372.3% |  | -8135.7015 | Plemmons Student Union | 53367 | 1.0555 | 32912 | 0.65095 | 38.33% | 20455 | 240223.2743 | 4.7513 | -350.1% | -186856.2743 | Plemmons Student Union | 1220706 | NA | 24.1437 | 950466 | NA | 18.7988 | 22.14% | 270240 | 3402873 | NA | 67.3037 | -178.8% | Plemmons Student Union | 15232506 | 301.2758 | 14629006 | 985521.6 | 90950 |  | 71248.14 | 37.4333 | SKA | 90.1-2004
Summit Living Learning Center | In Progress | ASU | Watauga | Jerry Marshall | 08-07327-02A | 2010-08-19 | CD | 2010-06-08 | 2012-12-18 | Residence Hall / Office Classrooms | 333 | 128585 | 386.1411 | 11 and 3 | Summit Living Learning Center | 90.1-2004 | 5 | 6323 | 49.1737 | 3660 | 28.4637 | 42.12% | 2663 | 2016-08-12 | 8394.074 | 65.2804 | Col/Univ | 78 | -32.75% |  | -2071.074 | Summit Living Learning Center | 153208 | 1.1915 | 89024 | 0.69234 | 41.89% | 64184 | 208325.366 | 1.6201 | -35.98% | -55117.366 | Summit Living Learning Center | 3388865 | 10176.7718 | 26.3551 | 1928009 | 5789.8168 | 14.994 | 43.11% | 1460856 | 2363896 | 7098.7868 | 18.3839 | 30.25% | Summit Living Learning Center | 40691217 | 316.4538 | 39309739 | 2664558.4 | 94925 |  | 192633.86 | 26.0039 | SKA | 90.1-2004
MARBIONC | Certified | UNCW | New Hanover | Steve Sharpe | 07-07853-02A | 2010-06-03 | DD | 2011-08-01 | 2013-01-29 | Labs/Offices | NA | 68000 |  | 2 | MARBIONIC | 90.1-2004 | 3 | 31233 | 459.3088 | 19781 | 290.8971 | 36.67% | 11452 | No data |  | 0 | Lab | 175 |  |  |  | MARBIONIC | 425995 | 6.2646 | 301801 | 4.4383 | 29.15% | 124194 |  |  |  |  | MARBIONIC | 5139169 | NA | 75.576 | 4083469 | NA | 60.051 | 20.54% | 1055700 |  |  |  |  | MARBIONIC | 24371201 | 358.4 | 19975000 | 2804957 | 110280 |  | 294243 | 38.655 | CRB/AEI | 90.1-2004
NC State Bar HQ | Silver | DOA | Wake | Joe Cerone <jcerone@ncbar.gov> | 09-07858-01A | 2011-05-31 | CD | 2011-11-28 | 2013-04-25 | Office/Courtroom | NA | 54565 |  | 4 | NC State Bar HQ | 90.1-2004 | 4 | 1689 | 30.9539 | 1116 | 20.4527 | 33.93% | 573 | 2016-07-19 | 3202.0766 | 58.6837 | Prof Office | 46 | -89.58% |  | -1513.0766 | NC State Bar HQ | 45238 | 0.82907 | 29457 | 0.53985 | 34.88% | 15781 | 83761.3 | 1.5351 | -85.16% | -38523.3 | NC State Bar HQ | 175310 | NA | 3.2129 | 116629 | NA | 2.1374 | 33.47% | 58681 | 229636 | NA | 4.2085 | -30.99% | NC State Bar HQ | 12962700 | 237.5644 | 12687413 | 1125000 | 6000 |  | 56200 | 21.3857 | CJMW | 90.1-2004
Science and Technology Building | Silver | FSU | Cumberland | Jon Parsons | 06-06971-02A | 2011-01-11 | Final | 2011-06-27 | 2013-05-21 | Office/Classrooms/Labs | NA | 65861 |  | 4 | Science and Technology Building | 90.1-2004 | 3 | 13356 | 202.7907 | 9641 | 146.3841 | 27.82% | 3715 | No data |  |  | Col/Univ | 62 |  |  |  | Science and Technology Building | 151889 | 2.3062 | 100888 | 1.5318 | 33.58% | 51001 |  |  |  |  | Science and Technology Building | 2163492 | NA | 32.8494 | 1785946 | NA | 27.1169 | 17.45% | 377546 |  |  |  |  | Science and Technology Building | 17028032 | 258.545 | 16327000 | 1576000 | 135000 |  | 290182 | 22.0822 | M&C | 90.1-2004
Student Recreation Facility Addition | Certified | UNCW | New Hanover | Steve Sharpe | 07-07060-03A | 2010-06-02 | CD | 2011-04-25 | 2013-05-22 | Gym/pool/fitness/courts/lockerrom | NA | 93917 |  | 2 | Student Recreation Facility Addition | 90.1-2004 | 3 | 22917 | 244.0133 | 15931 | 169.6285 | 30.48% | 6986 | No data |  | 0 | [5 empty] | Student Recreation Facility Addition | 351452 | 3.7422 | 248190 | 2.6427 | 29.38% | 103262 |  |  |  |  | Student Recreation Facility Addition | 810220 | NA | 8.627 | 634243 | NA | 6.7532 | 21.72% | 175977 |  |  |  |  | Student Recreation Facility Addition | 21478228 | 228.6937 | 20845432 | 2510110 | 215000 |  | 126000 | 9.4303 | SWA | 90.1-2004
Reaves Student Activities Center | Gold | WSSU | Forsyth | Dick Kabis | 06-07181-01A | 2010-10-25 | CD | 2011-05-17 | 2013-06-24 | Gym/Food Service/ | NA | 91513 |  | 3 | Reaves Student Activities Center | 90.1-2004 | 4 | 7587 | 82.9063 | 5004 | 54.6808 | 34.05% | 2583 | 2016-08-12 | 9764.0921 | 106.6962 |  |  | -28.7% |  | -2177.0921 | Reaves Student Activities Center | 105529 | 1.1532 | 66125 | 0.72257 | 37.34% | 39404 | 191606.9599 | 2.0938 | -81.57% | -86077.9599 | Reaves Student Activities Center | 1434603 | NA | 15.6765 | 990985 | NA | 10.8289 | 30.92% | 443618 | 597135.88 | NA | 6.5251 | 58.38% | Reaves Student Activities Center | 25393206 | 277.482 | 25315267 | 2408119 | 177240 |  | 287625 | 13.7754 | Sud | 90.1-2004
Creative Arts Building | In Progress | Haywood CC | Haywood | Josh Best rjbest@haywood.edu | 07-07315-03A | 2009-11-02 | DD-2 | 2010-10-28 | 2013-06-30 | Art studios, classrooms, offices | NA | 40722 |  | 3 | Creative Arts Building | 90.1-2004 | 4 | 3603 | 88.478 | 1672 | 41.0589 | 53.59% | 1931 | 2016-09-01 | 1859.3974 | 45.6608 | Col/Univ | 72 | 48.39% | ü | 1743.6026 | Creative Arts Building | 65069 | 1.5979 | 19856 | 0.4876 | 69.48% | 45213 | 22920.42 | 0.56285 | 64.78% | 42148.58 | Creative Arts Building | 977508 | NA | 24.0044 | 255213 | NA | 6.2672 | 73.89% | 722295 | 154338 | NA | 3.79 | 84.21% | Creative Arts Building | 8385286 | 205.9154 | 6402774 | 851000 | 50000 |  | 80000 | 46.7236 | Elm | 90.1-2004
Belk Residence Hall | None | UNCC | Mecklenburg | Tony Schallert | 10-08450-02A | 2011-12-22 | CD-2 | 2012-01-17 | 2013-07-09 | Residence Hall | 400 | 164377 | 410.9425 | 5 | Belk Residence Hall | 90.1-2004 | 3 | 10765 | 65.4897 | 7239 | 44.039 | 32.75% | 3526 | 2016-08-05 | 9281.6801 | 56.4658 | Dorm | 47 | 13.78% |  | 1483.3199 | Belk Residence Hall | 149183 | 0.90757 | 97190 | 0.59126 | 34.85% | 51993 | 132904.9425 | 0.80854 | 10.91% | 16278.0575 | Belk Residence Hall | 2719308 | 6798.27 | 16.5431 | 1869230 | 4673.075 | 11.3716 | 31.26% | 850078 | 5659473.68 | 14148.6842 | 34.4298 | -108.1% | Belk Residence Hall | 30027284 | 182.6733 | 30027284 | 2167790 | 126000 |  | 186000 |  |  | 90.1-2004
Cherry Building Renovation | None | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 10-08698-02A | 2011-11-17 | CD | 2012-07-12 | 2013-07-15 | Office/Classroom | NA | 22482 |  | 2.5 | Cherry Building Renovation | 90.1-2004 | 4 | 1449 | 64.4516 | 1017 | 45.2362 | 29.81% | 432 | 2016-09-01 | 1668.3426 | 74.2079 | High School | 52 | -15.14% |  | -219.3426 | Cherry Building Renovation | 27666 | 1.2306 | 21821 | 0.9706 | 21.13% | 5845 | 32612.7479 | 1.4506 | -17.88% | -4946.7479 | Cherry Building Renovation | 166500 | NA | 7.4059 | 120425 | NA | 5.3565 | 27.67% | 46075 | 100329.9897 | NA | 4.4627 | 39.74% | Cherry Building Renovation | 2670270 | 118.7737 | 2645494 | 292501 | 0 |  | 0 |  | SWA | 90.1-2004
Hunt Residence Hall | None | UNCC | Mecklenburg | Tony Schallert | 10-08610-03A | 2012-02-24 | CD | 2012-01-17 | 2013-07-29 | Residence Hall | 436 | 144175 | 330.6766 | 5 | Hunt Residence Hall | 90.1-2004 | 3 | 11671 | 80.9502 | 6976 | 48.3856 | 40.23% | 4695 | 2016-08-05 | 7923.7754 | 54.9594 | Dorm | 47 | 32.11% | ü | 3747.2246 | Hunt Residence Hall | 141674 | 0.98265 | 87499 | 0.60689 | 38.24% | 54175 | 95606.8933 | 0.66313 | 32.52% | 46067.1067 | Hunt Residence Hall | 1100206 | 2523.4083 | 7.631 | 860579 | 1973.805 | 5.969 | 21.78% | 239627 | 2661077.32 | 6103.3883 | 18.4573 | -141.9% | Hunt Residence Hall | 24655367 | 171.01 | 22816693 | 2078598 | 0 |  | 297680 |  | CN | 90.1-2004
Wolf Ridge at Centennial Bldg 6 - Lakeview Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-08-01 | Residence Hall | 151 | 67202 | 445.0464 | 6 | Wolf Ridge at Centennial Bldg 6 | 90.1-2004 | 4 | 4126 | 61.397 | 2853 | 42.4541 | 30.85% | 1273 | 2016-09-01 | 6660.6981 | 99.1146 | Dorm | 58 | -61.43% |  | -2534.6981 | Wolf Ridge at Centennial Bldg 6 | 76622 | 1.1402 | 51093 | 0.76029 | 33.32% | 25529 | 107302.4472 | 1.5967 | -40.04% | -30680.4472 | Wolf Ridge at Centennial Bldg 6 | 1630661 | 10799.0795 | 24.2651 | 1029702 | 6819.2185 | 15.3225 | 36.85% | 600959 | 517616 | 3427.9205 | 7.7024 | 68.26% | Wolf Ridge at Centennial Bldg 6 | 14207759 | 211.4187 | 11410139.74 | 995826.9923 | 0 |  | 47050.2499 |  | Dewberry | 90.1-2004
Wolf Ridge at Centennial Bldg 1 - Tower Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-08-01 | Residence Hall & Dining Hall | 251 | 154726 | 616.4382 | 6 | Wolf Ridge at Centennial Bldg 1 - Tower Hall | 90.1-2004 | 4 | 12056 | 77.9184 | 8300 | 53.6432 | 31.15% | 3756 | 2016-09-01 | 15729.4547 | 101.6601 | Dorm | 58 | -30.47% |  | -3673.4547 | Wolf Ridge at Centennial Bldg 1 - Tower Hall | 220350 | 1.4241 | 143383 | 0.92669 | 34.93% | 76967 | 276374.6503 | 1.7862 | -25.43% | -56024.6503 | Wolf Ridge at Centennial Bldg 1 - Tower Hall | 5618485 | 22384.4024 | 36.3125 | 4483837 | 17863.8924 | 28.9792 | 20.19% | 1134648 | 2116840 | 8433.6255 | 13.6812 | 62.32% | Wolf Ridge at Centennial Bldg 1 | 32712171 | 211.42 | 26270927.62 | 2292793.7742 | 0 |  | 108328.5759 |  | Dewberry | 90.1-2004
Spartan Village 1 - Lee Residence Hall | Silver | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 243 | 116224 | 478.2881 | 5 | Spartan Village 1 - Lee Residence Hall | 90.1-2004 | 4 | 5889 | 50.6694 | 4141 | 35.6295 | 29.68% | 1748 | 2016-08-30 | 3222.3179 | 27.7251 | Apart | 46 | 45.28% | ü | 2666.6821 | Spartan Village 1 - Lee Residence Hall | 127318 | 1.0955 | 80286 | 0.69079 | 36.94% | 47032 | 72819.93 | 0.62655 | 42.8% | 54498.07 | Spartan Village 1 - Lee Residence Hall | 2900134 | 11934.7078 | 24.953 | 2258696 | 9295.0453 | 19.434 | 22.12% | 641438 | 1677016 | 6901.3004 | 14.4292 | 42.17% | Spartan Village 1 - Lee Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Spartan Village 3 - Haywood Residence Hall | Silver | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 130 | 56295 | 433.0385 | 5 | Spartan Village 3 - Haywood Residence Hall | 90.1-2004 | 4 | 5889 | 104.6096 | 4141 | 73.5589 | 29.68% | 1748 | 2016-08-30 | 1749.9322 | 31.085 | Apart | 46 | 70.28% | ü | 4139.0678 | Spartan Village 3 - Haywood Residence Hall | 127318 | 2.2616 | 80286 | 1.4262 | 36.94% | 47032 | 39904.32 | 0.70884 | 68.66% | 87413.68 | Spartan Village 3 - Haywood Residence Hall | 1736095 | 13354.5769 | 30.8392 | 1384588 | 10650.6769 | 24.5952 | 20.25% | 351507 | 831776 | 6398.2769 | 14.7753 | 52.09% | Spartan Village 3 - Haywood Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Spartan Village 4 - Union Residence Hall | Silver | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 209 | 89104 | 426.3349 | 5 | Spartan Village 4 - Union Residence Hall | 90.1-2004 | 4 | 5889 | 66.0913 | 4141 | 46.4738 | 29.68% | 1748 | 2016-08-30 | 2544.3501 | 28.5548 | Apart | 46 | 56.79% | ü | 3344.6499 | Spartan Village 4 - Union Residence Hall | 127318 | 1.4289 | 80286 | 0.90104 | 36.94% | 47032 | 57042.94 | 0.64018 | 55.2% | 70275.06 | Spartan Village - Building 4 | 2627757 | 12573 | 29.4909 | 2069683 | 9902.7895 | 23.2277 | 21.24% | 558074 | 1345652 | 6438.5263 | 15.102 | 48.79% | Spartan Village 4 - Union Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Martin-Schexnider Residence Hall | Certified | WSSU | Forsyth | Dick Kabis | 11-09099-02A | 2012-07-18 | CD | No Contract (Privately Funded) | 2013-08-13 | Residence Hall | 227 | 55626 | 245.0485 | 5 | Martin-Schexnider Residence Hall | 90.1-2004 | 4 | 6193 | 111.3328 | 4672 | 83.9895 | 24.56% | 1521 | 2016-08-12 | 8030.0664 | 144.3581 | Dorm | 58 | -29.66% |  | -1837.0664 | Martin-Schexnider Residence Hall | 87219 | 1.568 | 53012 | 0.95301 | 39.22% | 34207 | 101331.4417 | 1.8217 | -16.18% | -14112.4417 | Martin-Schexnider Residence Hall | 2317437 | 10208.9736 | 41.661 | 1848705 | 8144.0749 | 33.2345 | 20.23% | 468732 | 4179382.68 | 18411.3774 | 75.1336 | -80.35% | Martin-Schexnider Residence Hall | 10000000 | 179.772 | 9516280 | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | M&C | 90.1-2004
Union Station | Silver | Cape Fear CC | New Hanover | Ken Pearce | 07-07399-03A | 2010-05-05 | CD | 2010-11-10 | 2013-08-22 | Office/Classroom/Auditorium | NA | 233900 |  | 6 | Union Station | 90.1-2004 | 3 | 12463 | 53.2835 | 8391 | 35.8743 | 32.67% | 4072 | 2016-09-12 | 28554.8028 | 122.0812 | Col/Univ | 62 | -129.1% |  | -16091.8028 | Union Station | 407210 | 1.741 | 294497 | 1.2591 | 27.68% | 112713 | 388989.38 | 1.6631 | 4.475% | 18220.62 | Union Station | 1939781 | NA | 8.2932 | 1222056 | NA | 5.2247 | 37% | 717725 | 4104276 | NA | 17.5471 | -111.6% | Union Station | 38141300 | 163.0667 | 37627193 | 6113085 | 339250 |  | 237711 | 9.6801 | Cheatham | 90.1-2004
Smith-Williams Center | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 08-07305-01F | 2012-03-01 | CD | 2012-05-01 | 2013-08-27 | Gym/Office | NA | 49170 |  | 2 | Smith-Williams Center | 90.1-2004 | 3 | 2396 | 48.7289 | 1518 | 30.8725 | 36.64% | 878 | 2016-08-09 | 3729.7454 | 75.8541 | Recreat | 26 | -55.67% |  | -1333.7454 | Smith-Williams Center | 48568 | 0.98776 | 38507 | 0.78314 | 20.72% | 10061 | 40839.2887 | 0.83057 | 15.91% | 7728.7113 | Smith-Williams Center | 347984 | NA | 7.0772 | 227682 | NA | 4.6305 | 34.57% | 120302 | No data |  |  |  | Smith-Williams Center | 13828376 | 281.236 | 12357348 | 736500 |  |  | 128800 |  | Edi | 90.1-2004
Wolf Ridge at Centennial Bldg 2 - Plaza Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-12-05 | Residence Hall | 223 | 84876 | 380.6099 | 6 | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 90.1-2004 | 4 | 5653 | 66.603 | 3934 | 46.35 | 30.41% | 1719 | 2016-09-01 | 6111.3624 | 72.0034 | Dorm | 58 | -8.108% |  | -458.3624 | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 102040 | 1.2022 | 70049 | 0.82531 | 31.35% | 31991 | 104016.0318 | 1.2255 | -1.937% | -1976.0318 | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 2385879 | 10699.009 | 28.1102 | 1498371 | 6719.1525 | 17.6536 | 37.2% | 887508 | 1066648 | 4783.1749 | 12.5671 | 55.29% | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 17944484 | 211.42 | 14286216 | 1257727.6242 | 0 |  | 59424.3774 |  | Dewberrry | 90.1-2004
Spartan Village 2 - Highland Residence Hall | Silver | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2014-01-09 | Residence Hall | 231 | 110627 | 478.9048 | 5 | Spartan Village 2 - Highland Residence Hall | 90.1-2004 | 4 | 5889 | 53.2329 | 4141 | 37.4321 | 29.68% | 1748 | 2016-08-30 | 3349.0996 | 30.2738 | Apart | 46 | 43.13% | ü | 2539.9004 | Spartan Village 2 - Highland Residence Hall | 127318 | 1.1509 | 80286 | 0.72574 | 36.94% | 47032 | 76217.97 | 0.68896 | 40.14% | 51100.03 | Spartan Village 2 - Highland Residence Hall | 2916495 | 12625.5195 | 26.3633 | 2297942 | 9947.8009 | 20.772 | 21.21% | 618553 | 1756304 | 7603.0476 | 15.8759 | 39.78% | Spartan Village 2 - Highland Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
PORTAL | None | UNCC | Mecklenburg | Tony Schallert | 08-07560-03A | 2011-02-03 | CD | 2012-04-09 | 2014-01-28 | Office | NA | 102914 |  | 4 | PORTAL | 90.1-2004 | 3 | 7934 | 77.0935 | 5513 | 53.569 | 30.51% | 2421 | 2016-08-05 | 8370.3726 | 81.3337 | Col/Univ | 62 | -5.5% |  | -436.3726 | PORTAL | 142246 | 1.3822 | 98494 | 0.95705 | 30.76% | 43752 | 81083.6788 | 0.78788 | 43% | 61162.3212 | PORTAL | 776459 | NA | 7.5447 | 565009 | NA | 5.4901 | 27.23% | 211450 | 98967.88 | NA | 0.96166 | 87.25% | PORTAL | 25748184 | 250.1913 | 24736184 | 2215000 | 0 |  | 240424 | 28.6255 | M&C | 90.1-2004
Wolf Ridge at Centennial Bldg 3 - Innovation Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-02-06 | Residence Hall | 219 | 88512 | 404.1644 | 6 | Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 90.1-2004 | 4 | 5069 | 57.2691 | 3543 | 40.0285 | 30.1% | 1526 | 2016-09-01 | 5019.298 | 56.7075 | Dorm | 58 | 0.9805% |  | 49.702 | Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 91459 | 1.0333 | 63494 | 0.71735 | 30.58% | 27965 | 87059.4298 | 0.98359 | 4.81% | 4399.5702 | Wolf Ridge at Centennial Bldg 3 | 2343922 | 10702.8402 | 26.4814 | 1472334 | 6722.9863 | 16.6343 | 37.19% | 871588 | 513876 | 2346.4658 | 5.8057 | 78.08% | Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 18713207 | 211.42 |  | 1311607.3739 | none noted |  | 61970.0562 |  | Dewberry | 90.1-2004
Hill Hall Renovation | Gold | WSSU | Forsyth | Dick Kabis | 11-08884-03A | 2012-09-27 | CD | 2012-12-13 | 2014-03-25 | Offices | NA | 37898 |  | 3 | Hill Hall Renovation - Student Success Center | 90.1-2007 | 4 | 2638 | 69.6079 | 1913 | 50.4776 | 27.48% | 725 | 2016-08-12 | 5904.0545 | 155.788 | Col/Univ | 72 | -123.8% |  | -3266.0545 | Hill Hall Renovation - Student Success Center | 41267 | 1.0889 | 25579 | 0.67494 | 38.02% | 15688 | 77663.2946 | 2.0493 | -88.2% | -36396.2946 | Hill Hall Renovation - Student Success Center | 2719308 | NA | 71.7533 | 1869230 | NA | 49.3227 | 31.26% | 850078 | 238612 | NA | 6.2962 | 91.23% | Hill Hall Renovation - Student Success Center | 10890470 | 287.3627 | 10890470 | 1125000 | 100000 |  | 90000 | 12.1112 | CN | 90.1-2007
Wolf Ridge at Centennial Bldg 5 - Grove Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-04-09 | Residence Hall | 144 | 62645 | 435.0347 | 6 | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 90.1-2004 | 4 | 3959 | 63.1974 | 2756 | 43.9939 | 30.39% | 1203 | 2016-09-01 | 5079.0775 | 81.0771 | Dorm | 58 | -28.29% |  | -1120.0775 | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 73439 | 1.1723 | 49084 | 0.78353 | 33.16% | 24355 | 76081.3207 | 1.2145 | -3.598% | -2642.3207 | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 1557237 | 10814.1458 | 24.8581 | 984137 | 6834.2847 | 15.7097 | 36.8% | 573100 | 488444 | 3391.9722 | 7.797 | 68.63% | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 13244406 | 211.42 |  | 928299.4841 | none noted |  | 43859.7498 |  | Dewberry | 90.1-2004
Wolf Ridge at Centennial Bldg 4 - Valley Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-05-09 | Residence Hall | 219 | 83460 | 381.0959 | 6 | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 90.1-2004 | 4 | 5197 | 62.2694 | 3476 | 41.6487 | 33.12% | 1721 | 2016-09-01 | 5078.8591 | 60.8538 | Dorm | 58 | 2.273% |  | 118.1409 | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 96219 | 1.1529 | 61768 | 0.74009 | 35.8% | 34451 | 84361.3391 | 1.0108 | 12.32% | 11857.6609 | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 2343922 | 10702.8402 | 28.0844 | 1472334 | 6722.9863 | 17.6412 | 37.19% | 871588 | 154088 | 703.5982 | 1.8462 | 93.43% | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 17645113 | 211.42 |  | 1236744.7513 | none noted |  | 58432.9909 |  | Dewberry | 90.1-2004
Aviation Center III Building | In Progress | GTCC | Guilford | mjohnson@gtcc.edu | 08-07309-02A | 2012-03-09 | CD | 2012-09-17 | 2014-07-21 | Office/Classroom | NA | 42087 |  | 4 | Aviation Center III Building | 90.1-2004 | 4 | 2425 | 57.6187 | 1699 | 40.3688 | 29.94% | 726 | 2016-08-05 | 2088.9237 | 49.6335 | Col/Univ | 72 | 13.86% |  | 336.0763 | Aviation Center III Building | 68705 | 1.6325 | 55378 | 1.3158 | 19.4% | 13327 | 39962.58 | 0.94952 | 41.83% | 28742.42 | Aviation Center III Building | 1135125 | NA | 26.9709 | 550575 | NA | 13.0818 | 51.5% | 584550 | 63580 | NA | 1.5107 | 94.4% | Aviation Center III Building | 6535600 | 155.2879 |  | 686500 | 20000 |  | 149249 |  | SWA | 90.1-2004
Martin Residence Hall | None | UNCC | Mecklenburg | Tony Schallert | 11-09156-02A | 2012-12-19 | CD | 2013-04-05 | 2014-08-13 | Residence Hall | 408 | 174657 | 428.0809 | 6 | Martin Residence Hall | 90.1-2007 | 3 | 21396 | 122.503 | 13060 | 74.7751 | 38.96% | 8336 | 2016-08-05 | 9112.4108 | 52.1732 | Dorm | 47 | 57.41% | ü | 12283.5892 | Martin Residence Hall | 306609 | 1.7555 | 210750 | 1.2067 | 31.26% | 95859 | 128462.1182 | 0.73551 | 58.1% | 178146.8818 | Martin Residence Hall | 4970906 | 12183.5931 | 28.461 | 3510140 | 8603.2843 | 20.0973 | 29.39% | 1460766 | 5002818.48 | 12261.81 | 28.6437 | -0.642% | Martin Residence Hall | 35192772 | 201.4965 | 29686104 | 2733245 | 15000 |  | 175000 | 59.4276 |  | 90.1-2007
New Library Building | None | UNCSA | Forsyth | boydc@uncsa.edu | 06-06981-05A | 2012-07-27 | FI | 2013-01-18 | 2014-09-09 | Library/Offices | NA | 73432 |  | 4 | New Library Building | 90.1-2004 | 4 | 6402 | 87.1827 | 4631 | 63.0651 | 27.66% | 1771 | No data |  |  | Fol/Univ | 67 |  |  |  | New Library Building | 90245 | 1.229 | 62106 | 0.84576 | 31.18% | 28139 |  |  |  |  | New Library Building | 706800 | NA | 9.6252 | 478350 | NA | 6.5142 | 32.32% | 228450 |  |  |  |  | New Library Building | 15433000 | 210.1672 | 17328709 | 1833332 | 0 |  | 108825 | -63.502 |  | 90.1-2004
Student Health Center | In Progress | NCA&T | Guilford | barlow@ncat.edu | 08-08109-02A | 2011-12-21 | DD | 2013-04-08 | 2014-10-29 | Offices/Clinics | NA | 27548 |  | 2 | Student Health Center | 90.1-2004 | 4 | 1911 | 69.3698 | 1336 | 48.4972 | 30.09% | 575 | 2016-08-06 | 1762.2514 | 63.9702 | Med Off Diag | 32 | 7.784% |  | 148.7486 | Student Health Center | 50033 | 1.8162 | 33648 | 1.2214 | 32.75% | 16385 | 25483.76 | 0.92507 | 49.07% | 24549.24 | Student Health Center | 154588 | NA | 5.6116 | 101825 | NA | 3.6963 | 34.13% | 52763 | 109208 | NA | 3.9643 | 29.36% | Student Health Center | 7444000 | 270.2193 | 7251633 | 785500 | 92000 |  | 51400 | 20.4923 | RMF | 90.1-2004
Campus Police Facility | Silver | UNCG | Guilford | Douglas Cato | 10-08905-03A | 2012-03-29 | CD | 2012-11-01 | 2014-11-12 | Offices | NA | 25877 |  | 2 | Campus Police Facility | 90.1-2004 | 4 | 2330 | 90.0413 | 1242 | 47.9963 | 46.7% | 1088 | 2016-08-30 | 2751.2913 | 106.3219 | Police Sta | 71 | -18.08% |  | -421.2913 | Campus Police Facility | 44281 | 1.7112 | 29471 | 1.1389 | 33.45% | 14810 | 48415.1928 | 1.871 | -9.336% | -4134.1928 | Campus Police Facility | 617945 | NA | 23.8801 | 478128 | NA | 18.4769 | 22.63% | 139817 | 106964 | NA | 4.1336 | 82.69% | Campus Police Facility | 6143700 | 237.4193 |  | 854040 | 43000 |  | 81680 |  | SWA | 90.1-2004
South Village Dining Facility | None | UNCC | Mecklenburg | Tony Schallert | 10-08633-03A | 2013-04-17 | FI | 2012-10-04 | 2014-11-21 | Food Service/Dining | NA | 56146 |  | 2 | South Village Dining Facility | 90.1-2004 | 3 | 12578 | 224.0231 | 7334 | 130.6237 | 41.69% | 5244 | 2016-08-05 | 16738.0843 | 298.1171 | Rest/café | 150 | -33.07% |  | -4160.0843 | South Village Dining Facility | 163454 | 2.9112 | 113314 | 2.0182 | 30.68% | 50140 | 192697.7964 | 3.4321 | -17.89% | -29243.7964 | South Village Dining Facility | 546557 | NA | 9.7346 | 435029 | NA | 7.7482 | 20.41% | 111528 | 4194417.48 | NA | 74.7055 | -667.4% | South Village Dining Facility | 26618418.39 | 474.0929 | 25649718.39 | 1918410 | 78000 |  | 182024 | 24.5059 | M&C | 90.1-2004
Moran Commons Dining Hall Renovation | None | UNCG | Guilford | Douglas Cato | 08-07382-02A | 2011-04-28 | CD | 2011-06-06 | 2015-02-05 | Food Service/Dining | NA | 111160 |  | 2 | Moran Commons Dining Hall Renovation | 90.1-2004 | 4 | 18584 | 167.1824 | 12522 | 112.6484 | 32.62% | 6062 | 2016-08-30 | 25465.0969 | 229.0851 | Rest/café | 166 | -37.03% |  | -6881.0969 | Moran Commons Dining Hall Renovation | 269366 | 2.4232 | 187898 | 1.6903 | 30.24% | 81468 | 230867.5238 | 2.0769 | 14.29% | 38498.4762 | Dining Hall Renovation | 6216053 | NA | 55.9199 | 3532573 | NA | 31.7792 | 43.17% | 2683480 | 5387297.96 | NA | 48.4644 | 13.33% | Dining Hall Renovation | 28459035 | 256.0187 |  | 2837884 | 60000 |  | 283540 |  | M&L | 90.1-2004
Center for Design Innovation | In Progress | WSSU | Forsyth | Dick Kabis | 06-06646-03A | 2013-05-03 | FI | 2012-04-12 | 2015-03-03 | Offices, classrooms, labs | NA | 23982 |  | 3 | Center for Design Innovation | 90.1-2007 | 4 | 4288 | 178.8008 | 2361 | 98.4488 | 44.94% | 1927 | 2016-08-12 | 1674.8205 | 69.8366 |  |  | 60.94% | ü | 2613.1795 | Center for Design Innovation | 106582 | 4.4442 | 65369 | 2.7258 | 38.67% | 41213 | 40841.285 | 1.703 | 61.68% | 65740.715 | Center for Design Innovation | 67775 | NA | 2.8261 | 44733 | NA | 1.8653 | 34% | 23042 | 8654.36 | NA | 0.36087 | 87.23% | Center for Design Innovation | 8727727 | 363.9282 | 6497174 | 700000 | 50000 |  | 80300 | 57.2842 | RMF | 90.1-2007
Jones Student Center - Renovation and Addition | In Progress | FSU | Cumberland | Jon Parsons | 11-09090-03A | 2013-06-28 | FI | 2013-06-10 | 2015-03-06 | Assembly/Dining/Offices | NA | 82961 |  | 2 | Jones Student Center - Renovation and Addition | 90.1-2007 | 3 | 14304 | 172.4184 | 11048 | 133.171 | 22.76% | 3256 | No data |  |  | Rest/café | 150 |  |  |  | Jones Student Center - Renovation and Addition | 215110 | 2.5929 | 143121 | 1.7252 | 33.47% | 71989 |  |  |  |  | Jones Student Center - Renovation and Addition | 4017684 | NA | 48.4286 | 3910346 | NA | 47.1348 | 2.672% | 107338 |  |  |  |  | Jones Student Center - Renovation and Addition | 17090447 | 206.0058 | 16915711 | 1536300 | 0 |  | 207560 | 5.3105 | Optima | 90.1-2007
Campus Police Facility | None | UNCSA | Forsyth | boydc@uncsa.edu | 08-07845-03A | 2012-04-05 | CD | 2013-05-30 | 2015-03-12 | Offices | NA | 9023 |  | 2 | Campus Police Facility | 90.1-2004 | 4 | 1171 | 129.7795 | 689 | 76.3604 | 41.16% | 482 | No data |  |  | Police Sta | 71 |  |  |  | Campus Police Facility | 18288 | 2.0268 | 12209 | 1.3531 | 33.24% | 6079 |  |  |  |  | Campus Police Facility | 289717 | NA | 32.1087 | 195438 | NA | 21.66 | 32.54% | 94279 |  |  |  |  | Campus Police Facility | 3059704 | 339.1005 |  | 292220 | none noted |  | 68561 |  | SWA | 90.1-2004
Central Storage Facility | None | UNCSA | Forsyth | boydc@uncsa.edu | 08-07844-03A | 2012-05-23 | CD | 2013-05-01 | 2015-03-25 | Warehouse/Storage | NA | 43637 |  | 2 | Central Storage Facility | 90.1-2007 | 4 | 1506 | 34.512 | 754 | 17.2789 | 49.93% | 752 | No data | [7 empty] | Central Storage Facility | 27891 | 0.63916 | 14976 | 0.34319 | 46.31% | 12915 |  |  |  |  | Central Storage Facility | 128138 | NA | 2.9365 | 58898 | NA | 1.3497 | 54.04% | 69240 |  |  |  |  | Central Storage Facility | 5260039 | 120.5408 | 1412707 | 596884 | 0 |  | 65343 |  |  | 90.1-2007
Talley Student Center Renovation and Addition | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07847-03A | 2012-02-22 | CD | 2011-02-21 | 2015-05-07 | Offices/Theater/Conference/Food Service/Book Store | NA | 294736 |  | 5 | Talley Student Center Renovation and Addition | 90.1-2004 | 4 | 41725 | 141.5674 | 27808 | 94.3488 | 33.35% | 13917 | 2016-09-01 | 43153.4378 | 146.4139 | Rest/café | 166 | -3.423% |  | -1428.4378 | Talley Student Center Renovation and Addition | 940212 | 3.19 | 699461 | 2.3732 | 25.61% | 240751 | 787073.6955 | 2.6704 | 16.29% | 153138.3045 | Talley Student Center Renovation and Addition | 1088442 | NA | 3.6929 | 869385 | NA | 2.9497 | 20.13% | 219057 | 5333250.8125 | NA | 18.095 | -390% | Talley Student Center Renovation and Addition | 89115690 | 302.3577 |  | 9079497 | 178918 |  | 526000 |  | SWA | 90.1-2004
CE and BLET | None | Nash CC | Nash |  | 09-07972-03A | 2012-11-19 | CD | 2013-11-05 | 2015-06-05 | Offices/Classrooms/Gym/Training | NA | 79295 |  | 2 | CE and BLET | 90.1-2007 | 4 | 5941 | 74.9228 | 4122 | 51.9831 | 30.62% | 1819 | 2016-09-01 | 5763.3437 | 72.6823 | Col/Univ | 62 | 2.99% |  | 177.6563 | CE and BLET | 95436 | 1.2036 | 64835 | 0.81764 | 32.06% | 30601 | 114944.21 | 1.4496 | -20.44% | -19508.21 | CE and BLET | 2356578 | NA | 29.7191 | 1527392 | NA | 19.2621 | 35.19% | 829186 | 950708 | NA | 11.9895 | 59.66% | CE and BLET | 11310270 | 142.6353 |  | 861998 | None Noted |  | 52620 |  | SWA | 90.1-2007
Film School Production Design Facility | None | UNCSA | Forsyth | boydc@uncsa.edu | 08-08115-03A | 2012-03-30 | CD | 2013-04-11 | 2015-06-16 | Various | NA | 29936 |  | 2 | Film School Production Design Facility | 90.1-2004 | 4 | 8887 | 296.8666 | 5860 | 195.7509 | 34.06% | 3027 | No data |  |  | Lab | 194 |  |  |  | Film School Production Design Facility | 148285 | 4.9534 | 99346 | 3.3186 | 33% | 48939 |  |  |  |  | Film School Production Design Facility | 55005 | NA | 1.8374 | 40257 | NA | 1.3448 | 26.81% | 14748 |  |  |  |  | Film School Production Design Facility | 7820696 | 261.2472 |  | 827850 | none noted |  | 47760 |  |  | 90.1-2004
Holshouser Residence Hall Renovation | None | UNCC | Mecklenburg | Tony Schallert | 12-09461-02A | 2014-03-17 | FD | 2014-02-06 | 2015-07-28 | Residence Hall | 400 | 99713 | 249.2825 | 12 | Holshouser Residence Hall Renovation | 90.1-2007 | 3 | 12163 | 121.9801 | 9302 | 93.2877 | 23.52% | 2861 | No data |  |  | Dorm | 47 |  |  |  | Holshouser Residence Hall Renovation | 169440 | 1.6993 | 126115 | 1.2648 | 25.57% | 43325 |  |  |  |  | Holshouser Residence Hall Renovation | 3663471 | 9158.6775 | 36.7402 | 2570153 | 6425.3825 | 25.7755 | 29.84% | 1093318 |  |  |  |  | Holshouser Residence Hall Renovation | 15172636 | 152.1631 | 14796933 | 1251550 | 11880 |  | 95000 | 11.1387 | CN | 90.1-2007 | 375703
Laurel Residence Hall | None | UNCC | Mecklenburg | Tony Schallert | 12-09496-03A | 2013-10-11 | DD-2 | 2014-01-02 | 2015-07-29 | Residence Hall | 412 | 143986 | 349.4806 | 6 | Laurel Residence Hall | 90.1-2007 | 3 | 7705 | 53.5121 | 5840 | 40.5595 | 24.21% | 1865 | No data |  |  | Dorm | 47 |  |  |  | Laurel Residence Hall | 102473 | 0.71169 | 56750 | 0.39414 | 44.62% | 45723 |  |  |  |  | Laurel Residence Hall | 4730466 | 11481.7136 | 32.8537 | 2731460 | 6629.7573 | 18.9703 | 42.26% | 1999006 |  |  |  |  | Laurel Residence Hall | 28765101 | 199.7771 | 26520850 | 2312090 | 13945 |  | 200000 | 53.7628 | Optima | 90.1-2007
Belk Residence Hall Renovation | Silver | ASU | Watauga | Jerry Marshall | 10-09113-02A | 2014-02-21 | FD-2 | 2014-05-05 | 2015-07-30 | Residence Hall | 176 | 32839 | 186.5852 | 5 | Belk Residence Hall Renovation | 90.1-2007 | 5 | 3330 | 101.4038 | 2305 | 70.1909 | 30.78% | 1025 | 2016-08-16 | 2998.182 | 91.2994 | Dorm | 47 | 9.965% | ü | 331.818 | Belk Residence Hall Renovation | 87029 | 2.6502 | 60703 | 1.8485 | 30.25% | 26326 | 70016.1 | 2.1321 | 19.55% | 17012.9 | Belk Residence Hall Renovation | 1209992 | 6874.9545 | 36.8462 | 755467 | 4292.4261 | 23.0052 | 37.56% | 454525 | 1103000 | 6267.0455 | 33.5881 | 8.842% | Belk Residence Hall Renovation | 7222300 | 219.9306 | 6512106 | 806400 | 50600 |  | 19450 | 29.6378 | CN | 90.1-2007
S & BS Building Renovation | None | UNCW | New Hanover | Steve Sharpe | 07-09975-02A | 2014-07-02 | CD | 2014-05-30 | 2015-08-03 | Offices, classrooms, labs | NA | 43554 |  | 2 | S & BS Building Renovation | 90.1-2010 | 3 | 5934.9 | 136.2653 | 5079 | 116.6139 | 14.42% | 855.9 | No data |  |  | Col/Univ | 62 |  |  |  | S & BS Building Renovation | 110349 | 2.5336 | 91957 | 2.1113 | 16.67% | 18392 |  |  |  |  | S & BS Building Renovation | 1075870 | NA | 24.702 | 760602 | NA | 17.4634 | 29.3% | 315268 |  |  |  |  | S & BS Building Renovation | 9820475 | 225.4781 | 5837018 | 859450 |  | 17250 | 0 | 217.5243 | MCBH | 90.1-2010
Gateway Residence Hall (Belk Replacement) | In Progress | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-09246-03A | 2013-10-03 | CD | 2013-05-22 | 2015-08-10 | Residence Hall | 720 | 208077 | 288.9958 | 5 | Gateway Residence Hall (Belk Replacement) | 90.1-2007 | 3 | 22829 | 109.7142 | 15444 | 74.2225 | 32.35% | 7385 | 2016-08-09 | 8654.0487 | 41.5906 | Dorm | 47 | 62.09% |  | 14174.9513 | Gateway Residence Hall (Belk Replacement) | 519318 | 2.4958 | 339219 | 1.6303 | 34.68% | 180099 | 222500.0794 | 1.0693 | 57.16% | 296817.9206 | Gateway Residence Hall (Belk Replacement) | 11970900 | 16626.25 | 57.5311 | 7250002 | 10069.4472 | 34.8429 | 39.44% | 4720898 | 5974020 | 8297.25 | 28.7106 | 50.1% | Gateway Residence Hall (Belk Replacement) | 48137413 | 231.3442 | 41707231 | 3917050 | 91100 |  | 322840 | 38.002 | SWA | 90.1-2007
Oak Residence Hall Renovation | None | UNCC | Mecklenburg | Tony Schallert | 12-09648-03A | 2014-01-06 | CD-2 | 2014-05-19 | 2015-08-24 | Residence Hall | 248 | 52844 | 213.0806 | 4 | Oak Residence Hall Renovation | 90.1-2007 | 3 | 4104 | 77.6626 | 2776 | 52.532 | 32.36% | 1328 | No data |  |  | Dorm | 47 |  |  |  | Oak Residence Hall Renovation | 78156 | 1.479 | 52863 | 1.0004 | 32.36% | 25293 |  |  |  |  | Oak Residence Hall Renovation | 3786332 | 15267.4677 | 71.6511 | 2951199 | 11899.996 | 55.8474 | 22.06% | 835133 |  |  |  |  | Oak Residence Hall Renovation | 7187260 | 136.009 | 5929373 | 591176 | 0 |  | 77500 | 52.7967 | Peterson | 90.1-2007
15.16 sums | [10 empty] | 8851 | 6548386 |  |  | 15.16 sums |  |  | 685034 |  | 461088.8 |  | 32.69% | 223945.2 | [8 empty] | 15.16 sums | 11588088 |  | 7810019 |  | 32.6% | 3778069 |  |  |  |  | 15.16 sums | [7 empty] | 48542961 |  | 73.5499 |  |  | 15.16 sums | 1293258021.39 |  |  | 126144177 | 3598752 |  | 9065583 | 1432066533.39
Holding Hall Renovation | In Progress | Wake TCC | Wake |  | 06-06753-02A | 2013-11-18 | CD | 2014-08-19 | 2015-12-21 | Offices/Classrooms | NA | 47729 |  | 1 | Holding Hall Renovation | 90.1-2007 | 4 | 2614 | 54.7675 | 1818 | 38.0901 | 30.45% | 796 |  |  |  | Col/Univ | 72 |  |  |  | Holding Hall Renovation | 52390 | 1.0977 | 33542 | 0.70276 | 35.98% | 18848 |  |  |  |  | Holding Hall Renovation | 1075022 | NA | 22.5235 | 817762 | NA | 17.1334 | 23.93% | 257260 |  |  |  |  | Holding Hall Renovation | 4947300 | 103.654 | 3327846 | 449750 | 41200 |  |  | 88.1077 | Dewberry | 90.1-2007
Rizzo Conference Center Phase III (Privately Funded) |  | UNC-CH | Orange |  | 11-08953-01A | 2012-09-04 | CD | Privately Funded | 2016-01-29 | Hotel/Classrooms/Conference | 66 | 97014 | 1469.9091 | 5 | Rizzo Conference Center Phase III (Privately Funded) | 90.1-2004 | 4 | 6933 | 71.4639 | 4473 | 46.1067 | 35.48% | 2460 | [8 empty] | Rizzo Conference Center Phase III (Privately Funded) | 14092 | 0.14526 | 10313 | 0.1063 | 26.82% | 3779 |  |  |  |  | Rizzo Conference Center Phase III (Privately Funded) | 2116678 | 32070.8788 | 21.8183 | 1698607 | 25736.4697 | 17.5089 | 19.75% | 418071 |  |  |  |  | Rizzo Conference Center Phase III (Privately Funded) | 25040939 | 258.1168 |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | 90.1-2004
Belk Gymnasium Renovation | None | UNCC | Mecklenburg | Tony Schallert | 12-09471-03A | 2013-10-18 | DD | 2014-05-05 | 2016-02-18 | Gym, Pool, Offices | NA | 105000 |  | 3 | Belk Gymnasium Renovation (Student Recreation Facility) | 90.1-2010 | 3 | 5893 | 56.1238 | 5553 | 52.8857 | 5.77% | 340 | [8 empty] | Belk Gymnasium Renovation (Student Recreation Facility) | 96234 | 0.91651 | 84246 | 0.80234 | 12.46% | 11988 |  |  |  |  | Belk Gymnasium Renovation (Student Recreation Facility) | 2939272 | NA | 27.9931 | 1888963 | NA | 17.9901 | 35.73% | 1050309 |  |  |  |  | Belk Gymnasium Renovation (Student Recreation Facility) | 14388687 | 137.0351 | 13744319 | 1224800 | 0 |  | 136650 | 65.15 | M&L | 90.1-2010
Winkler Residence Hall Renovation Demolished 06/01/14 |  | ASU |  | Jerry Marshall | 10-08894-03A | 2012-09-14 | CD | Demolished 06/01/14 | Demolished 06/01/14 | Residence Hall | 192 | 78450 |  | 12 | Winkler Residence Hall Renovation Demolished 06/01/14 | 90.1-2004 |  | 6070 | 77.3741 | 3601 | 45.9018 | 40.68% | 2469 | [8 empty] | Winkler Residence Hall Renovation Demolished 06/01/14 | 143502 | 1.8292 | 87933 | 1.1209 | 38.72% | 55569 |  |  |  |  | Winkler Residence Hall Renovation Demolished 06/01/14 | 2528379 | 13168.6406 | 32.2292 | 1493037 | 7776.2344 | 19.0317 | 40.95% | 1035342 |  |  |  |  | Winkler Residence Hall Renovation Demolished 06/01/14 | 11873469 | 151.3508 |  | 1313285 | 103000 |  | 92600 | 217.1907 |  | 90.1-2004
Bio-tech & Med Sim Center NOT SB 668 |  | Edgecombe CC |  |  | 05-06644-02A | 2014-04-09 | DD | Design Build / NOT SB 668 | Design Build / NOT SB 668 | Office/Classroom/Labs | NA | 44978 |  | 3 | Bio-tech & Med Sim Center NOT SB 668 | 90.1-2007 |  | 6871 | 152.7636 | 4929 | 109.5869 | 28.26% | 1942 | [8 empty] | Bio-tech & Med Sim Center NOT SB 668 | 134054 | 2.9804 | 98221 | 2.1838 | 26.73% | 35833 |  |  |  |  | Bio-tech & Med Sim Center NOT SB 668 |  | NA | 0 |  | NA | 0 |  | 0 |  |  |  |  | Bio-tech & Med Sim Center NOT SB 668 | 4825393 | 107.2834 | 4180000 | 932460 | 308832 |  | 28700 | 27.4307 |  | 90.1-2007
Student Recreation Center | In Progress | UNCG | Guilford | Douglas Cato | 09-07928-02A | 2014-03-17 | CD | 2014-03-06 | 2016-06-29 | Gym/Pool | NA | 213000 |  | 3 | Student Recreation Center | 90.1-2007 | 4 | 20211 | 94.8873 | 15288 | 71.7746 | 24.36% | 4923 | [8 empty] | Student Recreation Center | 275822 | 1.2949 | 188166 | 0.88341 | 31.78% | 87656 |  |  |  |  | Student Recreation Center | 2060500 | NA | 9.6737 | 1524900 | NA | 7.1592 | 25.99% | 535600 |  |  |  |  | Student Recreation Center (cost includes CUP?) | 69872746 | 328.0411 | 63588816 | 6427000 | 67200 |  | 344800 | 76.3887 | M&L | 90.1-2007
Reynolds Coliseum Renovation | In Progress | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 12-09912-01B | 2014-11-18 | CD | 2015-06-16 | 2016-09-01 | Basketball Arena, locker rooms, offices | NA | 165584 |  | 3 | Reynolds Coliseum Renovation | 90.1-2007 | 4 | 29857 | 180.3133 | 22062 | 133.2375 | 26.11% | 7795 | [8 empty] | Reynolds Coliseum Renovation | 534913 | 3.2305 | 426967 | 2.5786 | 20.18% | 107946 |  |  |  |  | Reynolds Coliseum Renovation | 330635 | NA | 1.9968 | 247594 | NA | 1.4953 | 25.12% | 83041 |  |  |  |  | Reynolds Coliseum Renovation | 23473863 | 141.7641 | 23473863 | 3170473 | 35000 | 60000 | 58725 | 1.4241 | BNK | 90.1-2007
Phase XIV Residence Hall | None | UNCC | Mecklenburg | Tony Schallert | 12-10117-03A | 2014-10-22 | CD | 2015-03-30 | 2016-10-28 | Residence Hall | 436 | 157219 | 360.594 | 6 | Phase XIV Residence Hall | 90.1-2007 | 3 | 8086 | 51.4314 | 6532 | 41.5471 | 19.22% | 1554 |  |  |  | Dorm | 47 |  |  |  | Phase XIV Residence Hall | 132669 | 0.84385 | 106400 | 0.67676 | 19.8% | 26269 |  |  |  |  | Phase XIV Residence Hall | 3855098 | 8841.9679 | 24.5206 | 2204228 | 5055.5688 | 14.0201 | 42.82% | 1650870 |  |  |  |  | Phase XIV Residence Hall | 38708442 | 246.2072 | 36840000 | 3018220 |  | 27500 | 164340 | 78.4302 | Optima | 90.1-2007
Western Crime Lab | None | NCDoJ | Henderson |  | 12-09454-02A | 2014-10-31 | CD-2 | 2015-07-30 | 2017-02-08 | Labs/Offices | NA | 35357 |  | 2 | Western Crime Lab | 90.1-2007 | 4 | 7819 | 221.1443 | 5695 | 161.0714 | 27.16% | 2124 |  |  |  | Lab | 194 |  |  |  | Western Crime Lab | 205920 | 5.824 | 145347 | 4.1108 | 29.42% | 60573 |  |  |  |  | Western Crime Lab | 142308 | NA | 4.0249 | 97350 | NA | 2.7533 | 31.59% | 44958 |  |  |  |  | Western Crime Lab | 14468100 | 409.2004 | 13630000 | 1440000 |  |  | 120000 | 15.8173 | M&C | 90.1-2007
Health Sciences Campus - Student Services Facility | In Progress | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-10217-02A | 2015-01-19 | CD | 2015-06-17 | 2017-02-15 | Offices/Gym/ Food Service/ Book Store | NA | 75843 |  | 4 | Health Sciences Campus - Student Services Facility | 90.1-2010 | 3 | 10944 | 144.2981 | 9185 | 121.1054 | 16.07% | 1759 | [8 empty] | Health Sciences Campus - Student Services Facility | 107685 | 1.4198 | 91262 | 1.2033 | 15.25% | 16423 |  |  |  |  | Health Sciences Campus - Student Services Facility | 1899740 | NA | 25.0483 | 1215180 | NA | 16.0223 | 36.03% | 684560 |  |  |  |  | Health Sciences Campus - Student Services Facility | 26731311 | 352.4559 | 21220000 | 2903738 | 154488 |  | 300000 | 363.2588 | RDK | 90.1-2004
New Student Center | In Progress | NCA&T | Guilford |  | 03-08608-02A | 2014-05-09 | CD | 2014-02-20 | 2017-02-27 | Offices/Theater/Conference/Food Service/Book Store | NA | 182275 |  | 4 | New Student Center | 90.1-2007 | 4 | 31691 | 173.8637 | 23425 | 128.5146 | 26.08% | 8266 |  |  |  | Rest/café | 166 |  |  |  | New Student Center | 529117 | 2.9029 | 366504 | 2.0107 | 30.73% | 162613 |  |  |  |  | New Student Center | 5763776 | NA | 31.6213 | 4434106 | NA | 24.3265 | 23.07% | 1329670 |  |  |  |  | New Student Center | 71806942 | 393.9484 | 64958142 | 7250000 | 166000 |  | 594000 | 46.7908 | RMF | 90.1-2007
Advanced + Emerging Technologies Center NOT SB 668 |  | CFCC |  |  | 11-08585-02A | 2013-07-19 | DD | 2015-07-07 | 2017-02-27 | Classrooms, labs, offices | NA | 94236 |  | 2 | Advanced + Emerging Technologies Center NOT SB 668 | 90.1-2007 | 3 | 6944 | 73.6873 | 6610 | 70.143 | 4.81% | 334 | [8 empty] | Advanced + Emerging Technologies Center NOT SB 668 | 249013 | 2.6424 | 222050 | 2.3563 | 10.83% | 26963 |  |  |  |  | Advanced + Emerging Technologies Center NOT SB 668 | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. |  |  |  |  | Advanced + Emerging Technologies Center NOT SB 668 | 31280403 | 197.2556 | 3432421 | 2079762 | 0 |  | 0 |  |  | 90.1-2007
Brown Building Renovation & Addition | In Progress | WCU |  |  | 13-10964-02A | 2015-09-04 | CD | 2015-11-30 | 2017-04-29 | Food Service/Dining | NA | 64342 |  | 3 | Brown Building Renovation & Addition | 90.1-2010 | 4 | 9679 | 150.4305 | 9209 | 143.1258 | 4.856% | 470 |  |  |  | Rest/Cafet | 166 |  |  |  | Brown Building Renovation & Addition | 137469 | 2.1365 | 123584 | 1.9207 | 10.1% | 13885 |  |  |  |  | Brown Building Renovation & Addition | 649069 | NA | 10.0878 | 492976 | NA | 7.6618 | 24.05% | 156093 |  |  |  |  | Brown Building Renovation & Addition | 21056907 | 327.2653 | 20955798 | 2504600 | 62800 | 17574 | 139652 | 23.1282 | Optima | 90.1-2010
Advanced Applied Technology Center | In Progress | Alamance CC |  |  | 07-07353-03A | 2015-12-18 | CD | 2016-05-02 | 2017-07-31 | Shops/Offices | NA | 55099 |  | 1 | Advanced Applied Technology Center | 90.1-2010 | 4 | 5015 | 91.018 | 4773 | 86.6259 | 4.826% | 242 |  |  |  | Col/Univ | 72 |  |  |  | Advanced Applied Technology Center | 128985 | 2.341 | 124246 | 2.255 | 3.674% | 4739 |  |  |  |  | Advanced Applied Technology Center | 152441 | NA | 2.7667 | 85722 | NA | 1.5558 | 43.77% | 66719 |  |  |  |  | Advanced Applied Technology Center | 13631526 | 247.4006 | 13659954 | 861500 | 43500 | 0 | 153000 | 35.4657 | Little | 90.1-2010
New Residence Hall - Freshman Living/Learning |  | WSSU | Forsyth | Dick Kabis | 13-10372-03A | 2014-10-20 | CD | Creating Contract | 2017-09-01 | Residence Hall | 290 | 71021 | 244.9 | 6 | New Residence Hall - Freshman Living/Learning | 90.1-2010 | 4 | 3347 | 47.1269 | 3202 | 45.0853 | 4.332% | 145 |  |  |  | Dorm | 58 |  |  |  | New Residence Hall - Freshman Living/Learning | 54763 | 0.77108 | 50499 | 0.71104 | 7.786% | 4264 |  |  |  |  | New Residence Hall - Freshman Living/Learning | 2798472 | 9649.9034 | 39.4034 | 2000107 | 6896.9207 | 28.1622 | 28.53% | 798365 |  |  |  |  | New Residence Hall - Freshman Living/Learning | 17750570 | 249.9341 | 16000000 | 1735188 | 75000 | 11000 | 176132 | 472.022 | RMF | 90.1-2010
Heavy Equipment + Transport Technology Center NOT SB 668 |  | CFCC |  |  | 11-08585-02A |  | DD | 2015-07-07 | 2017-10-05 | Equipment repair, offices, classrooms | NA | 32221 |  | 2 | Heavy Equipment + Transport Technology Center NOT SB 668 | 90.1-2007 | 3 | [14 empty] | Heavy Equipment + Transport Technology Center NOT SB 668 | 28938 | 0.89811 | 22854 | 0.70929 | 21.02% | 6084 |  |  |  |  | Heavy Equipment + Transport Technology Center NOT SB 668 | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. |  |  |  |  | Heavy Equipment + Transport Technology Center NOT SB 668 | included in AET Center bid amount |  | 2041899 | Included w/A+ETC | 0 |  | NOT SB 668 |  |  | 90.1-2007
Main Campus - Student Union | In Progress | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-09263-02A | 2015-07-20 | CD | 2015-12-18 | 2018-03-18 | Offices/Theater/Conference/ Food Service/ Book Store | NA | 213911 |  | 4 | Main Campus - Student Union | 90.1-2007 | 3 | 38581 | 180.3601 | 23447 | 109.611 | 39.23% | 15134 | [8 empty] | Main Campus - Student Union | 629463 | 2.9426 | 393838 | 1.8411 | 37.43% | 235625 |  |  |  |  | Main Campus - Student Union | 1394940 | NA | 6.5211 | 863295 | NA | 4.0358 | 38.11% | 531645 |  |  |  |  | Main Campus - Student Union | 95491076 | 446.4056 | 93491076 | 9640712 | 161300 |  | 707030 | 12.1733 | AEI | 90.1-2007
Mary Ellen Jones Renovation | In Progress | UNC | Orange |  | 11-09861-02A and 11-09861-02C | 2015-02-09 | DD-2 | 2016-01-04 | 2018-07-04 | Labs/Offices | NA | 221618 |  | 11 | Mary Ellen Jones Renovation | 90.1-2010 | 4 | 27375.8 | 123.527 | 22956.3 | 103.585 | 16.14% | 4419.5 |  |  |  | Lab | 194 |  |  |  | Mary Ellen Jones Renovation | 1006324 | 4.5408 | 813664 | 3.6715 | 19.14% | 192660 |  |  |  |  | Mary Ellen Jones Renovation | 663675 | NA | 2.9947 | 445591 | NA | 2.0106 | 32.86% | 218084 |  |  |  |  | Mary Ellen Jones Renovation | 84957809 | 383.3525 | 75208000 | 8628179 |  | 10370 | 730000 | 54.4492 | Newcomb & Boyd | 90.1-2007
Division 2 Equipment Shop | None | DOT |  | Eric Frazier | 12-09859-03A | 2016-05-04 | FD | No Contract | No Contract | Repair garage/storage/offices | NA | 36215 |  | 1 | Division 2 Equipment Shop | 90.1-2010 | 3 | 4215 | 116.3882 | 3907 | 107.8835 | 7.307% | 308 |  |  |  |  | 32 |  |  |  | Division 2 Equipment Shop | 66838 | 1.8456 | 33837 | 0.93434 | 49.37% | 33001 |  |  |  |  | Division 2 Equipment Shop | 252297 | NA | 6.9666 | 187574 | NA | 5.1795 | 25.65% | 64723 |  |  |  |  | Division 2 Equipment Shop | 6807340.17 | 187.9702 | 6767100.17 | 539733 | 12290 | 8000 | 37090 | 2.9581 | Dibble and Pledger | 90.1-2010
Sarah & Edward Smith Health Sciences Center | In Progress | Davidson CCC |  |  | 07-07386-02A | 2016-08-04 | FD-2 | No Contract | No Contract | Classrooms/Offices/Labs | NA | 48794 |  | 3 | Health Sciences Center | 90.1-2010 | 3 | 2713 | 55.6011 | 1981 | 40.5993 | 26.98% | 732 | [8 empty] | Health Sciences Center | 66149 | 1.3557 | 48211 | 0.98805 | 27.12% | 17938 |  |  |  |  | Health Sciences Center | 854321 | NA | 17.5087 | 540545 | NA | 11.0781 | 36.73% | 313776 |  |  |  |  | Health Sciences Center | 8963897 | 183.709 | 8685925 | 811900 | 32900 | 23500 | 98750 | 24.1455 | Little | 90.1-2010
Allied Health & Workforce (Courtesy review only of DD phase) |  | ABTCC |  |  | 12-09487-01A | 2012-11-13 | DD | No Contract | No Contract (Creating) | Office/Classroom/Lab/Assembly | NA | 185810 | #VALUE! | 6 | Allied Health & Workforce | 90.1-2004 |  | 10582 | 56.9506 | 3675 | 19.7783 | 65.27% | 6907 | [8 empty] | Allied Health & Workforce | 267259 | 1.4383 | 93214 | 0.50166 | 65.12% | 174045 |  |  |  |  | Allied Health & Workforce | 115375 | NA | 0.62093 | 50944 | NA | 0.27417 | 55.84% | 64431 |  |  |  |  | Allied Health & Workforce | 45400738 | 244.3396 | 42736000 | no contract |  |  |  | 15.3106 |  | 90.1-2004
Building 600 NOT SB 668 |  | RCCC |  |  | 11-08937-02A | 2013-01-25 | DD | No Contract | No Contract (Creating) | Classroom, offices | NA | 69250 | #VALUE! | 2 | Building 600 NOT SB 668 | 90.1-2004 |  | 4413 | 63.7256 | 2774 | 40.0578 | 37.14% | 1639 | [8 empty] | Building 600 NOT SB 668 | 82649 | 1.1935 | 58907 | 0.85064 | 28.73% | 23742 |  |  |  |  | Building 600 NOT SB 668 | 60744 | NA | 0.87717 | 45643 | NA | 0.6591 | 24.86% | 15101 |  |  |  |  | Building 600 NOT SB 668 | 10191099 | 147.1639 | 8586550 | Included w/ Bldgs 300 and 500. | 0 |  | 0 | 67.5827 |  | 90.1-2004
Scott Residence Hall Renovation | None | UNCC |  |  | 14-11473-01A | 2016-02-01 | SD | No Contract | No Contract | Residence Hall | 402 | 102000 | 253.7313 | 12 | Scott Residence Hall Renovation | 90.1-2007 | 3 | 10312 | 101.098 | 5939 | 58.2255 | 42.41% | 4373 |  |  |  | Dorm | 47 |  |  |  | Scott Residence Hall Renovation | 121370 | 1.1899 | 70653 | 0.69268 | 41.79% | 50717 |  |  |  |  | Scott Residence Hall Renovation | 9851029 | 24505.0473 | 96.5787 | 7633770 | 18989.4776 | 74.8409 | 22.51% | 2217259 |  |  |  |  | Scott Residence Hall Renovation | 14506733 | 142.2229 | 14196000 | 1485000 |  | 12000 | 108800.4975 | 8.5087 | KSQ | 90.1-2007
Elm Residence Hall Renovation | None | UNCC | Mecklenburg | Tony Schallert | 12-09940-03A | 2015-09-25 | CD | 2016-04-26 | No Contract (Creating) | Residence Hall | 95 | 29845 | 314.1579 | 3 | Elm Residence Hall Renovation | 90.1-2007 | 3 | 2122 | 71.1007 | 1669 | 55.9223 | 21.35% | 453 |  |  |  | Dorm | 47 |  |  |  | Elm Residence Hall Renovation | 34775 | 1.1652 | 26751 | 0.89633 | 23.07% | 8024 |  |  |  |  | Elm Residence Hall Renovation | 1044184 | 10991.4105 | 34.9869 | 677227 | 7128.7053 | 22.6915 | 35.14% | 366957 |  |  |  |  | Elm Residence Hall Renovation | 5379480 | 180.2473 | 5158196.28 | 448389 |  | 3312 | 23400 | 30.9067 | Peterson | 90.1-2007
Maple Residence Hall Renovation | None | UNCC | Mecklenburg | Tony Schallert | 12-09940-03A | 2015-09-25 | CD | 2016-04-26 | No Contract (Creating) | Residence Hall | 64 | 23270 | 363.5938 | 3 | Maple Residence Hall Renovation | 90.1-2007 | 3 | 1704 | 73.2273 | 1196 | 51.3966 | 29.81% | 508 |  |  |  | Dorm | 47 |  |  |  | Maple Residence Hall Renovation | 28673 | 1.2322 | 19427 | 0.83485 | 32.25% | 9246 |  |  |  |  | Maple Residence Hall Renovation | 692800 | 10825 | 29.7722 | 449405 | 7021.9531 | 19.3126 | 35.13% | 243395 |  |  |  |  | Maple Residence Hall Renovation | 4184040 | 179.804 | 4011930.44 | 348747 |  | 2576 | 18200 | 20.8615 | Peterson | 90.1-2007
Pine Residence Hall Renovation | None | UNCC | Mecklenburg | Tony Schallert | 12-09940-03A | 2015-09-25 | CD | 2016-04-26 | No Contract (Creating) | Residence Hall | 95 | 29799 | 313.6737 | 3 | Pine Residence Hall Renovation | 90.1-2007 | 3 | 2122 | 71.2104 | 1669 | 56.0086 | 21.35% | 453 |  |  |  | Dorm | 47 |  |  |  | Pine Residence Hall Renovation | 34775 | 1.167 | 26751 | 0.89771 | 23.07% | 8024 |  |  |  |  | Pine Residence Hall Renovation | 1044184 | 10991.4105 | 35.0409 | 677227 | 7128.7053 | 22.7265 | 35.14% | 366957 |  |  |  |  | Pine Residence Hall Renovation | 5379480 | 180.5255 | 5158196.28 | 448389 |  | 3312 | 23400 | 30.9067 | Peterson | 90.1-2007
Clement Residence Hall Renovation | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-10689-02A | 2016-05-18 | CD | 2016-03-04 | No Contract (Creating) | Residence Hall | 395 | 83462 | 211.2962 | 10 | Clement Residence Hall Renovation | 90.1-2010 | 3 | 5199 | 62.2918 | 5139 | 61.5729 | 1.154% | 60 |  |  |  | Dorm | 47 |  |  |  | Clement Residence Hall Renovation | 123606 | 1.481 | 119683 | 1.434 | 3.174% | 3923 |  |  |  |  | Clement Residence Hall Renovation | 2958825 | 7490.6962 | 35.4512 | 1891131 | 4787.6734 | 22.6586 | 36.09% | 1067694 |  |  |  |  | Clement Residence Hall Renovation | 17178395 | 205.8229 | 17047276 | 1750000 |  | 23400 | 89500 | 62.2021 | EDi | 90.1-2010
Workforce Solutions Complex | In Progress | Catawba Valley CC | Catawba |  | 07-07389-02A | 2015-06-09 | DD | No Contract | Project on Hold | Classrooms/Ofices/Lab&Shop/conf training/etc | NA | 80200 |  | 1 | Workforce Solutions Complex | 90.1-2010 | 4 | 6020 | 75.0623 | 5167 | 64.4264 | 14.17% | 853 |  |  |  |  | 72 |  |  |  | Workforce Solutions Complex | 88975 | 1.1094 | 79804 | 0.99506 | 10.31% | 9171 |  |  |  |  | Workforce Solutions Complex | 935004 | NA | 11.6584 | 509544 | NA | 6.3534 | 45.5% | 425460 |  |  |  |  | Workforce Solutions Complex | 20979000 | 261.5835 | 20407437 | 1928500 | 53000 |  | 45670 | 73.0818 | M&L | 90.1-2004
Student Housing Phase III |  | UNC | Orange |  | 12-09765-02A | 2015-01-14 | DD | Project on Hold | Project on Hold | Residence Hall and Offices | 275 | 112886 | 410.4945 | 7 | Student Housing Phase III | 90.1-2010 | 4 | 9032 | 80.0099 | 7916 | 70.1238 | 12.36% | 1116 |  |  |  | Dorm | 58 |  |  |  | Student Housing Phase III | 219320 | 1.9428 | 186485 | 1.652 | 14.97% | 32835 |  |  |  |  | Student Housing Phase III | 917871 | 3337.7127 | 8.131 | 584333 | 2124.8473 | 5.1763 | 36.34% | 333538 |  |  |  |  | Student Housing Phase III | 26052469 | 230.7857 | 25799369 | 1961668 | 53300 | 31970 | 250000 | 17.919 | CN | 90.1-2010
Sanford Residence Hall Renovation |  | UNCC | Mecklenburg | Tony Schallert | 12-09978-03A | 2014-07-09 | DD | No Contract | Project on Hold | Residence Hall | 440 | 99436 | 225.9909 | 12 | Sanford Residence Hall Renovation | 90.1-2010 | 3 | 5384 | 54.1454 | 4674 | 47.0051 | 13.19% | 710 |  |  |  | Dorm | 47 |  |  |  | Sanford Residence Hall Renovation | 58913 | 0.59247 | 50839 | 0.51127 | 13.7% | 8074 |  |  |  |  | Sanford Residence Hall Renovation | 4280271 | 9727.8886 | 43.0455 | 2887348 | 6562.1545 | 29.0373 | 32.54% | 1392923 |  |  |  |  | Sanford Residence Hall Renovation | 15688400 | 157.7738 | 15615290 | 1287470 |  | 4100 | 100000 | 21.9482 | M&L | 90.1-2010 | 73110
Collaborative Science Building |  | UNC | Orange |  | 11-09030-02A | 2013-11-01 | DD | No Contract | Project on Hold | Labs/Offices | NA | 274810 |  | 9 | Collaborative Science Building | 90.1-2007 | 4 | 15342 | 55.8277 | 11509 | 41.8798 | 24.98% | 3833 | [8 empty] | Collaborative Science Building | 293091 | 1.0665 | 229379 | 0.83468 | 21.74% | 63712 |  |  |  |  | Collaborative Science Building | 1871354 | NA | 6.8096 | 1339798 | NA | 4.8754 | 28.4% | 531556 |  |  |  |  | Collaborative Science Building | 72817169 | 264.9728 | 78341076 | 7995000 | 223000 | 65350 | 500000 | -74.3276 | Atelier Ten | 90.1-2007
Science and Office Bldg | In Progress | WSSU | Forsyth | Dick Kabis | 07-07236-01A | 2013-04-01 | CD | Approved to bid 11/04/2013 | Project on Hold | Classroom/Lab/Offices | NA | 123275 |  | 6 | Science and Office Bldg | 90.1-2004 | 4 | 23068 | 187.1263 | 15903 | 129.0043 | 31.06% | 7165 | [8 empty] | Science and Office Bldg | 425425 | 3.451 | 296267 | 2.4033 | 30.36% | 129158 |  |  |  |  | Science and Office Bldg | 1377837 | NA | 11.1769 | 878485 | NA | 7.1262 | 36.24% | 499352 |  |  |  |  | Science and Office Bldg | 42881459 | 347.852 | 39331912 | 4603210 | 138000 |  | 455967 | 32.081 | AEI | 90.1-2004
Highway Patrol Training Facility |  | DOA | Wake |  | 10-08389-02A | 2012-06-28 | CD | Project on Hold | Project on Hold | Office/Classroom/Training | NA | 34386 |  | 2 | Highway Patrol Training Facility | 90.1-2004 | 4 | 2484 | 72.2387 | 1436 | 41.7612 | 42.19% | 1048 | [8 empty] | Highway Patrol Training Facility | 59882 | 1.7415 | 41042 | 1.1936 | 31.46% | 18840 |  |  |  |  | Highway Patrol Training Facility | 667359 | NA | 19.4079 | 310095 | NA | 9.0181 | 53.53% | 357264 |  |  |  |  | Highway Patrol Training Facility | 6245727 | 181.6358 | 5604454 | is for multiple buildings | is for multiple buildings |  | 84000 |  |  | 90.1-2004
School of Aviation |  | ECSU | Pasquotank | Elizabeth Linney | 07-07166-02A | 2011-01-24 | CD | Project on Hold | Project on Hold | Office/Classroom/Hangar | NA | 44000 |  | 1 | School of Aviation | 90.1-2004 | 3 | 1913 | 43.4773 | 1115 | 25.3409 | 41.71% | 798 | [8 empty] | School of Aviation | 118819 | 2.7004 | 67443 | 1.5328 | 43.24% | 51376 |  |  |  |  | School of Aviation | 179563 | NA | 4.081 | 121788 | NA | 2.7679 | 32.18% | 57775 |  |  |  |  | School of Aviation | [9 empty] | 90.1-2004
Locomotive and Railcar Maint. Facility |  | DOT | Mecklenburg |  | 10-08634-03A | 2011-10-20 | SD | Project on Hold | Project on Hold | Offices & Railcar | NA | 68400 |  | 1 | Locomotive and Railcar Maint. Facility | 90.1-2004 | 3 | 23291 | 340.5117 | 8015 | 117.1784 | 65.59% | 15276 | [8 empty] | Locomotive and Railcar Maint. Facility | 210152 | 3.0724 | 107570 | 1.5727 | 48.81% | 102582 |  |  |  |  | Locomotive and Railcar Maint. Facility | [12 empty] | Locomotive and Railcar Maint. Facility | [9 empty] | 90.1-2004
Basic Skills Building |  | Robeson CC | Robeson |  | 07-07572-01A | 2010-12-22 | AP/SD | Project on Hold | Project on Hold | Office/Classroom | NA | 34271 |  | 2 | Basic Skills Building | 90.1-2004 | 3 | 2178 | 63.5523 | 1492 | 43.5354 | 31.5% | 686 | [8 empty] | Basic Skills Building | 51338 | 1.498 | 36026 | 1.0512 | 29.83% | 15312 |  |  |  |  | Basic Skills Building |  | NA | 0 |  | NA | 0 |  | 0 |  |  |  |  | Basic Skills Building | [9 empty] | 90.1-2004
Multipurpose Bldg |  | South Piedmont CC |  |  | 07-07352-03A | 2010-07-23 | CD | Approved to bid 05/15/2011 | Project on Hold | Office/Classroom/Labs | NA | 75000 |  | 3 | Multipurpose Bldg | 90.1-2004 | 4 | 5827 | 77.6933 | 3550 | 47.3333 | 39.08% | 2277 | [8 empty] | Multipurpose Bldg | 135642 | 1.8086 | 87360 | 1.1648 | 35.6% | 48282 |  |  |  |  | Multipurpose Bldg | 587500 | NA | 7.8333 | 398125 | NA | 5.3083 | 32.23% | 189375 |  |  |  |  | Multipurpose Bldg | [9 empty] | 90.1-2004
Discovery Center Project - Reynolds East |  | NCSSM | Durham |  | 07-07313-04A | 2010-05-10 | CD | Final Not Approved 05/23/2011 | Project on Hold | Residence Hall / Classroom | 31 | 26000 | 838.7097 | 4 | Discovery Center Project - Reynolds East | 90.1-2004 | 4 | 1846 | 71 | 1121 | 43.1154 | 39.27% | 725 | [8 empty] | Discovery Center Project - Reynolds East | 30466 | 1.1718 | 19282 | 0.74162 | 36.71% | 11184 |  |  |  |  | Discovery Center Project - Reynolds East | 475929 | 15352.5484 | 18.305 | 337075 | 10873.3871 | 12.9644 | 29.18% | 138854 |  |  |  |  | Discovery Center Project - Reynolds East | [9 empty] | 90.1-2004
Note on AC3: Thagard, Leonard: No normalization factor or no table 7-3 multiplier.
Note on BH4: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on Z5: Thagard, Leonard: model was for addition and renovation. Meter is for entire building.
Note on AS5: Leonard Thagard: limited kitchen use and limited bathroom use. Number is extremely low.
Note on AV5: Leonard Thagard: limited kitchen and bathroom use. Number is low.
Note on BH5: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on T6: Leonard Thagard: highest residence hall baseline EUI to date.
Note on V6: Leonard Thagard: highest proposed EUI for residence halls.
Note on BH6: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on AE7: Leonard Thagard: five months of steam consumption is not included.
Note on AN7: Leonard Thagard: Does not include steam cost.
Note on BH7: Leonard Thagard: Calculated from original amount construction contract less increase noted in LCCA for envelope, plumb, chillers and lights.
Note on AE8: Leonard Thagard: five months of steam consumption is not included.
Note on AN8: Thagard, Leonard: Does not include steam cost.
Note on BA8: Thagard, Leonard: water consumption is much less than last year.
Note on BH8: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on BJ8: Leonard Thagard: SB 668 at $99800 and LEED at $73700
Note on BA10: Thagard, Leonard: shared water meter.
Note on BH10: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on M11: Leonard Thagard: size is for addition only
Note on S11: Leonard Thagard: energy use is for addition only
Note on Z11: Thagard, Leonard: metered energy usage is for entire building; addition, renovation and existing building
Note on AA11: Thagard, Leonard: EUI is for entire building.
Note on AN11: Thagard, Leonard: metered energy cost is for entire building, not just addition and renovation.
Note on AO11: Thagard, Leonard: $/sqft is for entire building.
Note on BA11: Thagard, Leonard: metered water consumption is for entire facility.
Note on BH11: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on BF13: Leonard Thagard: Includes RUP?
Note on BH13: Leonard Thagard: Does not include RUP?
Note on BJ13: Leonard Thagard: LEED fees of 180,000 plus design amend #1 for SB 668 for 41,084
Note on BA14: Thagard, Leonard: shared water meter.
Note on L17: Leonard Thagard: One model performed and applied to seven bldgs
Note on M17: Leonard Thagard: One model performed and applied to seven bldgs.
Note on S17: Leonard Thagard: One model performed and applied to seven bldgs
Note on AN17: Thagard, Leonard: Chilled water cost is not included.
Note on AQ17: Thagard, Leonard: Chilled water cost is not included.
Note on BF17: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BI17: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BJ17: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BL17: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L18: Leonard Thagard: One model performed and applied to seven bldgs
Note on M18: Leonard Thagard: One model performed and applied to seven bldgs.
Note on S18: Leonard Thagard: One model performed and applied to seven bldgs
Note on AN18: Thagard, Leonard: Chilled water cost is not included.
Note on AQ18: Thagard, Leonard: Chilled water cost is not included.
Note on BF18: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BI18: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BJ18: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BL18: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L19: Leonard Thagard: One model performed and applied to seven bldgs
Note on M19: Leonard Thagard: One model performed and applied to seven bldgs.
Note on S19: Leonard Thagard: One model performed and applied to seven bldgs
Note on AN19: Thagard, Leonard: Chilled water cost is not included.
Note on AQ19: Thagard, Leonard: Chilled water cost is not included.
Note on BF19: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BI19: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BJ19: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BL19: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L20: Leonard Thagard: One model performed and applied to seven bldgs
Note on M20: Leonard Thagard: One model performed and applied to seven bldgs.
Note on S20: Leonard Thagard: One model performed and applied to seven bldgs
Note on AN20: Thagard, Leonard: Chilled water cost is not included.
Note on AQ20: Thagard, Leonard: Chilled water cost is not included.
Note on BF20: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BI20: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BJ20: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BL20: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L21: Leonard Thagard: One model performed and applied to seven bldgs
Note on M21: Leonard Thagard: One model performed and applied to seven bldgs.
Note on S21: Leonard Thagard: One model performed and applied to seven bldgs
Note on AN21: Thagard, Leonard: Site lighting cost is included. Chilled water cost is not included.
Note on AQ21: Thagard, Leonard: Chilled water cost is not included.
Note on BF21: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BI21: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BJ21: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BL21: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L22: Leonard Thagard: One model performed and applied to seven bldgs
Note on M22: Leonard Thagard: One model performed and applied to seven bldgs.
Note on S22: Leonard Thagard: One model performed and applied to seven bldgs
Note on AN22: Thagard, Leonard: Chilled water costs are not included.
Note on AQ22: Thagard, Leonard: Chilled water cost is not included.
Note on BF22: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BI22: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BJ22: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BL22: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L23: Leonard Thagard: One model performed and applied to seven bldgs
Note on M23: Leonard Thagard: One model performed and applied to seven bldgs.
Note on S23: Leonard Thagard: One model performed and applied to seven bldgs
Note on Z23: Thagard, Leonard: Missing seven months of steam meter data. Largest building on the quad.
Note on AA23: Thagard, Leonard: Missing seven months of steam meter data. Largest building on the quad.
Note on AD23: Thagard, Leonard: Missing seven months of steam meter data. Largest building on the quad.
Note on AF23: Thagard, Leonard: Missing seven months of steam meter data. Largest building on the quad.
Note on AN23: Thagard, Leonard: Steam and chilled water costs are not included.
Note on AQ23: Thagard, Leonard: Steam and chilled water cost are not included.
Note on BF23: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BI23: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BJ23: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BL23: Leonard Thagard: Cx fee divided by 7 buildings.
Note on Z24: Thagard, Leonard: Missing January and February meter data. Meter Down.
Note on AE24: Thagard, Leonard: Missing Jan and Feb meter data.
Note on AN24: Thagard, Leonard: Missing Jan and Feb meter data.
Note on BJ26: Leonard Thagard: LEED services added as design amendment. Add to OTDF.
Note on Z27: Thagard, Leonard: No meter data.
Note on AA27: Thagard, Leonard: No meter data.
Note on AN27: Thagard, Leonard: No meter data.
Note on BI28: Leonard Thagard: Combined design fee for original building design and revised building design.
Note on BJ29: Leonard Thagard: SB 668 at 17520 and LEED at 139300
Note on Z30: Thagard, Leonard: No meter data.
Note on AA30: Thagard, Leonard: No meter data.
Note on AN30: Thagard, Leonard: No meter data.
Note on AN31: Thagard, Leonard: does not include chilled water cost.
Note on BA31: Thagard, Leonard: meter inoperable.
Note on Z32: Thagard, Leonard: does not include chilled water consumption
Note on AA32: Thagard, Leonard: does not include chilled water consumption
Note on AN32: Thagard, Leonard: does not include chilled water consumption
Note on BF33: Leonard Thagard: CMR bid packages, NCSU utility assessment, parking deck assessment, etc. make bid amount difficult to accurately calculate.
Note on BF35: Leonard Thagard: Amount is for entire football complex.
Note on BG35: Leonard Thagard: Error in calculation due to entire football complex in one bid package. Building was not broken out.
Note on BI35: Leonard Thagard: Fee includes design for complete football stadium complex.
Note on AD37: Thagard, Leonard: Energy model was for addition and renovation. Energy meter is for entire building.
Note on AP37: Thagard, Leonard: Energy model was for addition and renovation. Energy meter is for entire building.
Note on BF37: Leonard Thagard: Best guess from multiple bid packages. Will revisit later.
Note on BI37: Leonard Thagard: 27% of full design fee
Note on BF38: Leonard Thagard: 73 percent of bid package total for Plemmons and Summitt
Note on BI38: Leonard Thagard: 73 percent of full design fee.
Note on T39: Leonard Thagard: Baseline is high.
Note on V39: Leonard Thagard: Proposed is high.
Note on BH39: Leonard Thagard: Note in LCCA report: "*Initial Cost estimated to be 85% of Construction Budget."
Note on J40: Leonard Thagard: BO
Note on Z43: Leonard Thagard: Metered on square footage basis.
Note on AN43: Leonard Thagard: Metered on square footage basis for thermal utilities or steam and chilled water.
Note on BH44: Leonard Thagard: deduct for wall, roof, glaze, bid alt 3, plumb, daylighting, bid alt 1
Note on BF45: Leonard Thagard: Early site package plus building package.
Note on BH45: Leonard Thagard: Clark Nexsen analysis indicated baseline building cost more to build than the proposed building. Analysis not used here.
Note on BF47: Leonard Thagard: Early site plus site and building bid packages.
Note on N49: Thagard, Leonard: includes dining hall
Note on AB49: Thagard, Leonard: This building also contains a dining hall.
Note on BB49: Thagard, Leonard: building also contains a dining hall
Note on J53: Leonard Thagard: Best guess.
Note on Z53: Leonard Thagard: Thermal utiities are metered on a square foot basis not on usage.
Note on BF53: Leonard Thagard: Designer's LCCA estimate.
Note on BH53: Leonard Thagard: Designer's LCCA estimate.
Note on J54: Leonard Thagard: BO per Jerry Rogers' handwritten notes in file.
Note on BH54: Leonard Thagard: LCCA cost estimate for proposed building was $46,642,869 while baseline was $46,128,762 for a difference of 514,107 which was deducted from the bid amount to arrive at the baseline building estimate.
Note on BJ54: Leonard Thagard: LEED certification 110000 and article 15-1 fee 229250
Note on Z55: Thagard, Leonard: Does not include heating hot water consumption.
Note on AN55: Thagard, Leonard: does not include heating hot water cost. Does not include chilled water cost.
Note on BH58: Leonard Thagard: baseline calculated from bid amount less delta of $1,012,000 between proposed and baseline estimates by designer.
Note on BF60: Leonard Thagard: Early site plus building package.
Note on BH63: Leonard Thagard: baseline and proposed building cost estimates exceeded the bid amount. Costs to implement energy legislation are negative.
Note on BJ64: Leonard Thagard: Green Globes.
Note on BF68: Leonard Thagard: CMR bid packages and CO's through CO#10.
Note on BH68: Leonard Thagard: CD estimates for baseline and proposed buildings exceed CMR bids through CO #10. Baseline estimate is CMR contract amount through CO #10 less designer's delta between baseline and proposed buildings.
Note on Z69: Thagard, Leonard: partial meter data. Incomplete
Note on AA69: Thagard, Leonard: incomplete meter data
Note on AN69: Thagard, Leonard: partial meter data incomplete
Note on AY71: Leonard Thagard: includes kitchen load and cooling tower make up at 3,600,000 gall/yr.
Note on BF74: Leonard Thagard: Captures most but not all bid packages.
Note on BI74: Leonard Thagard: includes swing space, promotion support, bridge over RR tracks, etc.
Note on Z75: Thagard, Leonard: does not include electricity for the month of June, 2015.
Note on W78: Leonard Thagard: 27% improvement without plug and process loads.
Note on BJ78: Leonard Thagard: Green Globes
Note on M80: Leonard Thagard: GSF does not include tempered un-occupied attic space of ~22,000 SF.
Note on BF80: Leonard Thagard: Designer's proposed building estimate is $5,957,771. Early demo is not included. Contract may include CUP and distribution piping. Ear
Note on BH80: Leonard Thagard: does not include early demo, CEP, CEP distribution, etc.
Note on BL80: Leonard Thagard: There is no SCO contract for Cx.
Note on M81: Leonard Thagard: Listed now as two buildings East at 102,127 GSF and West at 105,950 GSF.
Note on Z81: Thagard, Leonard: does not include steam/consdenate meter data
Note on AN81: Thagard, Leonard: does not include steam/condensate meter data
Note on BA81: Thagard, Leonard: does not include Aug 15 and July 16 meter data
Note on AT82: Leonard Thagard: Includes cooling tower make up and large laundry load.
Note on I85: Leonard Thagard: Private funding. No state contract.
Note on J85: Thagard, Leonard: ?
Note on N85: Thagard, Leonard: include conference center meeting rooms.
Note on J86: Thagard, Leonard: BO. Working through punch list and natatorium.
Note on M86: Leonard Thagard: 131,341 includes pool deck and pool lobby in GSF. M&L estimate at 105,000 GSF.
Note on S86: Leonard Thagard: Includes plug and process loads. Pool equipment and HVAC are considered process loads.
Note on W86: Leonard Thagard: 6% less energy than A90.1-2010.
Note on BM86: Leonard Thagard: Not correct since base is A90.1-2010 instead of A90.1-2004. Also window and roof replacement not analyzed based on LCCA.
Note on BF88: Leonard Thagard: SB 668 bldg estimate from PDC. BCC DB GMP is $9,751,745
Note on BH88: Leonard Thagard: Proposed bldg estimate from PDC. BCC DB GMP is $9,751,745
Note on BJ88: Leonard Thagard: PDC estimate from HB 628 study.
Note on BL88: Leonard Thagard: PDC estimate for Cx.
Note on J89: Thagard, Leonard: BO
Note on M89: Leonard Thagard: GSF includes alternates for additional space and per email from Rebecca dated 12.19.13.
Note on S89: Leonard Thagard: Includes process loads.
Note on U89: Leonard Thagard: Inlcudes process loads.
Note on O90: Leonard Thagard: base=57,963 1st=70,579 mez=37,042 Need to verify GSF.
Note on W91: Leonard Thagard: 25% improvement w/o plug load
Note on AG91: Leonard Thagard: energy dollars include plug and process loads
Note on BH91: Leonard Thagard: baseline estimate from energy model report. Proposed estimate si $36,334,998 compared to CM estimate of
Note on BL92: Leonard Thagard: Current contract is for $22,000. $120,000 is commissioning reserve.
Note on BJ93: Thagard, Leonard: $154,488 for LEED Silver Certification
Note on S94: Leonard Thagard: Includes process load
Note on U94: Leonard Thagard: Includes process load.
Note on W94: Leonard Thagard: Savings are 46% with process load removed.
Note on AH94: Leonard Thagard: Includes process load.
Note on AJ94: Leonard Thagard: Includes process load.
Note on AS94: Leonard Thagard: Includes cooling tower consumption.
Note on AV94: Leonard Thagard: Includes cooling tower consumption that is reduced due to smaller cooling load.
Note on BH94: Leonard Thagard: Baseline whole building estimate from LCCA.
Note on BI94: Leonard Thagard: Includes fee for swing space and others.
Note on M95: Leonard Thagard: Base bid GSF. Alt Bid adds 4019 GSF.
Note on S95: Leonard Thagard: No updates for the DD submission.
Note on U95: Leonard Thagard: No updates for the DD submission.
Note on M96: Leonard Thagard: Building Area including overhang.
Note on BH96: Leonard Thagard: Proposed building reconciled CRM cost estimate less delta for base buillding from LCCA.
Note on BJ97: Leonard Thagard: LEED certification design & documentation for $35,000. LEED Registration for $8,500.
Note on J98: Thagard, Leonard: 520 contract days. Waiting on official NTP.
Note on S99: Leonard Thagard: No data provided with SD or DD submission.
Note on U99: Leonard Thagard: No data provided with SD or DD submission.
Note on BH100: Leonard Thagard: Delta between proposed and baseline is $2,000,000 per AEI LCCA.
Note on S101: Leonard Thagard: Plug and process has not been included.
Note on U101: Leonard Thagard: Plug and process has not been included.
Note on AI101: Leonard Thagard: Highest $/GSF to date.
Note on AK101: Leonard Thagard: Highest $/GSF to date.
Note on BL101: Leonard Thagard: $730,000 Cx reserve. Current Cx contract is $36,940.
Note on BH102: Leonard Thagard: LED Lighting at $40,240 selected on LCCA. No other alternates selected for energy savings. Envelope improvements were not shown to reduce energy consumption.
Note on BJ103: Leonard Thagard: Silver LEED Consulting & Certification.
Note on BK103: Leonard Thagard: 7500 for predicting energy and water use. 6000 for preliminary study for LEED Silver certification 10000 for potential energy and water conservation strategies.
Note on A104: Leonard Thagard: Courtsey review only of energy model and LCCA per Greg Driver & Joe Bace discussion (SCO Director & AB Tech Fac/Oper Director)
Note on V104: Leonard Thagard: second lowest proposed EUI, second only to a warehouse/storage facility.
Note on W104: Leonard Thagard: Highest percentage savings to date.
Note on BL106: Thagard, Leonard: estimated at .75% of proposed construction cost.
Note on BJ110: Leonard Thagard: Not LEED per meeting minutes 04.09.14.
Note on BH112: Leonard Thagard: from page 89 of the energy model lcca report.
Note on BI112: Leonard Thagard: contract not signed as of 09.02.14
Note on BJ112: Leonard Thagard: from design contract: $43,200 for model and $10,100 for LEED
Note on BL112: Leonard Thagard: Cx reserve of $250,000
Note on S113: Leonard Thagard: Includes plug and process
Note on BL114: Leonard Thagard: Cx reserve. Design only Cx is for $44,680.
Note on BI115: Leonard Thagard: complicated fee structure due to multiple increases in scope and square footage of project.
Note on BJ115: Leonard Thagard: complex due to multiple increases in scope and square footage

## 15.16 Meter Data
2015/2016 Meter Data Summary
1 | ASU - Cone Residence Hall Renovation | [16 empty] | ASU - Cone Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 85574.32 | 64583.12 | 90419.52 | 94077.84 | 56724 | 57251.68 | 55614.56 | 56960.72 | 68456.08 | 57964.48 | 68523.04 | 67612.88 |  |  |  | 823762.2401 | kwhs | 2811.5005 | MMbtu
| Steam (lbs) |  | 45881 | 66736 | 118456.4 | 211886.8 | 203544.8 | 191031.8 | 271115 | 274451.8 | 215223.6 | 182689.8 | 118456.4 | 75078 |  |  |  | 1974551.4 | lbs | 1974.5514 | MMbtu | 4786.0519 | MMbtu
| Water (gallons) |  | 52258 | 146625 | 200127 | 186747 | 161422 | 75000 | 146000 | 183000 | 135515 | 196342 | 105169 | 121026 |  |  |  | 1709231 | gallons | 1709231 | gallons
| Electricity Cost ($) |  | 7624.2295 | 5757.5883 | 8055.0809 | 8380.3984 | 5058.7196 | 5105.6409 | 4960.0661 | 4814.7908 | 5528.75 | 4683.6496 | 5534.148 | 5460.8274 |  |  |  | 70963.8897 |  | 70963.8897
| Steam Costs ($) |  | 963.6 | 1401.6 | 2487.84 | 4450.08 | 4274.88 | 4012.08 | 5694 | 5764.08 | 4520.16 | 3836.88 | 2487.84 | 1576.8 |  |  |  | 41469.84 |  | 41469.84
112433.7297
2 | UNCC - Prospector Hall Renovation Phase II | [16 empty] | UNCC - Prospector Hall Renovation Phase II
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 68670 | 73539 | 87810 | 96658.1 | 90305.9 | 85231 | 88739 | 83201 | 94822.2 | 93120 | 88476.7 | 82379.9 |  |  |  | 1032952.8 | kwhs | 3525.4679 | MMbtu
| Nat Gas (Therms) |  | 1044 | 1159 | 1776 | 1873 | 2255 | 2066 | 2594 | 3202 | 2402 | 1922 | 1608 | 788 |  |  |  | 22689 | therms | 2268.3583 | MMbtu
| Chilled Water (MMBtu) |  | 935 | 865 | 703 | 243 | 165 | 171 | 11 | 45 | 227 | 311 | 447 | 655 |  |  |  | 4778 | MMbtu | 4778 | MMbtu | 10571.8262 | MMbtu
| Water Usage (CF) |  | 8689 | 11420 | 16370 | 14780 | 11420 | 7375 | 8690 | 10980 | 10430 | 19410 | 6230 | 3760 |  |  |  | 129554 | CF | 969063.92 | gallons
| Electricity Cost ($) |  | 4584.4429 | 4911.7624 | 5868.6686 | 5906.6012 | 5080.9622 | 4799.2881 | 5024.4851 | 4857.9844 | 5581.3641 | 5343.6397 | 5181.2631 | 5320.456 |  |  |  | 62460.9178 |  | 62460.9178
| Nat Gas Costs ($) |  | 753.53 | 834.11 | 1233.44 | 1334.41 | 1590.89 | 1442.35 | 1770.16 | 2162.73 | 1627.88 | 1312.38 | 1121 | 562.26 |  |  |  | 15745.14 |  | 15745.14
| Chilled Water ($) |  | 6221.5035 | 4679.6377 | 3519.7932 | 1246.9226 | 554.6476 | 502.6282 | 51.1746 | 541.1947 | 2138.5115 | 1073.8311 | 1518.7688 | 2002.2446 |  |  |  | 24050.858 |  | 24050.858
102256.9158
3 | UNCC - Miltimore Residence Hall | [16 empty] | UNCC - Miltimore Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 181002 | 164911 | 153590 | 135645.7 | 141852.6 | 130677.7 | 133798 | 129641.4 | 161554 | 166720.5 | 116672.5 | 113155 |  |  |  | 1729220.4 | kwhs | 5901.8292 | MMbtu
| Nat Gas (Therms) |  | 2307 | 2201 | 2860 | 2962 | 4916 | 6029 | 8502 | 7404 | 6551 | 5382 | 3886 | 1952 |  |  |  | 54952 | therms | 5493.888 | MMbtu | 11395.7172 | MMbtu
| Water Usage (CF) |  | 68321 | 52430 | 84445 | 61521 | 45121 | 35543 | 59045 | 72881 | 49465 | 56214 | 36023 | 32652 |  |  |  | 653661 | CF | 4889384.28 | gallons
| Electricity Cost ($) |  | 12083.7824 | 11014.6134 | 10264.9904 | 8289.0628 | 7981.1806 | 7358.3547 | 7575.7677 | 7569.5713 | 9509.289 | 9567.1636 | 6832.4307 | 7308.0472 |  |  |  | 105354.2538 |  | 105354.2538
| Nat Gas Costs ($) |  | 1638.51 | 1564.24 | 2026 | 2097.47 | 3442.25 | 4166.87 | 5751.7 | 4972.02 | 4401.74 | 3635.34 | 2677.93 | 1360.31 |  |  |  | 37734.38 |  | 37734.38
143088.6338
4 | NCCU - Nursing Building | [16 empty] | NCCU - Nursing Building
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 108048 | 105904 | 95632 | 87664 | 64040 | 68928 | 69072 | 106000 | 131912 | 116648 | 53704 | 147744 |  |  | 1155296 | kwhs | 3943.0252 | MMbtu
| Steam (lbs) | No Data | [15 empty] | 0 | lbs | 0 | MMbtu
| Natural Gas (Therms) |  |  | 299 | 1048 | 1363 | 1305 | 1441 | 413 | 1758 | 1804 | 1243 | 1424 | 277 | 289 |  |  | 12664 | therms | 1266.0976 | MMbtu | 5209.1229 | MMbtu
| Water (gal) |  |  | 150658 | 189718 | 177482 | 150751 | 121168 | 114305 | 113391 | 312047 | 136449 | 35873 | 23436 | 36393 |  |  | 1561671 | gallons | 1561671 | gallons
| Electricity Cost ($) |  |  | 6720.85 | 6587.49 | 5948.55 | 5452.92 | 3983.45 | 4287.49 | 4296.45 | 6593.46 | 8205.25 | 7255.79 | 3340.52 | 9190.04 |  |  | 71862.26 |  | 71862.26
| Steam Costs ($) | No Data | [15 empty] | 0 |  | 0
| Natural Gas ( $) |  |  | 246.83 | 782.85 | 1002.29 | 945.52 | 977.62 | 305.32 | 1088.3 | 1115.43 | 794.14 | 932.98 | 208.18 | 216.39 |  |  | 8615.85 |  | 8615.85
80478.11
5 | NCCU - Chidley Residence Hall | [16 empty] | NCCU - Chidley Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 85846 | 75525 | 65435 | 63722 | 50560 | 44272 | 51578 | 67404 | 69770 | 75377 | 85576 | 101534 |  |  | 836599 | kwhs | 2855.3124 | MMbtu
| Steam (lbs) | No Data | [15 empty] | 0 | lbs | 0 | MMbtu
| Natural Gas (Therms) |  |  | 36 | 40 | 48 | 42 | 44 | 50 | 44 | 45 | 49 | 45 | 51 | 39 |  |  | 533 | therms | 53.2873 | MMbtu | 2908.5997 | Mmbtu
| Water (CF) |  |  | 13940 | 11790 | 5472 | 5359 | 7986 | 18983 | 3178 | 13821 | 20524 | 20347 | 30042 | 29190 |  |  | 180632 | CF | 1351127.36 | gallons
| Electricity Cost ($) |  |  | 5339.83 | 4697.84 | 4070.22 | 3963.67 | 3144.96 | 2753.83 | 3208.28 | 4192.7 | 4339.87 | 4688.64 | 5323.04 | 6315.67 |  |  | 52038.55 |  | 52038.55
| Steam Costs ($) | No Data | [15 empty] | 0 |  | 0
| Natural Gas ( $) |  |  | 46.19 | 49.24 | 55.33 | 50.47 | 49.86 | 53.7 | 47.53 | 48.18 | 51.03 | 49.5 | 53.61 | 45.4 |  |  | 600.04 |  | 600.04
52638.59
6 | UNC-CH - Loudermilk | [16 empty] | UNC-CH - Loudermilk
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 151445 | 168628 | 183405 | 162532 | 200968 | 168714 | 143137 | 187325 | 151869 | 161325 | 187114 | 157789 |  |  | 2024251 | kwhs | 6908.7687 | MMbtu
| Steam Usage (mlbs) |  |  | 676 | 558 | 557 | 498 | 478 | 524 | 1005 | 693 | 383 | 441 | 535 | 473 |  |  | 6821 | mlbs | 8144.274 | MMbtu
| Chilled water (ton-hrs) |  |  | 167354 | 155825 | 141384 | 38112 | 26509 | 34916 | 7 | 1984 | 22678 | 33930 | 80849 | 138870 |  |  | 842418 | ton-hrs | 10109.016 | MMbtu
| Natural Gas (therms) |  |  | 159 | 201 | 366 | 434 | 513 | 311 | 240 | 329 | 358 | 258 | 310 | 169 |  |  | 3648 | therms | 364.7129 | MMbtu | 25526.7716 | Mmbtu
| Water Usage (kgallons) |  |  | 391 | 328 | 372 | 261 | 161 | 134 | 161 | 176 | 190 | 202 | 155 | 152 |  |  | 2683 | kgallons | 2683000 | gallons
| Electricity Cost ($) |  |  | 9086.7 | 9864.74 | 11664.56 | 9946.96 | 9465.59 | 8520.06 | 9060.57 | 9628.51 | 9294.38 | 9372.98 | 8906.63 | 9498.9 |  |  | 114310.58 |  | 114310.58
| Steam Cost ($) |  |  | 7594.25 | 6268.63 | 6257.39 | 5594.58 | 5369.9 | 5886.67 | 11290.27 | 7785.23 | 4302.66 | 4954.24 | 6010.24 | 5202.91 |  |  | 76516.97 |  | 76516.97
| Chilled Water ($) |  |  | 16082.72 | 14974.78 | 13587 | 3662.56 | 2547.51 | 3355.43 | 0.67 | 190.66 | 2179.36 | 3260.67 | 7769.59 | 12706.61 |  |  | 80317.56 |  | 80317.56
| Natural Gas ($) |  |  | 103.76 | 131.17 | 521.9 | 618.32 | 704.68 | 411.34 | 305.94 | 402.56 | 438.04 | 322.76 | 396.3 | 108.02 |  |  | 4464.79 |  | 4464.79
271145.11
7 | DoAg&CS - Davis Event Center | [16 empty] | DoAg&CS - Davis Arena
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 41520 | 43760 | 43320 | 58920 | 42800 | 34560 | 29680 | 27280 | 43440 | 3900 | 41360 | 46600 |  |  |  | 457140 | kwhs | 1560.2188 | MMbtu
| Nat Gas (Therms) |  | 315 | 116 | 77 | 260 | 256 | 1382 | 2629 | 1370 | 5683 | 1508 | 1463 | 533 |  |  |  | 15592 | therms | 1558.8277 | MMbtu | 3119.0466 | Mmbtu
| Water Usage (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) |  | 4459.02 | 4658.28 | 4596.15 | 5791.06 | 4348.2 | 3926.63 | 3285.66 | 3175.9 | 4419.01 | 4245.91 | 4427 | 4966.67 |  |  |  | 52299.49 |  | 52299.49
| Nat Gas Costs ($) |  | 143.98 | 100.21 | 72.4 | 202.82 | 191.27 | 878.2 | 1607.87 | 803.64 | 3151.46 | 885.69 | 894.51 | 278.03 |  |  |  | 9210.08 |  | 9210.08
61509.57
8 | NCSU - Student Health Center Addition and Renovation | [16 empty] | NCSU - Student Health Center Addition and Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electric (kWh) |  |  | 68624 | 67811 | 62411 | 53655 | 52772 | 55746 | 54644 | 57649 | 55716 | 55280 | 57553 | 53503 |  |  | 695364 | kwhs | 2373.2773 | MMbtu
| Chilled Water (Dtherms) |  |  | 801.25 | 669.8 | 226.01 | 128.13 | 144.41 | 24.11 | 49.41 | 185.8 | 224.7 | 345.7 | 580.5 | 617 |  |  | 3996.82 | dthrms | 3996.82 | MMbtu
| Steam (1,000 lbs) |  |  | 295 | 304 | 355 | 316 | 314 | 433 | 365 | 305 | 287 | 241 | 78 | 373 |  |  | 3666 | 1000 lbs | 3666 | MMbtu | 10036.0973 | Mmbtu
| Water (CCF) |  |  | 50.0949 | 48.5713 | 50.2727 | 49.5519 | 39.9971 | 41.561 | 48 | 55.7 | 62 | 48 | 38 | 40.4396 |  |  | 572.1887 | CCF | 427997.122 | gallons
| Electricity Cost ($) |  |  | 5901.664 | 5831.746 | 5367.346 | 4614.33 | 4538.392 | 4794.156 | 4699.384 | 4957.814 | 4791.576 | 4754.08 | 4949.558 | 4654.761 |  |  | 59854.807 |  | 59854.807
| Chilled Water Cost ($) |  |  | 11193.4625 | 9357.106 | 3157.3597 | 1789.9761 | 2017.4077 | 336.8167 | 690.2577 | 2595.626 | 3139.059 | 4829.429 | 8109.585 | 7990.15 |  |  | 55206.2354 |  | 55206.2354
| Steam Cost ($) |  |  | 3950.05 | 4070.56 | 4753.45 | 4231.24 | 4204.46 | 5797.87 | 4887.35 | 4083.95 | 3842.93 | 3226.99 | 1044.42 | 4483.46 |  |  | 48576.73 |  | 48576.73
163637.7724
9 | ECSU - Gilchrist Ed & Psych Bldg | [16 empty] | ECSU - Gilchrist Ed & Psych Bldg
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity Usage (KWhs) |  | 57984 | 59712 | 61440 | 54720 | 48768 | 35904 | 35904 | 55104 | 67008 | 56256 | 78528 | 130368 |  |  |  | 741696 | kwhs | 2531.4084 | MMbtu
| Water Usage (CCF) | No data. | [15 empty] | 0 | CCF | 0 | gallons
| Electricity Cost ($) |  | 6660.13 | 7047.97 | 6843.95 | 6044.45 | 5473.96 | 3779.56 | 3434.3 | 4934.12 | 6173.75 | 6107.88 | 7718.11 | 12387.32 |  |  |  | 76605.5 |  | 76605.5
10 | DoAg&CS - SENC Ag Center | [16 empty] | DoAg&CS - SENC Ag Center
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 52360 | 43759 | 44567 | 53275 | 42179 | 32440 | 44607 | 36358 | 250 | 51400 | 47064 | 56146 |  |  |  | 504405 | kwhs | 1721.5343 | MMbtu
| Nat Gas (Therms) |  | 23 | 31 | 27 | 99 | 601 | 978 | 3984 | 2928 | 754 | 428 | 74 | 35 |  |  |  | 9962 | therms | 995.9622 | MMbtu | 2717.4964 | Mmbtu
| Water Usage (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) |  | 7055.76 | 6534.48 | 6312.33 | 7261.31 | 6112.41 | 5032.46 | 6292.22 | 5457.24 | 50.67 | 7175.17 | 6720.76 | 7891.28 |  |  |  | 71896.09 |  | 71896.09
| Nat Gas Costs ($) |  | 61 | 66.01 | 63 | 115.39 | 456.26 | 717.3 | 2708.28 | 2001.65 | 526.83 | 336.53 | 94.71 | 68.86 |  |  |  | 7215.82 |  | 7215.82
79111.91
11 | UNCC - EPIC | [16 empty] | UNCC - EPIC
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 439536 | 433347 | 433663 | 441674 | 417461 | 430847 | 426042.9 | 403208.3 | 436202.6 | 417591 | 422135.4 | 408032 |  |  |  | 5109740.2 | kwhs | 17439.5433 | MMbtu
| Nat Gas (Therms) |  | 156 | 149 | 169 | 872 | 1662 | 2824 | 2299 | 437 | 1635 | 1516 | 260 | 157 |  |  |  | 12136 | therms | 1213.3102 | MMbtu
| Chilled water (BTU*10^6) |  | 3176 | 2770 | 2066 | 1356 | 948 | 1080 | 439 | 557 | 1095.8 | 1149 | 1621.1 | 2159.9 |  |  |  | 18417.8 | MMbtu | 18417.8 | MMbtu
| Hot Water (BTU*10^6) |  | 339 | 369 | 348 | 524 | 646 | 569 | 759 | 627 | 446.5 | 397.3 | 372.6 | 191 |  |  |  | 5588.4 | MMbtu | 5588.4 | MMbtu | 42659.0535 | MMbtu
| Water Usage (CF) |  | 4410 | 5359 | 9127 | 8827 | 11326 | 11084 | 12616 | 9158 | 17051.4 | 13434.3 | 7685.1 | 6763.5 |  |  |  | 116841.3 | CF | 873972.924 | gallons
| Electricity Cost ($) |  | 29343.6392 | 28943.7919 | 28983.3096 | 26989.8974 | 23487.9842 | 24260.6431 | 24122.947 | 23542.7416 | 25675.4805 | 23963.2284 | 24720.5714 | 26352.4999 |  |  |  | 310386.7341 |  | 310386.7341
| Nat Gas Costs ($) |  | 131.31 | 126.4 | 140.42 | 633.01 | 1178.32 | 1963.47 | 1571.35 | 314.16 | 1115.1 | 1039.81 | 199.7 | 129.64 |  |  |  | 8542.69 |  | 8542.69
| Chilled Water |  | 16372.3879 | 14377.94 | 10936.4472 | 6758.9774 | 4955.9043 | 4723.8498 | 2613.6698 | 3309.6247 | 5343.2288 | 3718.4897 | 6603.2634 | 9545.3459 |  |  |  | 89259.129 |  | 89259.129
| Hot Water |  | 1520.1754 | 2150.2358 | 1921.8172 | 2152.0815 | 2174.9931 | 2580.1328 | 3320.2591 | 2365.5364 | 1809.0395 | 1858.7424 | 1890.108 | 1708.3104 |  |  |  | 25451.4317 |  | 25451.4317
433639.9848
12 | NCDVA - NC State Veterans Home - Black Mountain | [16 empty] | DOA - VA - VA Home Swananoa
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 197842 | 181087 | 169500 | 136848 | 140900 | 169923 | 157756 | 144687 | 144392 | 142200 | 177000 | 177800 |  |  |  | 1939935 | kwhs | 6620.9982 | MMbtu
| Nat Gas (Therms) |  | 2035 | 1902 | 2130 | 2136 | 2861 | 2903 | 2537 | 2419 | 2588 | 1943 | 1945 | 2482 |  |  |  | 27881 | therms | 2787.4343 | MMbtu | 9408.4325 | Mmbtu
| Water Usage (CCF) |  | 490 | 374 | 457 | 427 | 522 | 552 | 488 | 488 | 493 | 493 | 398 | 420 |  |  |  | 5602 | CCF | 4190296 | gallons
| Electricity Cost ($) |  | 15986.9 | 14888.92 | 13812.05 | 11373.94 | 11466.82 | 13405.55 | 12517.76 | 11631.02 | 11456.99 | 11253.54 | 13873.41 | 14147.48 |  |  |  | 155814.38 |  | 155814.38
| Nat Gas Costs ($) |  | 1472.23 | 1379.22 | 1538.44 | 1539.93 | 1900.37 | 1917.73 | 1552.41 | 1478.3 | 1578.03 | 1252.45 | 1255.66 | 1588.24 |  |  |  | 18453.01 |  | 18453.01
174267.39
13 | Pitt CC - Russell Classroom Building | [16 empty] | Pitt CC - Russell Classroom Building
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Gas Usage (Therms) | [16 empty] | 0 | Therms | 0 | MMbtu | 0 | Mmbtu
| Water CCF | [16 empty] | 0 | CCF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Gas Cost ($) | [16 empty] | 0 |  | 0
0
14 | UNCG - Bailey Residence Hall Renovation | [16 empty] | UNCG - Bailey Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 17165 | 25595 | 24164 | 25172 | 21933 | 22308 | 21584 | 23656 | 24638 | 23837 | 18322 | 17851 |  |  |  | 266225 | kwhs | 908.6259 | MMbtu
| Steam Usage (lbs) |  | 5030 | 8310 | 11460 | 14760 | 17321.9512 | 19080 | 53994.9375 | 47894.7812 | 23680 | 20580 | 6800 | 6400 |  |  |  | 235311.67 | lbs | 235.3117 | MMbtu
| Chilled water (ton-hrs) |  | 20523 | 18946 | 17090 | 10892 | 8437 | 7533 | 3846 | 5104 | 9942 | 10519 | 10997 | 15490 |  |  |  | 139319 | ton-hrs | 1671.828 | MMbtu | 2815.7656 | Mmbtu
| Water (gallons) |  | 10000 | 77300 | 97800 | 138700 | 91100 | 57700 | 160600 | 82700 | 69300 | 68600 | 33100 | 25800 |  |  |  | 912700 | gallons | 912700 | gallons
| Electricity Cost ($) |  | 1201.9698 | 1819.1866 | 1662.833 | 1602.7892 | 1396.5508 | 1312.5068 | 1280.4776 | 1397.0632 | 1472.6165 | 1384.1102 | 1090.2448 | 1164.71 |  |  |  | 16785.0586 |  | 16785.0586
| Steam Cost ($) |  | 39.3039 | 64.9335 | 89.5473 | 115.3332 | 135.352 | 149.0892 | 421.911 | 374.245 | 185.0332 | 160.8101 | 53.1345 | 50.009 |  |  |  | 1838.7019 |  | 1838.7019
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
18623.7605
15 | UNCG - Coit Residence Hall Renovation | [16 empty] | UNCG - Coit Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 14811 | 22427 | 21884 | 23712 | 21302 | 21171 | 21753 | 25110 | 22206 | 21916 | 19196 | 17919.5 |  |  |  | 253407.5 | kwhs | 864.8798 | MMbtu
| Steam Usage (lbs) |  | 5855 | 10655 | 7500 | 15020 | 14550 | 15470 | 45020.2344 | 40077.6953 | 21613.75 | 16057 | 16140 | 4780 |  |  |  | 212738.6797 | lbs | 212.7387 | MMbtu
| Chilled water (ton-hrs) |  | 18529 | 22885 | 22789 | 17791 | 14628 | 12298 | 12333 | 10937 | 12907 | 13883 | 13340 | 16784 |  |  |  | 189104 | ton-hrs | 2269.248 | MMbtu | 3346.8665 | Mmbtu
| Water (gallons) |  | 24400 | 29000 | 72000 | 75300 | 64800 | 34800 | 74000 | 84500 | 73400 | 79700 | 24300 | 20300 |  |  |  | 656500 | gallons | 656500 | gallons
| Electricity Cost ($) |  | 1037.1322 | 1594.0183 | 1505.936 | 1509.8259 | 1356.3728 | 1245.6106 | 34.7646 | 588.5076 | 1327.2556 | 1272.5662 | 734.8829 | 1083 |  |  |  | 13289.8726 |  | 13289.8726
| Steam Cost ($) |  | 45.7504 | 83.2571 | 58.6043 | 117.3648 | 113.6922 | 120.881 | 351.7836 | 313.1631 | 168.8877 | 125.4678 | 126.1163 | 37.3504 |  |  |  | 1662.3188 |  | 1662.3188
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
14952.1914
16 | UNCG - Cotten Residence Hall Renovation | [16 empty] | UNCG - Cotten Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 17928 | 27420 | 26490 | 27592 | 24206 | 23917 | 22057 | 24845 | 25664 | 28515 | 19449 | 18617 |  |  |  | 286700 | kwhs | 978.5071 | MMbtu
| Steam Usage (lbs) |  | 6680 | 13000 | 19100 | 35130 | 10000 | 14470 | 42376.293 | 36995.6191 | 22197.1875 | 51990 | 8710 | 7980 |  |  |  | 268629.0996 | lbs | 268.6291 | MMbtu
| Chilled water (ton-hrs) |  | 19231 | 21446 | 20118 | 14783 | 11547 | 9616 | 5516 | 6976 | 12798 | 12870 | 12322 | 16624 |  |  |  | 163847 | ton-hrs | 1966.164 | MMbtu | 3213.3002 | Mmbtu
| Water (gallons) |  | 13500 | 80300 | 122000 | 119200 | 99400 | 66000 | 98100 | 114700 | 98500 | 87300 | 27800 | 52000 |  |  |  | 978800 | gallons | 978800 | gallons
| Electricity Cost ($) |  | 1255.3985 | 1948.9 | 1822.8954 | 1756.8791 | 1541.2806 | 1407.1735 | 1308.5385 | 1467.2825 | 1533.9407 | 1655.7412 | 1157.3066 | 1214.6886 |  |  |  | 18070.0252 |  | 18070.0252
| Steam Cost ($) |  | 52.1969 | 101.5807 | 149.2455 | 274.5023 | 78.139 | 113.0671 | 331.1241 | 289.0801 | 173.4466 | 406.2447 | 68.0591 | 62.3549 |  |  |  | 2099.0409 |  | 2099.0409
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
20169.0662
17 | UNCG - Gray Residence Hall Renovation | [16 empty] | UNCG - Gray Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 17881 | 25823 | 25262 | 27592 | 22992 | 23272 | 21878 | 22370 | 24352 | 24196 | 19926 | 18382 |  |  |  | 273926 | kwhs | 934.9094 | MMbtu
| Steam Usage (lbs) |  | 2990 | 7420 | 11540 | 13660 | 17000 | 19470 | 55596 | 52406 | 19280 | 17918 | 5670 | 5140 |  |  |  | 228090 | lbs | 228.09 | MMbtu
| Chilled water (ton-hrs) |  | 18910 | 21330 | 21444 | 13159 | 9189 | 8344 | 3436 | 4313 | 10606 | 11178 | 13308 | 19159 |  |  |  | 154376 | ton-hrs | 1852.512 | MMbtu | 3015.5114 | Mmbtu
| Water (gallons) |  | 9500 | 64700 | 87500 | 100100 | 75300 | 41800 | 78400 | 89900 | 70300 | 75800 | 23400 | 39600 |  |  |  | 756300 | gallons | 756300 | gallons
| Electricity Cost ($) |  | 1252.1073 | 1835.3919 | 1738.3913 | 1756.8791 | 1463.981 | 1369.2244 | 1297.9193 | 1321.1153 | 1455.5223 | 1404.9558 | 1185.6903 | 1199.3557 |  |  |  | 17280.5337 |  | 17280.5337
| Steam Cost ($) |  | 23.3636 | 57.9791 | 90.1724 | 106.7379 | 132.8363 | 152.1366 | 434.4216 | 409.4952 | 150.652 | 140.0095 | 44.3048 | 40.1634 |  |  |  | 1782.2725 |  | 1782.2725
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
19062.8062
18 | UNCG - Hinshaw Residence Hall Renovation | [16 empty] | UNCG - Hinshaw Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 20706 | 31693 | 32266 | 32710 | 29305 | 29247 | 27937 | 29569 | 30145 | 30013 | 23424 | 23243 |  |  |  | 340258 | kwhs | 1161.3006 | MMbtu
| Deduct site lighting (KWhs) |  | 2583 | 2923 | 3112 | 3510 | 3735 | 3915 | 3851 | 3311 | 3715 | 3107 | 2948 | 2670 |  |  |  | 39380 | kwhs | 134.4039 | MMbtu
| Steam Usage (lbs) |  | 4390 | 11340 | 16340 | 19400 | 20070 | 11480 | 35100 | 33730 | 21480 | 21780 | 6750 | 7200 |  |  |  | 209060 | lbs | 209.06 | MMbtu
| Chilled water (ton-hrs) |  | 18284 | 22007 | 21871 | 12915 | 10214 | 7974 | 4325 | 5323 | 10817 | 11584 | 12586 | 19547 |  |  |  | 157447 | ton-hrs | 1889.364 | MMbtu | 3125.3206 | Mmbtu
| Water (gallons) |  | 4400 | 54200 | 73200 | 76200 | 70400 | 33200 | 74500 | 83800 | 71000 | 76300 | 18800 | 23800 |  |  |  | 659800 | gallons | 659800 | gallons
| Electricity Cost ($) |  | 1449.9264 | 2252.6071 | 2220.3679 | 2082.76 | 1865.9518 | 1720.7677 | 1657.3713 | 1746.27 | 1801.7707 | 1742.7235 | 1393.8377 | 1516.5176 |  |  |  | 21450.8718 |  | 21450.8718
| Steam Cost ($) |  | 34.303 | 88.6096 | 127.6791 | 151.5897 | 156.825 | 89.7036 | 274.2679 | 263.5628 | 167.8426 | 170.1867 | 52.7438 | 56.2601 |  |  |  | 1633.5739 |  | 1633.5739
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
23084.4457
19 | UNCG - Jamison Residence Hall Renovation | [16 empty] | UNCG - Jamison Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 17284 | 25723 | 27480 | 27696 | 23456 | 23047 | 21494 | 21134 | 24628 | 24142 | 19087 | 16828 |  |  |  | 271999 | kwhs | 928.3326 | MMbtu
| Steam Usage (lbs) |  | 1690 | 1710 | 1180 | 12260 | 14520 | 11850 | 35390 | 26280 | 22015 | 3950 | 420 | 6300 |  |  |  | 137565 | lbs | 137.565 | MMbtu
| Chilled water (ton-hrs) |  | 18738.5 | 15540 | 14419 | 10251 | 9091 | 7664 | 4935 | 5032 | 7646 | 9019 | 9143 | 12709 |  |  |  | 124187.5 | ton-hrs | 1490.25 | MMbtu | 2556.1476 | Mmbtu
| Water (gallons) |  | 5200 | 56500 | 85000 | 98400 | 87400 | 71800 | 91900 | 113400 | 97500 | 80500 | 21800 | 26000 |  |  |  | 835400 | gallons | 835400 | gallons
| Electricity Cost ($) |  | 1210.3027 | 1828.2843 | 1891.0218 | 1763.5011 | 1493.5255 | 1355.9864 | 1275.1383 | 1248.1203 | 1472.0188 | 1401.8202 | 1135.7659 | 1097.9631 |  |  |  | 17173.4486 |  | 17173.4486
| Steam Cost ($) |  | 13.2055 | 13.3618 | 9.2204 | 95.7984 | 113.4578 | 92.5947 | 276.5339 | 205.3493 | 172.023 | 30.8649 | 3.2818 | 49.2276 |  |  |  | 1074.9192 |  | 1074.9192
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
18248.3678
20 | UNCG - Shaw Residence Hall Renovation | [16 empty] | UNCG - Shaw Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 35665 | 47881 | 46903 | 48407 | 42494 | 44158 | 41997 | 44103 | 45877 | 44951 | 36651 | 38142 |  |  |  | 517229 | kwhs | 1765.3026 | MMbtu
| Steam Usage (lbs) |  | 1490 | 2150 | 10110 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | 35290 | 14330 |  |  |  | 63370 | lbs | 63.37 | MMbtu
| Chilled water (ton-hrs) |  | 47976 | 46657 | 44307 | 31922 | 26803 | 22795 | 16977 | 20489 | 31565 | 33938 | 34826 | 49966 |  |  |  | 408221 | ton-hrs | 4898.652 | MMbtu | 6727.3246 | Mmbtu
| Water (gallons) |  | 1911.7647 | 127100 | 157900 | 154500 | 123500 | 83700 | 127900 | 139000 | 114800 | 114500 | 46500 | 49500 |  |  |  | 1240811.7647 | gallons | 1240811.7647 | gallons
| Electricity Cost ($) |  | 2497.4222 | 3403.1831 | 3227.6053 | 3082.2429 | 2705.7415 | 2598.0669 | 2491.4853 | 2604.6111 | 2742.0744 | 2610.1077 | 2180.9062 | 2488.6208 |  |  |  | 32632.0675 |  | 32632.0675
| Steam Cost ($) |  | 11.6427 | 16.7999 | 78.9985 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | 275.7525 | 111.9732 |  |  |  | 495.1668 |  | 495.1668
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
|  | Note 1: Inaccurate Steam Meter | [17 empty] | 33127.2343
21 | WCU - Harrill Residence Hall Renovation | [16 empty] | WCU - Harrill Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 56876 | 74032 | 80325 | 73896 | 72153 | 43317 | meter down | meter down | 76832 | 69878 | 53689 | 52885 |  |  |  | 653883 | kwhs | 2231.7027 | MMbtu
| Water (CCF) |  | 31.0406 | 166.2986 | 263.3239 | 214.0092 | 243.7932 | 80.997 | 171.98 | 228.2194 | 198.8632 | 249.0201 | 37.4573 | 12.1248 |  |  |  | 1897.1275 | CCF | 1419051.3494 | gallons
| Electricity Cost ($) |  | 4159.8538 | 5809.9573 | 5936.4191 | 4395.7775 | 4292.0934 | 2698.2592 | meter down | meter down | 4556.1376 | 4268.1482 | 3248.0234 | 4009.5292 |  |  |  | 43374.1987 |  | 43374.1987
22 | UNCP Health Science Builidng | [16 empty] | UNCP Health Science Builidng
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 161839 | 131675 | 169020 | 131395 | 123099 | 115651 | 90881 | 101201 | 89476 | 129462 | 103558 | 113370 |  |  |  | 1460627 | kwhs | 4985.12 | MMbtu
| Nat Gas (Therms) |  | 1765 | 1268 | 1379 | 1519 | 1787 | 2640 | 2405 | 3310 | 2511 | 2617 | 1485 | 1321 |  |  |  | 24007 | therms | 2400.1268 | MMbtu | 7385.2468 | MMBtu
| Water (gallons) | No data. | [15 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) |  | 13070.1176 | 10634.073 | 13650.0552 | 10611.4602 | 9941.4752 | 9339.9748 | 7339.5496 | 8172.9928 | 7226.0818 | 10455.3511 | 8363.3441 | 9155.7612 |  |  |  | 117960.2365 |  | 117960.2365
| Nat Gas Costs ($) |  | 1015.581 | 729.6072 | 793.4766 | 874.0326 | 1028.2398 | 1519.056 | 1383.837 | 1904.574 | 1444.8294 | 1505.8218 | 854.469 | 760.1034 |  |  |  | 13813.6278 |  | 13813.6278
131773.8643
23 | FSU - Renaissance Residence Hall | [16 empty] | FSU - Renaissance Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | No Data. | [15 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | No Data. | [15 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | No Data. | [15 empty] | 0 |  | 0
24 | UNCA - Overlook Residence Hall | [16 empty] | UNCA - Overlook Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [12 empty] | * No meter data |  |  |  | 0 | kwhs | 0 | MMbtu
| Water (CCF) | 137 | 189 | 479 | 583 | 578 | 545 | 145 | 693 | 669 | 868 | 665 | 98 |  |  |  |  | 5649 | CCF | 4225452 | gallons
| Electricity Cost ($) | [12 empty] | * No meter data |  |  |  | 0 |  | 0
25 | ECSU - Viking Tower Residence Hall | [16 empty] | ECSU - Viking Tower Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity Usage (KWhs) |  | 40760 | 51843 | 57560 | 58807 | 54797 | 49241 | 50985 | 51811 | 53229.2 | 56043.7 | 51204.8 | 43161.1 |  |  |  | 619442.8 | kwhs | 2114.1583 | MMbtu
| Water (gallons) |  | 9563 | 176523 | 176523 | 219217 | 114451 | 114451 | 114451 | 200352 | 110648 | 266982 | 251199 | 251089 |  |  |  | 2005449 | gallons | 2005449 | gallons
| Electricity Cost ($) |  | 3713.22 | 4608.81 | 5289.79 | 5345.56 | 5030.38 | 4554.79 | 4797.65 | 4787.3 | 4897.09 | 5195.25 | 4741.56 | 4009.67 |  |  |  | 56971.07 |  | 56971.07
26 | UNCW - Teaching Lab | [16 empty] | UNCW Teaching Lab
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Heating Hot Water Usage (Mbtu) | [16 empty] | 0 | Mbtu | 0 | MMbtu
| Chilled water (ton-hrs) | [16 empty] | 0 | ton-hrs | 0 | MMbtu | 0 | MMbtu
| Water Usage (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Heating Hot Water ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
0
27 | UNCA - Rhoades Hall Renovation | [16 empty] | UNCA - Rhoades Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [12 empty] | * No meter data |  |  |  | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | 850 | 205 | 237 | 1123 | 1576 | 3001 | 4718 | 5697 | 6373 | 4261 | 3275 | 1851 |  |  |  |  | 33167 | therms | 3315.9081 | MMbtu | 3315.9081 | MMBtu
| Water (CCF) |  | 398 |  | 211 |  | 222 |  | 108 |  | 157 |  | 222 |  |  |  |  | 1318 | CCF | 985864 | gallons
| Electricity Cost ($) | [12 empty] | * No meter data |  |  |  | 0 |  | 0
| Nat Gas Costs ($) | 623.39 | 181.27 | 203.98 | 799.84 | 1094.39 | 1918.77 | 2902.32 | 3269.8 | 3521.96 | 2416.7 | 1935.26 | 1137.99 |  |  |  |  | 20005.67 |  | 20005.67
20005.67
28 | ECU - Ross Hall | [16 empty] | ECU - Ross Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 195786.52 | 193318.21 | 190165.6 | 186489.03 | 179960.13 | 192952.99 | 196114.78 | 190897.88 | 201911.74 | 192422.26 | 199238.14 | 200415.37 |  |  |  | 2319672.65 | kwhs | 7917.0428 | MMbtu
| Chilled water (ton-hrs) |  | 130223 | 117883 | 112675 | 61763 | 47561 | 40723 | 20532 | 22875 | 50367 | 48735 | 67625 | 117328 |  |  |  | 838290 | ton-hrs | 10059.48 | MMbtu
| Natural Gas (Therms) |  | 459 | 1155 | 1487 | 1719 | 1745 | 2025 | 3795 | 3764 | 2144 | 1803 | 1378 | 1420 |  |  |  | 22894 | therms | 2288.8534 | MMbtu | 20265.3761 | MMbtu
| Water Usage (gallons) |  | No Data. | [14 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) |  | 17180.2671 | 16963.6729 | 16687.0314 | 16364.4124 | 15791.5014 | 16931.6249 | 17209.0719 | 16751.289 | 17717.7552 | 16885.0533 | 17483.1468 | 17586.4487 |  |  |  | 203551.275 |  | 203551.275
| Chilled Water ($) |  | No Data. | [14 empty] | 0 |  | 0
| Nat Gas Costs ($) |  | 523.21 | 1152.14 | 1327.57 | 1516.17 | 1537.3 | 1764.91 | 3203.75 | 3178.55 | 1861.65 | 1584.45 | 1238.97 | 1267.24 |  |  |  | 20155.91 |  | 20155.91
203551.275
29 | Gaston College - Lena Sue Beam Renovation | [16 empty] | Gaston College - Lena Sue Beam Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 27480 | 29080 | 31240 | 28480 | 23520 | 18840 | 21560 | 24650 | 23200 | 23680 | 28000 | 17560 |  |  | 297290 | kwhs | 1014.6508 | MMbtu
| Heating Hot Water (?) |  |  | 0 | 1050 | 59050 | 143150 | 147350 | 264700 | 192850 | 72800 | 22800 | 0 | 0 | 0 |  |  | 903750 | lbs | 903.75 | MMbtu
| Chilled water (ton-hrs) | No data | [15 empty] | 0 | ton-hrs | 0 | MMbtu | 1918.4008 | MMbtu
| Water (gallons) |  |  | 9665 | 11022 | 10187 | 9900 | 6974 | 7940 | 10850 | 9965 | 10166 | 33768 | 6367 | 3449 |  |  | 130253 | gallons | 130253 | gallons
| Electricity Cost ($) |  |  | 2414.2801 | 2541.3274 | 2401.7624 | 2232.6611 | 1792.4451 | 1403.256 | 1665.4733 | 1771.4673 | 1739.1022 | 1381.8701 | 3247.4624 | 1608.9174 |  |  | 24200.0249 |  | 24200.0249
| Heating Hot Water Cost ($) |  |  | 0 | 28 | 680.8 | 1513.6 | 1511.2 | 2528.8 | 1861.6 | 740.8 | 264.8 | 0 | 0 | 0 |  |  | 9129.6 |  | 9129.6
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
| missing a meter reading for one critical piece of information related to Chilled Water | [18 empty] | 33329.6249
30 | NCSU - Hunt Library | [16 empty] | NCSU - Hunt Library
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (kWh) |  |  | 371394.5312 | 372462.4023 | 382747.0703 | 368691.8945 | 374088.8672 | 375130.8594 | 352869.1406 | 421780.2734 | 383250.9766 | 384455.0781 | 360948.2422 | 375840.8203 |  |  | 4523660.1562 | kwh | 15439.2521 | MMbtu
| Chilled Water (Dtherms) |  |  | 1188.704 | 1065.488 | 520.544 | 403.264 | 439.44 | 134.784 | 217.952 | 506 | 525 | 781 | 1117 | 1530 |  |  | 8429.176 | dthrms | 8429.176 | MMbtu
| Steam (1,000 lbs) |  |  | 263.0938 | 282.7969 | 420.2031 | 527.4062 | 593.6875 | 1087.7031 | 909.1094 | 662 | 517 | 415 | 327 | 335 |  |  | 6340 | 1000 lbs | 6340 | MMbtu | 30208.4281 | MMbtu
| Water (CCF) |  |  | 382 | 317 | 190 | 189 | 170 | 107 | 197 | 203 | 240 | 156 | 116 | 93 |  |  | 2360 | CCF | 1765280 | gallons
| Electricity Cost ($) |  |  | 31939.9297 | 32031.7666 | 32916.248 | 31707.5029 | 32171.6426 | 32261.2539 | 30346.7461 | 36273.1035 | 32959.584 | 33063.1367 | 31041.5488 | 32698.1514 |  |  | 389410.6143 |  | 389410.6143
| Chilled Water Cost ($) |  |  | 16606.1949 | 14884.8674 | 7271.9997 | 5633.5981 | 6138.9768 | 1882.9325 | 3044.7894 | 7068.82 | 7334.25 | 10910.57 | 15604.49 | 19813.5 |  |  | 116194.9887 |  | 116194.9887
| Steam Cost ($) |  |  | 3522.8253 | 3786.6502 | 5626.5198 | 7061.9697 | 7949.4756 | 14564.3448 | 12172.9745 | 8864.18 | 6922.63 | 5556.85 | 4378.53 | 4026.7 |  |  | 84433.65 |  | 84433.65
590039.253
31 | UNCC - Rose Football Center | [16 empty] | UNCC - Rose Football Center
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 153348 | 204930 | 186979 | 216712.2 | 210352.9 | 124355.6 | 116637.7 | 112030 | 126273.9 | 136211 | 123814.9 | 136677.8 |  |  |  | 1848323 | kwhs | 6308.3264 | MMbtu
| Nat Gas (Therms) |  | 1240 | 976 | 1627 | 2150 | 3202 | 2860 | 4149 | 3704 | 2627 | 1905 | 1628 | 1023 |  |  |  | 27091 | therms | 2708.4532 | MMbtu | 9016.7796 | Mmbtu
| Water Usage (CF) |  | 78754 | 34591 | 25069 | 44991 | 15285 | 12019 | 21527 | 10314 | 11210 | 28835 | 20732 | 19184 |  |  |  | 322511 | CF | 2412382.28 | gallons
| Electricity Cost ($) |  | 10237.5878 | 13687.5328 | 12496.5013 | 13242.8896 | 11835.2747 | 7002.3624 | 6604.1355 | 6541.2675 | 7432.6541 | 7816.3928 | 7250.6951 | 8827.253 |  |  |  | 112974.5467 |  | 112974.5467
| Nat Gas Costs ($) |  | 890.87 | 705.88 | 1162.04 | 1528.51 | 2249.76 | 1988.22 | 2818.11 | 2498.35 | 1778.31 | 1778.31 | 1134.67 | 723.38 |  |  |  | 19256.41 |  | 19256.41
132230.9567
32 | NC Division of Veterans Affairs - NC State Veterans Home - Kinston | [16 empty] | NC Division of Veterans Affairs - NC State Veterans Home - Kinston
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 200600 | 218000 | 2084000 | 169200 | 166000 | 178800 | 151800 | 153400 | 164400 | 161800 | 186400 | 228400 |  |  |  | 4062800 | kwhs | 13866.3364 | MMbtu
| Nat Gas (Therms) |  | 1388 | 1948 |  |  | 1946 | 1778 | 2078 | 1884 | 2185 | 1682 |  | 1881 |  |  |  | 16770 | therms | 1676.5996 | MMbtu | 15542.936 | MMBtu
| Water Usage (gallons) |  | 313000 | 343200 | 411900 | 468800 | 426700 | 3067000 | 295400 | 311700 | 274500 | 279200 | 257100 | 261900 |  |  |  | 6710400 | gallons | 6710400 | gallons
| Electricity Cost ($) |  | 17162.63 | 18673.51 | 18211.23 | 15024.62 | 14372.26 | 14668.42 | 13084.35 | 13290.26 | 14102.62 | 13922.34 | 16067.44 | 19309.93 |  |  |  | 187889.61 |  | 187889.61
| Nat Gas Costs ($) |  | 1064.19 | 1507.59 |  |  | 1477.19 | 1330.66 | 1526.77 | 1371.28 | 1586.6 | 1228.24 |  | 1402.88 |  |  |  | 12495.4 |  | 12495.4
200385.01
33 | Randolph CC - Klaussner Building Renovation | [16 empty] | Randolph CC - Klaussner Building Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 74600 | 75300 | 90000 | 64800 | 59400 | 53600 | 54300 | 38300 | 54900 | 58000 | 71300 | 77300 |  |  |  | 771800 | kwhs | 2634.1534 | MMbtu
| Nat Gas (Therms) |  | 401 | 287 | 599 | 605 | 871 | 1332 | 1226 | 829 | 787 | 907 | 734 | 513 |  |  |  | 9091 | therms | 908.8829 | MMbtu | 3543.0363 | MMbtu
| Water Usage (CF) |  | 810 | 410 | 270 | 240 | 230 | 90 | 160 | 510 | 260 | 390 | 150 | 130 |  |  |  | 3650 | CF | 27302 | gallons
| Electricity Cost ($) |  | 7496.84 | 7587.43 | 8516.99 | 5789.8 | 5453.97 | 4920.43 | 4698.49 | 4079.05 | 5175.72 | 5182.37 | 6051.77 | 6665.95 |  |  |  | 71618.81 |  | 71618.81
| Nat Gas Costs ($) |  | 324.19 | 238.72 | 472.64 | 488.86 | 662.31 | 1000.3 | 900.57 | 616.58 | 567.61 | 686.83 | 560.47 | 400.31 |  |  |  | 6919.39 |  | 6919.39
78538.2
34 | ASU - Plemmons Student Union Addition | [16 empty] | ASU - Plemmons Student Union Addition
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 126492.56 | 131062.96 | 176404.16 | 167466.72 | 120254 | 123945.44 | 113920.48 | 131483.76 | 147519.64 | 134698.84 | 141380.32 | 111725.04 |  |  |  | 1626353.9202 | kwhs | 5550.7459 | MMbtu
| Steam (lbs) |  | 271115 | 312825 | 280291.2 | 475494 | 413763.2 | 394576.6 | 684044 | 611468.6 | 436286.6 | 301146.2 | 307819.8 | 281125.4 |  |  |  | 4769955.6 | lbs | 4769.9556 | MMbtu | 10320.7015 | MMbtu
| Water (gallons) |  | 252014 | 322375 | 368441 | 253901 | 185426 | 92000 | 603000 | 290000 | 231245 | 300786 | 189327 | 314358 |  |  |  | 3402873 | gallons | 3402873 | gallons
| Elecricity Cost ($) |  | 11291.262 | 11697.6702 | 15729.616 | 14934.8507 | 10736.5003 | 11064.7504 | 10173.2963 | 11123.4077 | 11925.7743 | 10893.0468 | 11431.2475 | 9042.492 |  |  |  | 140043.9143 |  | 140043.9143
| Steam Costs ($) |  | 5694 | 6570 | 5886.72 | 9986.4 | 8689.92 | 8286.96 | 14366.4 | 12842.16 | 9162.96 | 6324.72 | 6464.88 | 5904.24 |  |  |  | 100179.36 |  | 100179.36
240223.2743
35 | ASU - Summit Residence Hall and Appalachian Hall | [16 empty] | ASU - Summit Residence Hall and Appalachian Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 95653.12 | 104193.92 | 115816.32 | 104813.44 | 91664 | 78922.88 | 80144.96 | 80595.52 | 79393.28 | 96367.68 | 92576.64 | 83022.08 |  |  |  | 1103163.8401 | kwhs | 3765.0982 | MMbtu
| Steam (lbs) |  | 180187.2 | 238581.2 | 311990.8 | 301980.4 | 437120.8 | 430447.2 | 718246.2 | 713241 | 376224.2 | 385400.4 | 283628 | 251928.4 |  |  |  | 4628975.8 | lbs | 4628.9758 | MMbtu | 8394.074 | MMbtu
| Water (gallons) |  | 98728 | 214000 | 289432 | 263352 | 217152 | 96000 | 201000 | 258000 | 203240 | 310872 | 123504 | 88616 |  |  |  | 2363896 | gallons | 2363896 | gallons
| Elecricity Cost ($) |  | 8535.3185 | 9294.8014 | 10328.333 | 9349.9009 | 8180.5801 | 7047.5987 | 7156.2676 | 6821.3914 | 6424.5957 | 7791.8936 | 7486.5245 | 6716.9106 |  |  |  | 95134.116 |  | 95134.116
| Steam Costs ($) |  | 4406.07 | 5833.97 | 7629.04 | 7384.25 | 10688.82 | 10525.62 | 17563.11 | 17440.72 | 9199.72 | 9424.1 | 6935.49 | 6160.34 |  |  |  | 113191.25 |  | 113191.25
208325.366
36 | UNCW - MARBIONC | [16 empty] | UNCW - MARBIONC
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (MCF) | [16 empty] | 0 | MCF | 0 | MMbtu | 0 | MMbtu
| Water Usage (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0 |  |  | MCF=1000CF
[20 empty] | 0 |  |  | 1 cubic foot = 1,025 Btu
37 | DOA - NC State Bar HQ | [16 empty] | DOA - NC State Bar HQ
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 77200 | 67600 | 68400 | 81800 | 67800 | 84600 | 87200 | 81400 | 83000 | 85600 | 78800 | 74800 |  |  |  | 938200 | kwhs | 3202.0766 | MMbtu
| Water Usage (CCF) |  | 37 | 20 | 19 | 19 | 23 | 25 | 23 | 25 | 27 | 28 | 29 | 32 |  |  |  | 307 | CCF | 229636 | gallons
| Elecricity Cost ($) |  | 6845.41 | 6114.04 | 6267.63 | 7319.38 | 6252.8 | 7471.3 | 7540.61 | 7276.39 | 7457.85 | 7520.86 | 7030.4 | 6664.63 |  |  |  | 83761.3 |  | 83761.3
83761.3
38 | FSU - Science and Technology Building | [16 empty] | FSU - Science and Technology Building
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
39 | UNCW - Student Rec Facility Addition | [16 empty] | UNCW - Student Rec Facility Addition
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (MCF) | [16 empty] | 0 | MCF | 0 | MMbtu
| Heating Hot Water Usage (Mbtu) | [16 empty] | 0 | Mbtu | 0 | MMbtu
| Chilled water (ton-hrs) | [16 empty] | 0 | ton-hrs | 0 | MMbtu | 0 | MMbtu
| Water Usage (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0 |  |  | MCF=1000CF
| Heating Hot Water ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
[20 empty] | 0 |  |  | 1 cubic foot = 1,025 Btu
40 | WSSU - Reaves Student Activities Center | [16 empty] | WSSU - Reaves Student Activities Center
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 68049 | 94819 | 105441 | 110223 | 95645 | 74913 | 102885 | 104979 | 103536 | 106757 | 64417 | 69747 |  |  |  | 1101411 | kwhs | 3759.1157 | MMbtu
| Steam (Nat Gas in therms) |  | 0 | 0 | 0 | 0 | 0 | 7394.553 | 9386.719 | 7926.583 | 7099.156 | 5846.022 | 2908.071 | 0 |  |  |  | 40561.104 | therms | 4055.142 | MMbtu
| Chilled water (kwh) |  | 124193.4309 | 144505.6921 | 109863.1534 | 63533.9859 | 42945.056 | 59940.8656 | 56182.7266 | 88921.1862 | 75964.8736 | 138779.1636 | 115908.7776 | 144395.1586 |  |  |  | 1165134.0701 | kwhs | 3976.6026 | MMbtu
| Nat Gas (Therms) |  | 2270 | 1660 | 2451 | 2683 | 2616 | 866 | 993 | 1519 | 710 | 640 | 1246 | 1849 |  |  |  | 19503 | therms | 1949.8344 | MMbtu | 9764.0921 | Mmbtu
| Water (CCF) |  | 23.01 | 78.56 | 101.36 | 90.88 | 89.03 | 30.44 | 79.81 | 99.14 | 47.85 | 102.66 | 32.37 | 23.2 |  |  |  | 798.31 | CCF | 597135.88 | gallons
| Electricity Cost ($) |  | 4845.0888 | 6751.1128 | 7507.3992 | 7847.8776 | 6809.924 | 5333.8056 | 7325.412 | 7474.5048 | 7371.7632 | 7601.0984 | 4586.4904 | 4965.9864 |  |  |  | 78420.4632 |  | 78420.4632
| Steam Costs ($ Natural Gas) |  | 0 | 0 | 0 | 0 | 0 | 3140.6445 | 4000.468 | 3244.9456 | 2574.7563 | 2300.8264 | 1213.8501 | 0 |  |  |  | 16475.4909 |  | 16475.4909
| Chilled water ($) |  | 8842.5723 | 10288.8053 | 7822.2565 | 4523.6198 | 3057.688 | 4267.7896 | 4000.2101 | 6331.1885 | 5408.699 | 9881.0764 | 8252.705 | 10280.9353 |  |  |  | 82957.5458 |  | 82957.5458
| Nat Gas Costs ($) |  | 1612.59 | 1185.16 | 1739.42 | 1960.98 | 1814.46 | 616.05 | 685.88 | 1037.54 | 477.13 | 459.41 | 873.7 | 1291.14 |  |  |  | 13753.46 |  | 13753.46
191606.9599
41 | Haywood Community College - Creative Arts Building | [16 empty] | Haywood Community College - Creative Arts Building
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 27170.48 | 22042 | 20689.61 | 19381 | 17218.59 | 20494.68 | 22876.24 | 22344 | 18131 | 22855.6 | 23879.83 | 27520.965 |  | 282277 | kwhs | 963.4114 | MMbtu
| Nat Gas (therms) |  |  |  | 270 | 593 | 1089 | 1466 | 2214 | 1547 | 1029 | 498 | 217 | 0 | 0 | 39 |  | 8962 | therms | 895.986 | MMbtu | 1859.3974 | MMbtu
| Water Usage (CF) |  |  |  | 27350 | 9686.76 | 7171.124 | 4935 | 7080 | 7742 | 7905.5 | 9036.81 | 6305.3 | 11924 | 13898.476 | 2851 |  | 154338 | gallons | 154338 | gallons
| Elecricity Cost ($) |  |  |  | 2717.048 | 2204.2 | 2068.961 | 1938.1 | 1721.859 | 2049.468 | 2287.624 | 2234.4 | 1813.1 | 2285.56 | 2387.983 | 2752.0965 |  | 16996 |  | 16996
| Nat Gas Costs ($) |  |  |  | 224.54 | 450.62 | 751.28 | 958.61 | 1357.35 | 963.8 | 672 | 359.33 | 167.13 | 15.63 | 16 | 45.4 |  | 5924.42 |  | 5924.42
22920.42
42 | UNCC - Belk Residence Hall | [16 empty] | UNCC - Belk Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 198506 | 163733 | 163642 | 152567.2 | 142257 | 131679.1 | 136880 | 135495 | 143859.8 | 156668.8 | 148419.1 | 158055 |  |  |  | 1831762 | kwhs | 6251.8037 | MMbtu
| Nat Gas (Therms) |  | 2684 | 2067 | 2465 | 2291 | 1827 | 2694 | 3702 | 3920 | 2632 | 2129 | 2308 | 1587 |  |  |  | 30306 | therms | 3029.8764 | MMbtu | 9281.6801 | Mmbtu
| Water (CF) |  | 14453.2086 | 85831.5508 | 89032.0856 | 83711.2299 | 59041.4439 | 36978.6096 | 81380 | 33919 | 94720 | 68565 | 29394 | 79588 |  |  |  | 756614.1283 | CF | 5659473.68 | gallons
| Electricity Cost ($) |  | 13252.3581 | 10935.9333 | 10936.8029 | 9323.105 | 8003.9337 | 7414.7427 | 7750.2735 | 7911.3544 | 8467.7842 | 8990.3524 | 8691.5358 | 10207.8866 |  |  |  | 111886.0625 |  | 111886.0625
| Nat Gas Costs ($) |  | 1902.68 | 1470.35 | 1749.23 | 1627.3 | 1293.11 | 1874.09 | 2516.86 | 2642.76 | 1781.65 | 1451.36 | 1599.43 | 1110.06 |  |  |  | 21018.88 |  | 21018.88
132904.9425
43 | NCSU - Cherry Building Renovation | [16 empty] | NCSU - Cherry Building Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 30902.9541 | 29335.022 | 22770.0195 | 23882.9956 | 21528.0151 | 27824.9512 | 28780.0293 | 28239.9902 | 28801.0254 | 29156.0059 | 30916.9922 | 31935.9741 |  |  | 334073.9746 | kwhs | 1140.1945 | MMbtu
| Nat Gas (Therms) |  |  | 52.8824 | 113.5378 | 230.9699 | 184.7368 | 558.4539 | 1281.6964 | 1331.601 | 707.8276 | 295.1786 | 218.9464 | 176.0179 | 130.8942 |  |  | 5282.7429 | therms | 528.1482 | MMbtu | 1668.3426 | Mmbtu
| Water (CCF) |  |  | 18.8182 | 14.5333 | 11.919 | 12.0143 | 7.6 | 7.669 | 9.5453 | 10.3675 | 11.4182 | 12.4032 | 10.8429 | 7 |  |  | 134.131 | CCF | 100329.9897 | gallons
| Electricity Cost ($) |  |  | 2657.6541 | 2522.8119 | 1958.2217 | 2053.9376 | 1851.4093 | 2392.9458 | 2475.0825 | 2428.6392 | 2476.8882 | 2507.4165 | 2658.8613 | 2778.4297 |  |  | 28762.2978 |  | 28762.2978
| Nat Gas Costs ($) |  |  | 51.7275 | 101.4221 | 255.4112 | 260.3684 | 428.602 | 818.2254 | 835.5763 | 465.7004 | 217.8637 | 168.2168 | 138.6907 | 108.6458 |  |  | 3850.4501 |  | 3850.4501
32612.7479
44 | UNCC - Hunt Residence Hall | [16 empty] | UNCC - Hunt Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 72541 | 83889 | 100939 | 102210 | 97671 | 93457 | 93202 | 92374 | 91453 | 90879 | 73565 | 27670 |  |  |  | 1019850 | kwhs | 3480.7481 | MMbtu
| Nat Gas (Therms) |  | 111 | 237 | 226 | 710 | 870 | 725 | 669 | 1016 | 893 | 856 | 691 | 228 |  |  |  | 7232 | therms | 723.0273 | MMbtu
| Chilled Water (MMBtu) |  | 489 | 472 | 428 | 211 | 136 | 120 | 53 | 79 | 191 | 244 | 260 | 384 |  |  |  | 3067 | MMbtu | 3067 | MMbtu
| Hot Water (MMBtu) |  | 41 | 21 | 17 | 86 | 87 | 73 | 28 | 15 | 27 | 91 | 85 | 82 |  |  |  | 653 | MMbtu | 653 | MMbtu | 7923.7754 | MMbtu
| Water (CF) |  | 3009 | 20503 | 42490 | 40544 | 37565 | 27110 | 33128 | 42047 | 35614 | 42330 | 22460 | 8959 |  |  |  | 355759 | CF | 2661077.32 | gallons
| Electricity Cost ($) |  | 4842.8728 | 5603.052 | 6746.1284 | 6245.8678 | 5495.3514 | 5262.4874 | 5277.1843 | 5393.5824 | 5383.0484 | 5215.0411 | 4308.0226 | 1787.0502 |  |  |  | 61559.6889 |  | 61559.6889
| Nat Gas Costs ($) |  | 99.78 | 188.07 | 490.77 | 519.5 | 627.29 | 520.43 | 472.85 | 701.26 | 619.02 | 596.7 | 494.27 | 178.32 |  |  |  | 5508.26 |  | 5508.26
| Chilled Water ($) |  | 2690.5656 | 2554.7929 | 2087.9207 | 915.3609 | 589.2054 | 554.9729 | 442.9162 | 460.0509 | 887.3198 | 1159.8199 | 1224.8985 | 2269.6413 |  |  |  | 15837.4649 |  | 15837.4649
| Hot Water ($) |  | 723.0144 | 399.0989 | 428.9759 | 1925.198 | 1778.2184 | 1559.7605 | 378.2253 | 232.8643 | 595.2236 | 1534.994 | 1609.4198 | 1536.4864 |  |  |  | 12701.4795 |  | 12701.4795
95606.8933
45 | NCSU - Wolf Ridge at Centennial Bldg 6 - Lakeview Hall | [16 empty] | NCSU - Wolf Ridge 6 - Lakeview
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 36510.9863 | 36674.9878 | 37328.0029 | 35902.9846 | 34626.0376 | 36817.0166 | 35030.9448 | 35036.0107 | 35270.0195 | 31382.019 | 29618.9575 | 30471.0083 |  |  | 414668.9758 | kwhs | 1415.2652 | MMbtu
| Steam (1000lbs) |  |  | 104.82 | 96.8701 | 192.7798 | 213.35 | 211.9201 | 322.6202 | 230.6999 | 219.1299 | 195 | 141 | 89 | 58 |  |  | 2075.19 | 1000lbs | 2075.19 | MMbtu
| Chilled Water (Dtherms) |  |  | 391 | 326 | 246 | 213 | 222 | 175 | 163 | 222 | 230 | 262 | 333 | 388 |  |  | 3171 | dtherms | 3170.2429 | MMbtu | 6660.6981 | Mmbtu
| Water (CCF) |  |  | 57 | 81 | 70 | 71 | 58 | 57 | 69 | 74 | 72 | 41 | 22 | 20 |  |  | 692 | CCF | 517616 | gallons
| Electricity Cost ($) |  |  | 3139.9448 | 3154.049 | 3210.2083 | 3087.6567 | 2977.8392 | 3166.2634 | 3012.6613 | 3013.0969 | 3033.2217 | 2698.8536 | 2547.2303 | 2650.9777 |  |  | 35692.0029 |  | 35692.0029
| Steam Costs ($) |  |  | 1403.5394 | 1297.0912 | 2581.3212 | 2856.7567 | 2837.6105 | 4319.8839 | 3089.0717 | 2934.1496 | 2611.05 | 1887.99 | 1191.71 | 697.16 |  |  | 27707.3343 |  | 27707.3343
| Chilled Water ($) |  |  | 5462.27 | 4554.22 | 3436.62 | 2975.61 | 3101.34 | 2444.75 | 2277.11 | 3101.34 | 3213.1 | 3660.14 | 4652.01 | 5024.6 |  |  | 43903.11 |  | 43903.11
107302.4472
46 | NCSU - Wolf Ridge at Centennial Bldg 1 - Tower Hall | [16 empty] | NCSU - Wolf Ridge 1 - Tower
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 127816.9556 | 137784.9655 | 139607.8339 | 133268.1427 | 123161.9263 | 138121.1548 | 135089.8437 | 133420.166 | 132151.7944 | 118179.3657 | 125991.9128 | 127717.041 |  |  | 1572311.1024 | kwhs | 5366.2978 | MMbtu
| Steam (1000lbs) |  |  | 152.2565 | 173.6534 | 311.1538 | 351.6681 | 416.4682 | 705.8845 | 594.0203 | 337.192 | 316.9561 | 271.7266 | 182.9589 | 175.4545 |  |  | 3989.3929 | 1000lbs | 3989.3929 | MMbtu
| Chilled water (Dtherms) |  |  | 938.4351 | 831.1128 | 391.9482 | 294.2559 | 312.6807 | 112.0356 | 147.8418 | 333.7402 | 375.0562 | 561.2676 | 888.5132 | 1188.3989 |  |  | 6375.2861 | dtherms | 6373.764 | MMbtu
| Natural Gas (thms) |  |  | 980 | 1242 | 1114 | 1123 | 737 | 1103 | 1196 | 1165 | 1261 | 580 | 1580 |  |  |  | 12081 | therms | 1207.8116 | MMbtu | 15729.4547 | Mmbtu
| Water (CCF) |  |  | 185 | 310 | 280 | 295 | 205 | 255 | 345 | 300 | 330 | 150 | 90 | 85 |  |  | 2830 | CCF | 2116840 | gallons
| Electricity Cost ($) |  |  | 10992.2582 | 11849.507 | 12006.2737 | 11461.0603 | 10591.9257 | 11878.4193 | 11617.7266 | 11474.1343 | 11365.0543 | 10163.4254 | 10835.3045 | 11111.3826 |  |  | 135346.4719 |  | 135346.4719
| Steam Costs ($) |  |  | 2038.7142 | 2325.2186 | 4166.35 | 4708.8352 | 5576.5097 | 9451.7939 | 7953.9317 | 4515.0015 | 4244.0417 | 3638.4187 | 2449.8198 | 2108.9631 |  |  | 53177.5981 |  | 53177.5981
| Chilled Water ($) |  |  | 13109.9378 | 11610.6457 | 5475.5169 | 4110.7544 | 4368.1489 | 1565.138 | 2065.3499 | 4662.3511 | 5239.5344 | 7840.9081 | 12412.5292 | 15389.7661 |  |  | 87850.5804 |  | 87850.5804
| Natural Gas ($) |  |  | 735.37 | 918.08 | 823.2 | 773.14 | 520.2 | 701.82 | 763.72 | 742.69 | 832.05 | 410.25 | 567.77 |  |  |  | 7788.29 |  | 7788.29
276374.6503
47 | UNCG - Spartan Village 1 - Lee | [16 empty] | UNCG - Spartan Village 1
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 87080 | 66054 | 71936 | 55367 | 60814 | 55142 | 84371 | 80199 | 59713 | 60841 | 44681 | 46658 |  |  |  | 772856 | kwhs | 2637.7575 | MMbtu
| Nat Gas (Therms) |  | 451 | 285 | 482 | 470 | 586 | 521 | 378 | 708 | 676 | 630 | 499 | 161 |  |  |  | 5847 | therms | 584.5604 | MMbtu | 3222.3179 | Mmbtu
| Water (gallons) |  | 123420 | 98736 | 168300 | 189244 | 202708 | 132396 | 45628 | 191488 | 178772 | 179520 | 160820 | 5984 |  |  |  | 1677016 | gallons | 1677016 | gallons
| Electricity Cost ($) |  | 7073.86 | 5781.09 | 6135.4 | 5150.7 | 5485.92 | 5136.86 | 6910.1 | 6645.51 | 5393.3 | 5462.25 | 4474.48 | 4595.32 |  |  |  | 68244.79 |  | 68244.79
| Nat Gas Costs ($) |  | 361.68 | 237.22 | 384.92 | 379.77 | 467.28 | 406.12 | 298.86 | 530.01 | 507.13 | 472.19 | 388.46 | 141.5 |  |  |  | 4575.14 |  | 4575.14
72819.93
48 | UNCG - Spartan Village 3 - Haywood | [16 empty] | UNCG - Spartan Village 3
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 34899 | 35352 | 42931 | 35078 | 40217 | 37592 | 55586 | 4273.14 | 39018 | 36408 | 28469 | 34907 |  |  |  | 424730.14 | kwhs | 1449.604 | MMbtu
| Nat Gas (Therms) |  | 82 | 74 | 230 | 242 | 323 | 302 | 201 | 406 | 402 | 355 | 280 | 107 |  |  |  | 3004 | therms | 300.3283 | MMbtu | 1749.9322 | Mmbtu
| Water (gallons) |  | 2992 | 2992 | 79288 | 94996 | 97240 | 68816 | 20944 | 94248 | 92004 | 153340 | 108460 | 16456 |  |  |  | 831776 | gallons | 831776 | gallons
| Electricity Cost ($) |  | 3164.91 | 3189.93 | 3651.01 | 3188.84 | 3505.1 | 3343.56 | 4434.09 | 144 | 3415.07 | 3255.53 | 2770.26 | 3163.79 |  |  |  | 37226.09 |  | 37226.09
| Nat Gas Costs ($) |  | 85.02 | 79.02 | 195.98 | 402.92 | 268.12 | 245.3 | 169.94 | 313.98 | 311.11 | 276.6 | 228.31 | 101.93 |  |  |  | 2678.23 |  | 2678.23
39904.32
49 | UNCG - Spartan Village 4 - Union | [16 empty] | UNCG - Spartan Village 4
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 47471 | 47413 | 58833 | 49656 | 54502 | 48126 | 70496 | 64777 | 46794 | 49320 | 35860 | 39368 |  |  |  | 612616 | kwhs | 2090.8584 | MMbtu
| Nat Gas (Therms) |  | 143 | 120 | 397 | 400 | 486 | 435 | 311 | 602 | 575 | 531 | 396 | 140 |  |  |  | 4536 | therms | 453.4917 | MMbtu | 2544.3501 | Mmbtu
| Water (gallons) |  | 6732 | 17204 | 153340 | 169048 | 183260 | 117436 | 39644 | 169048 | 166056 | 171292 | 148104 | 4488 |  |  |  | 1345652 | gallons | 1345652 | gallons
| Electricity Cost ($) |  | 4231.56 | 4224.36 | 4918.76 | 4382.7 | 4680.93 | 4288.54 | 5643.88 | 5289.3 | 4187.09 | 4341.49 | 3518.75 | 3733.18 |  |  |  | 53440.54 |  | 53440.54
| Nat Gas Costs ($) |  | 130.75 | 113.51 | 321.19 | 326.65 | 391.56 | 342.97 | 250.06 | 454.18 | 434.87 | 397.41 | 313.14 | 126.11 |  |  |  | 3602.4 |  | 3602.4
57042.94
50 | WSSU - Martin-Schexnider Residence Hall | [16 empty] | WSSU - Martin-Schexnider Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 36421 | 49419.8 | 52487 | 51882 | 46191 | 36899 | 49331 | 46857 | 50816 | 52531 | 28283 | 29786 |  |  |  | 530903.8 | kwhs | 1811.9747 | MMbtu
| Steam (Nat Gas in Therms) |  | 2198.592 | 2148.672 | 2502.336 | 3130.368 | 3577.968 | 4276.368 | 5428.464 | 4584.048 | 4105.536 | 3380.832 | 1681.776 | 2077.872 |  |  |  | 39092.832 | therms | 3908.3498 | MMbtu
| Chilled Water (kwh) |  | 72135.6381 | 83933.6689 | 63812.1406 | 36902.6331 | 24943.904 | 34815.6304 | 32632.7794 | 51648.3558 | 44122.9024 | 80607.5124 | 67323.6384 | 83869.4674 |  |  |  | 676748.2709 | kwhs | 2309.7418 | MMbtu | 8030.0664 | Mmbtu
| Water (CCF) |  | 206.02 | 407.3 | 545.46 | 451.07 | 436.15 | 208.76 | 509.03 | 557.9 | 322.89 | 761.14 | 852.68 | 329.01 |  |  |  | 5587.41 | CCF | 4179382.68 | gallons
| Electricity Cost ($) |  | 2593.1752 | 3518.6898 | 3737.0744 | 3693.9984 | 3288.7992 | 2627.2088 | 3512.3672 | 3336.2184 | 3618.0992 | 3740.2072 | 2013.7496 | 2120.7632 |  |  |  | 37800.3506 |  | 37800.3506
| Steam ($) |  | 881.5978 | 885.0581 | 961.9934 | 1166.1149 | 1070.6314 | 1816.2763 | 2313.5237 | 1876.595 | 1489.0157 | 1330.5984 | 701.9856 | 853.224 |  |  |  | 15346.6142 |  | 15346.6142
| Chilled Water($) |  | 5136.0574 | 5976.0772 | 4543.4244 | 2627.4675 | 1776.006 | 2478.8729 | 2323.4539 | 3677.3629 | 3141.5507 | 5739.2549 | 4793.4431 | 5971.5061 |  |  |  | 48184.4769 |  | 48184.4769
101331.4417
51 | Cape Fear Community College - Union Station | [16 empty] | Cape Fear Community College - Union Station
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | 402725 | 382700 | 391650 | 307450 | 295100 | 297825 | 303025 | 227825 | 301550 | 301125 | 337450 | 358325 |  |  |  |  | 3906750 | kwhs | 13333.7378 | MMbtu
| Nat Gas (Therms) | 10246 | 10824 | 9645 | 10015 | 12258 | 12572 | 13897 | 18428 | 15704 | 15110 | 12862 | 10686 |  |  |  |  | 152247 | therms | 15221.065 | MMbtu | 28554.8028 | MMbtu
| Water (CCF) | 593 | 593 | 805 | 559 | 559 | 345 | 345 | 284 | 284 | 305 | 305 | 510 |  |  |  |  | 5487 | CCF | 4104276 | gallons
| Electricity Cost ($) | 30185.84 | 29058.39 | 29743.3 | 22657.74 | 21425.02 | 20909.88 | 19677.22 | 16754.24 | 20472.96 | 20183.69 | 23005.53 | 25594.84 |  |  |  |  | 279668.65 |  | 279668.65
| Nat Gas Costs ($) | 7600.68 | 8138.83 | 7254.87 | 7532.28 | 9213.96 | 9240.74 | 10257.22 | 13219.12 | 10073.26 | 10365.37 | 9408.26 | 7016.14 |  |  |  |  | 109320.73 |  | 109320.73
388989.38
52 | ECU - Smith-Williams Center | [16 empty] | ECU - Smith-Williams Center
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 43438 | 32746 | 46886 | 38945 | 44107 | 33601 | 34815 | 43808 | 40223 | 31585 | 36781 | 38470 |  |  | 465405 | kwhs | 1588.4273 | MMbtu
| Hot Water (MMBtu) | No Meter | [15 empty] | 0 | lbs | 0 | MMbtu
| Chilled Water (ton-hrs) |  |  | 24886.1458 | 20179.375 | 11632.2917 | 10289.9864 | 10582.6866 | 3631.086 | 4267.5363 | 8632.7583 | 13117.6303 | 17418.6778 | 24730 | 29075 |  |  | 178443.1742 | ton-hrs | 2141.3181 | MMbtu | 3729.7454 | MMbtu
| Water (gallons) | Water meter inop - is being replaced | [15 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) |  |  | 3811.6845 | 2873.4615 | 4114.2465 | 3417.4237 | 3870.3892 | 2948.4877 | 3055.0162 | 3844.152 | 3529.5682 | 2771.5837 | 3227.5327 | 3375.7425 |  |  | 40839.2887 |  | 40839.2887
| Hot Water ($) | No Meter | [15 empty] | 0 |  | 0
| Chilled Water ($) | No Data | [15 empty] | 0 |  | 0
40839.2887
53 | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 48640.9912 | 49838.0127 | 49971.9849 | 47547.9736 | 44005.0049 | 47034.0576 | 44637.9395 | 45383.0566 | 45377.9297 | 39505.9814 | 35999.0234 | 27633.0566 |  |  | 525575.0122 | kwhs | 1793.7875 | MMbtu
| Steam (1000lbs) |  |  | 40.4099 | 39.6398 | 98.6099 | 125.6003 | 114.2597 | 267.6306 | 216.4797 | 108.9101 | 106 | 113.58 | 59.3603 | 101.4298 |  |  | 1391.91 | 1000lbs | 1391.91 | MMbtu
| Chilled Water (Dtherms) |  |  | 461.8455 | 376.8711 | 158.752 | 108.4395 | 55.0464 | 37.667 | 56.2261 | 130.2666 | 221.105 | 297.3047 | 443.3623 | 579.4775 |  |  | 2926.3635 | dtherms | 2925.6648 | MMbtu | 6111.3624 | Mmbtu
| Water (CCF) |  |  | 271 | 215 | 137 | 132 | 107 | 103 | 120 | 105 | 106 | 65 | 32 | 33 |  |  | 1426 | CCF | 1066648 | gallons
| Electricity Cost ($) |  |  | 4183.1252 | 4286.0691 | 4297.5907 | 4089.1257 | 3784.4304 | 4044.929 | 3838.8628 | 3902.9429 | 3902.502 | 3397.5144 | 3095.916 | 2404.0759 |  |  | 45227.0841 |  | 45227.0841
| Steam Costs ($) |  |  | 541.088 | 530.777 | 1320.3868 | 1681.7874 | 1529.9375 | 3583.5736 | 2898.6638 | 1458.306 | 1419.34 | 1520.8366 | 794.8338 | 1219.1857 |  |  | 18498.7163 |  | 18498.7163
| Chilled Water ($) |  |  | 6451.9811 | 5264.8892 | 2217.7648 | 1514.8992 | 768.998 | 526.2079 | 785.4783 | 1819.8244 | 3088.8366 | 4153.3465 | 6193.7714 | 7504.2341 |  |  | 40290.2314 |  | 40290.2314
104016.0318
54 | UNCG - Spartan Village Building 2 - Highland | [16 empty] | UNCG - Spartan Village Building 2 - Highland
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 54581 | 60418 | 77125 | 63722 | 69467 | 62518 | 86863 | 85967 | 67171 | 71204 | 59045 | 75766 |  |  |  | 833847 | kwhs | 2845.9198 | MMbtu
| Nat Gas (Therms) |  | 84 | 80 | 376 | 395 | 525 | 490 | 331 | 682 | 656 | 590 | 450 | 374 |  |  |  | 5033 | therms | 503.1798 | MMbtu | 3349.0996 | Mmbtu
| Water (gallons) |  | 5236 | 35904 | 142120 | 203456 | 216920 | 143616 | 64328 | 211684 | 215424 | 227392 | 164560 | 125664 |  |  |  | 1756304 | gallons | 1756304 | gallons
| Electricity Cost ($) |  | 5102.08 | 5449.56 | 6450.17 | 5675.06 | 6023.35 | 5602.06 | 7083.82 | 7031.59 | 5890.34 | 6135.21 | 5396.94 | 6412.21 |  |  |  | 72252.39 |  | 72252.39
| Nat Gas Costs ($) |  | 86.52 | 83.52 | 305.44 | 322.74 | 421.09 | 383.35 | 264.62 | 511.42 | 492.82 | 443.88 | 352.63 | 297.55 |  |  |  | 3965.58 |  | 3965.58
76217.97
55 | UNCC - PORTAL | [16 empty] | UNCC - PORTAL
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 76766 | 80807 | 72885.4 | 70898.8 | 71999.6 | 73852.2 | 75118 | 68766 | 77821 | 78207.2 | 85712.8 | 87298.8 |  |  |  | 920132.8 | kwhs | 3140.4132 | MMbtu
| Nat Gas (Therms) |  | 37 | 35 | 119 | 137 | 213 | 196 | 188 | 206 | 197 | 156 | 119 | 100 |  |  |  | 1703 | therms | 170.2593 | MMbtu
| Chilled Water mmBTU |  | 424 | 343 | 174 | 122 | 163 | 239 | 137 | 148 | 174 | 273.7 | 337.2 | 411.8 |  |  |  | 2946.7 | MMbtu | 2946.7 | MMbtu
| Hot Water mmBTU |  | 135 | 115 | 77 | 147 | 242 | 208 | 314 | 276 | 177 | 156.6 | 152.4 | 113 |  |  |  | 2113 | MMbtu | 2113 | MMbtu | 8370.3726 | Mmbtu
| Water (CF) |  | 150 | 2400 | 4050 | 2530 | 2470 | 1570 | 2750 | 2900 | 3090 | 3060 | 2700 | 1950 |  |  |  | 29620 | CF | 221557.6 | gallons
| Electricity Cost ($) |  | 5124.9359 | 5397.2013 | 4871.2021 | 4332.4971 | 4050.9783 | 4158.5571 | 4253.2513 | 4015.1459 | 4580.6503 | 4487.8769 | 5019.407 | 5638.1402 |  |  |  | 55929.8435 |  | 55929.8435
| Nat Gas Costs ($) |  | 47.93 | 46.52 | 105.38 | 118 | 170.19 | 156.75 | 148.7 | 159.72 | 153.71 | 126.73 | 103.33 | 90.56 |  |  |  | 1427.52 |  | 1427.52
| Chilled Water ($) |  | 2185.7344 | 1780.3731 | 921.0754 | 608.1086 | 852.1228 | 1045.3705 | 815.6555 | 879.3976 | 848.4411 | 885.7708 | 1373.5244 | 1819.8868 |  |  |  | 14015.461 |  | 14015.461
| Hot Water ($) |  | 605.3796 | 670.1277 | 425.2297 | 603.7328 | 814.7807 | 943.1769 | 1373.5986 | 1041.2888 | 717.1333 | 732.643 | 773.0877 | 1010.6758 |  |  |  | 9710.8544 |  | 9710.8544
81083.6788
56 | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 42022.0337 | 41414.0015 | 40640.9912 | 39221.9849 | 38379.0283 | 41500 | 39580.9937 | 40283.9966 | 39995.9717 | 37370.9717 | 36082.0312 | 37901.9775 |  |  | 474393.9819 | kwhs | 1619.1067 | MMbtu
| Steam (1000lbs) |  |  | 51.5101 | 43.5099 | 106.0499 | 143.3102 | 148.63 | 312.6702 | 246.9596 | 128.5202 | 94.5902 | 45.8998 | 25.0396 | 28.8003 |  |  | 1375.49 | 1000lbs | 1375.49 | MMbtu
| Chilled Water (Dtherms) |  |  | 376.0398 | 279.2551 | 93.2671 | 59.8391 | 70.082 | 27.1128 | 33.918 | 86.2432 | 97.4399 | 153.2837 | 310.918 | 437.7861 |  |  | 2025.1848 | dtherms | 2024.7013 | MMbtu | 5019.298 | Mmbtu
| Water (CCF) |  |  | 56 | 78 | 65 | 63 | 56 | 63 | 75 | 72 | 72 | 44 | 22 | 21 |  |  | 687 | CCF | 513876 | gallons
| Electricity Cost ($) |  |  | 3613.8949 | 3561.6041 | 3495.1252 | 3373.0907 | 3300.5964 | 3569 | 3403.9655 | 3464.4237 | 3439.6536 | 3213.9036 | 3103.0547 | 3297.472 |  |  | 40835.7844 |  | 40835.7844
| Steam Costs ($) |  |  | 689.7208 | 582.5974 | 1420.0084 | 1918.9237 | 1990.1559 | 4186.6541 | 3306.7893 | 1720.8854 | 1266.5629 | 614.598 | 335.2805 | 346.1791 |  |  | 18378.3554 |  | 18378.3554
| Chilled Water ($) |  |  | 5253.2759 | 3901.1941 | 1302.9412 | 835.9524 | 979.046 | 378.7657 | 473.834 | 1204.817 | 1361.236 | 2141.3732 | 4343.524 | 5669.3304 |  |  | 27845.29 |  | 27845.29
87059.4298
57 | WSSU - Hill Hall Renovation | [16 empty] | WSSU - Hill Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 36485 | 43096 | 39521 | 42293 | 35250 | 29593 | 39198 | 37209 | 48237 | 48818 | 41529 | 40109 |  |  |  | 481338 | kwhs | 1642.8066 | MMbtu
| Steam (Nat Gas in therms) |  | 1511.532 | 1477.212 | 1720.356 | 2152.128 | 2459.853 | 2940.003 | 3732.069 | 3151.533 | 2822.556 | 2324.322 | 1156.221 | 1428.537 |  |  |  | 26876.322 | therms | 2686.9905 | MMbtu
| Chilled Water (kwh) |  | 49165.6932 | 57206.9108 | 43492.6232 | 25151.8332 | 17001.088 | 23729.3888 | 22241.6168 | 35202.1176 | 30072.9728 | 54939.8928 | 45885.9648 | 57163.1528 |  |  |  | 461253.2548 | kwhs | 1574.2574 | MMbtu | 5904.0545 | Mmbtu
| Water (CCF) |  | 11.4 | 25.6 | 47.4 | 46.1 | 43.1 | 11.4 | 25.1 | 34.8 | 21.3 | 30.7 | 11.7 | 10.4 |  |  |  | 319 | CCF | 238612 | gallons
| Electricity Cost ($) |  | 2597.732 | 3068.4352 | 2813.8952 | 3011.2616 | 2509.8 | 2107.0216 | 2790.8976 | 2649.2808 | 3434.4744 | 3475.8416 | 2956.8648 | 2855.7608 |  |  |  | 34271.2656 |  | 34271.2656
| Steam ($) |  | 606.0985 | 608.4774 | 661.3705 | 801.704 | 736.0591 | 1248.69 | 1590.5475 | 1290.1591 | 1023.6983 | 914.7864 | 482.6151 | 586.5915 |  |  |  | 10550.7973 |  | 10550.7973
| Chilled Water ($) |  | 3500.5974 | 4073.132 | 3096.6748 | 1790.8105 | 1210.4775 | 1689.5325 | 1583.6031 | 2506.3908 | 2141.1957 | 3911.7204 | 3267.0807 | 4070.0165 |  |  |  | 32841.2317 |  | 32841.2317
77663.2946
58 | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 34236.9995 | 36642.9901 | 37118.0115 | 35600.0061 | 33330.9937 | 37289.978 | 32999.0234 | 28028.9917 | 33976.0132 | 31752.9907 | 27868.988 | 29325.0122 |  |  | 398169.9982 | kwhs | 1358.9542 | MMbtu
| Steam (1000lbs) |  |  | 55.778 | 52.872 | 122.9539 | 152.874 | 160.0262 | 297.2637 | 203.8082 | 85.2779 | 149.7198 | 280.0901 | 249.3102 | 212.0899 |  |  | 2022.0639 | 1000lbs | 2022.0639 | MMbtu
| Chilled Water (Dtherms) |  |  | 325.4529 | 237.6841 | 66.032 | 37.0249 | 42.3601 | 13.325 | 16.8 | 68.5488 | 65.865 | 129.9961 | 277.842 | 417.5339 |  |  | 1698.4648 | dtherms | 1698.0593 | MMbtu | 5079.0775 | Mmbtu
| Water (CCF) |  |  | 49 | 83 | 70 | 70 | 53 | 60 | 75 | 66 | 68 | 36 | 11 | 12 |  |  | 653 | CCF | 488444 | gallons
| Electricity Cost ($) |  |  | 2944.382 | 3151.2971 | 3192.149 | 3061.6005 | 2866.4655 | 3206.9381 | 2837.916 | 2410.4933 | 2921.9371 | 2730.7572 | 2396.733 | 2551.2761 |  |  | 34271.9449 |  | 34271.9449
| Steam Costs ($) |  |  | 749.5726 | 819.6 | 1501.154 | 1797.7393 | 1889.4665 | 3289.117 | 2410.4691 | 1078.5613 | 1097.98 | 843.57 | 535.6 | 489.0928 |  |  | 16501.9226 |  | 16501.9226
| Chilled Water ($) |  |  | 4337.3644 | 3703.3495 | 1439.1897 | 1011.3277 | 1102.542 | 409.7105 | 503.0735 | 1063.9165 | 1440.6256 | 1989.7768 | 3558.9257 | 4747.6515 |  |  | 25307.4533 |  | 25307.4533
76081.3207
59 | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 36541.9922 | 32219.9707 | 32330.0171 | 28742.981 | 30244.9951 | 32134.0519 | 30700.9983 | 35416.0042 | 36603.9963 | 32574.9969 | 32916.0004 | 37680.0079 |  |  | 398106.012 | kwhs | 1358.7358 | MMbtu
| Steam (1000lbs) |  |  | 55.778 | 52.872 | 122.9539 | 152.874 | 160.0262 | 297.2637 | 203.8082 | 85.2779 | 149.7198 | 280.0901 | 249.3102 | 212.0899 |  |  | 2022.0639 | 1000lbs | 2022.0639 | MMbtu
| Chilled Water (Dtherms) |  |  | 325.4529 | 237.6841 | 66.032 | 37.0249 | 42.3601 | 13.325 | 16.8 | 68.5488 | 65.865 | 129.9961 | 277.842 | 417.5339 |  |  | 1698.4648 | dtherms | 1698.0593 | MMbtu | 5078.8591 | Mmbtu
| Water (CCF) |  |  | 35 | 12 | 12 | 11 | 9 | 4 | 18 | 20 | 18 | 11 | 22 | 34 |  |  | 206 | CCF | 154088 | gallons
| Electricity Cost ($) |  |  | 3142.6113 | 2770.9175 | 2780.3815 | 2471.8964 | 2601.0696 | 2763.5285 | 2640.2859 | 3045.7764 | 3147.9437 | 2801.4497 | 2830.776 | 3278.1607 |  |  | 34274.797 |  | 34274.797
| Steam Costs ($) |  |  | 746.867 | 707.9563 | 1646.3528 | 2046.9833 | 2142.751 | 3980.3612 | 2728.9919 | 1141.8707 | 2004.7482 | 3750.4066 | 3338.2637 | 2549.3201 |  |  | 26784.8728 |  | 26784.8728
| Chilled Water ($) |  |  | 4546.5767 | 3320.4466 | 922.4668 | 517.2379 | 591.7707 | 186.1496 | 234.6967 | 957.6271 | 920.1339 | 1816.0454 | 3881.4533 | 5407.0645 |  |  | 23301.6693 |  | 23301.6693
84361.3391
60 | Guilford Technical Community College - Aviation Center III Building | [16 empty] | Guilford Technical Community College - Aviation Center III Building
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 44997 | 41362 | 31658 | 33749 | 24073 | 24187 | 26355 | 25999 | 28659 | 31857 | 33705 | 36789 |  |  |  | 383390 | kwhs | 1308.5101 | MMbtu
| Nat Gas (Therms) |  | 117 | 148 | 346 | 663 | 978 | 782 | 1915 | 1732 | 455 | 305 | 232 | 133 |  |  |  | 7806 | therms | 780.4136 | MMbtu | 2088.9237 | Mmbtu
| Water (gallons) |  | 2244 | 7480 | 6732 | 20944 | 4488 | 1496 | 2992 | 3740 | 3740 | 4488 | 2244 | 2992 |  |  |  | 63580 | gallons | 63580 | gallons
| Electricity Cost ($) |  | 3935.36 | 3578.18 | 2741.16 | 2819.97 | 2196.4 | 2245.97 | 2422.46 | 2353.69 | 2509.35 | 2734.19 | 3138.44 | 3332.3 |  |  |  | 34007.47 |  | 34007.47
| Nat Gas Costs ($) |  | 110.51 | 134.5 | 282.95 | 534.5 | 740.98 | 596.41 | 1393.45 | 1262.55 | 338.18 | 246.59 | 193.27 | 121.22 |  |  |  | 5955.11 |  | 5955.11
39962.58
61 | UNCC - Martin Residence Hall | [16 empty] | UNCC - Martin Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 186825 | 183184 | 161861 | 129523 | 130154 | 131739 | 106152 | 121893 | 138818 | 148064 | 134975 | 163897 |  |  |  | 1737085 | kwhs | 5928.6711 | MMbtu
| Nat Gas (Therms) |  | 1390 | 968 | 1881 | 2020 | 2621 | 3487 | 3868 | 4816 | 3136 | 2768 | 2998 | 1892 |  |  |  | 31845 | therms | 3183.7397 | MMbtu | 9112.4108 | Mmbtu
| Water (CF) |  | 26755 | 65503 | 67495 | 65577 | 65709 | 40024 | 50489 | 59711 | 55065 | 68618 | 60481 | 43399 |  |  |  | 668826 | CF | 5002818.48 | gallons
| Electricity Cost ($) |  | 12472.5288 | 12235.0901 | 10817.772 | 7914.9157 | 7322.9717 | 7418.1156 | 6010.4254 | 7117.1536 | 8171.017 | 8496.5707 | 7904.2391 | 10585.1886 |  |  |  | 106465.9882 |  | 106465.9882
| Nat Gas Costs ($) |  | 995.97 | 700.28 | 1340.02 | 1437.41 | 1845.53 | 2419.27 | 2628.74 | 3241.78 | 2118.6 | 1878.35 | 2071.01 | 1319.17 |  |  |  | 21996.13 |  | 21996.13
128462.1182
62 | UNCSA - New Library Building | [16 empty] | UNCSA - New Library Building
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
0
63 | NCA&T - Student Health Center | [16 empty] | NCA&T - Student Health Center
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 32571 | 33777 | 26945 | 20269 | 19441 | 17141 | 17406 | 20710 | 19561 | 20052 | 23035 | 29474 |  |  |  | 280382 | kwhs | 956.9438 | MMbtu
| Nat Gas (Therms) |  | 156 | 324 | 490 | 608 | 962 | 777 | 873 | 1467 | 631 | 491 | 512 | 764 |  |  |  | 8055 | therms | 805.3077 | MMbtu | 1762.2514 | Mmbtu
| Water (CCF) |  | 13 | 12 | 12 | 14 | 12 | 10 | 9 | 14 | 11 | 14 | 12 | 13 |  |  |  | 146 | CCF | 109208 | gallons
| Electricity Cost ($) |  | 2279.97 | 2364.39 | 1886.15 | 1418.83 | 1360.87 | 1199.87 | 1218.42 | 1449.7 | 1369.27 | 1403.64 | 1612.45 | 2063.18 |  |  |  | 19626.74 |  | 19626.74
| Nat Gas Costs ($) |  | 140.5 | 266.46 | 390.91 | 479.39 | 699.74 | 555.61 | 614.81 | 1002.78 | 443.86 | 345.71 | 371.93 | 545.32 |  |  |  | 5857.02 |  | 5857.02
25483.76
64 | UNCG - Campus Police Facility | [16 empty] | UNCG - Campus Police Facility
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 58911 | 50302 | 45092 | 37399 | 37572 | 32861 | 36614 | 34312 | 37139 | 40184 | 35306 | 46821 |  |  |  | 492513 | kwhs | 1680.9469 | MMbtu
| Nat Gas (Therms) |  | 334 | 312 | 374 | 690 | 947 | 1113 | 1514 | 1745 | 1265 | 1100 | 714 | 598 |  |  |  | 10706 | therms | 1070.3444 | MMbtu | 2751.2913 | Mmbtu
| Water (gallons) |  | 4488 | 20196 | 5984 | 12716 | 11220 | 8976 | 5984 | 6732 | 8228 | 748 | 14960 | 6732 |  |  |  | 106964 | gallons | 106964 | gallons
| Electricity Cost ($) |  | 4466.906 | 3967.1217 | 3549.9744 | 3074.1882 | 3082.2608 | 2768.1073 | 3046.6539 | 2911.5943 | 3101.1835 | 3310.5722 | 2988.95 | 3742.7906 |  |  |  | 40010.3028 |  | 40010.3028
| Nat Gas Costs ($) |  | 273.95 | 257.46 | 303.94 | 847.84 | 740.63 | 840.83 | 1125.27 | 1271.84 | 928.47 | 807.32 | 545.69 | 461.65 |  |  |  | 8404.89 |  | 8404.89
48415.1928
65 | UNCC - South Village Dining Facility | [16 empty] | UNCC - South Village Dining Facility
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 125849 | 187598 | 177291 | 187480 | 178291 | 169137 | 164254 | 171012 | 169281.8 | 183634.8 | 141157.6 | 124718.7 |  |  |  | 1979704.9 | kwhs | 6756.7328 | MMbtu
| Nat Gas (Therms) |  | 616 | 1307 | 3678 | 4293 | 5631 | 5544 | 6329 | 7429 | 5019 | 4479 | 3493 | 287 |  |  |  | 48105 | therms | 4809.3515 | MMbtu
| Chilled Water mmBTU |  | 505 | 698 | 535 | 279 | 216 | 236 | 37 | 95 | 280 | 363 | 414 | 505 |  |  |  | 4163 | MMbtu | 4163 | MMbtu
| Hot Water mmBTU |  | 78 | 42 | 46 | 75 | 92 | 52 | 178 | 154 | 97 | 76 | 71 | 48 |  |  |  | 1009 | MMbtu | 1009 | MMbtu | 16738.0843 | Mmbtu
| Water (CF) |  | 7522 | 52053 | 70851 | 65585 | 58110 | 40236 | 48273 | 63411 | 50103 | 65019 | 29891 | 9697 |  |  |  | 560751 | CF | 4194417.48 | gallons
| Electricity Cost ($) |  | 8401.741 | 12529.9067 | 11849.0163 | 11456.5629 | 10031.3471 | 9523.9665 | 9300.2149 | 9985.14 | 9964.1578 | 10537.7813 | 8266.2969 | 8054.8818 |  |  |  | 119901.0132 |  | 119901.0132
| Nat Gas Costs ($) |  | 453.63 | 937.81 | 2599.17 | 3030.11 | 3939.7 | 3833.44 | 4287.26 | 4988.73 | 3377.5 | 3029.09 | 2409.33 | 218.77 |  |  |  | 33104.54 |  | 33104.54
| Chilled Water ($) |  | 2778.6005 | 3778.0623 | 2609.9008 | 1210.3588 | 935.7969 | 1091.4467 | 309.2056 | 553.2258 | 1300.7829 | 1725.4697 | 1950.4153 | 2984.8147 |  |  |  | 21228.0801 |  | 21228.0801
| Hot Water ($) |  | 1375.4908 | 798.1978 | 1160.7583 | 1678.9517 | 1880.4148 | 1111.0622 | 2404.4323 | 2390.7405 | 2138.3959 | 1281.973 | 1344.3389 | 899.4067 |  |  |  | 18464.1631 |  | 18464.1631
192697.7964
66 | UNCG - Dining Hall Renovation | [16 empty] | UNCG - Dining Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 237396 | 296404 | 292447 | 298357 | 271644 | 220151 | 256814 | 261897 | 277239 | 283360 | 213393 | 272438 |  |  |  | 3181540 | kwhs | 10858.596 | MMbtu
| Nat Gas (Therms) |  | 1818 | 1950 | 4943 | 4312 | 5211 | 3111 | 1468 | 4609 | 3236 | 4627 | 3701 | 949 |  |  |  | 39935 | therms | 3992.5465 | MMbtu
| Chilled Water (ton-hrs) |  | Note 2 | Note 2 | 275675.4729 | 188795.4115 | 170295.5094 | 127155.0646 | 122574.7365 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 |  |  |  | 884496.1948 | ton-hrs | 10613.9543 | MMbtu
| Steam Usage (lbs) |  | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 |  |  |  | 0 | MMbtu | 0 | MMbtu | 25465.0969 | Mmbtu
| Water (gallons) |  | 312903.36 | 519515.92 | 662997.28 | 636368.48 | 546099.84 | 196724 | 552203.52 | 589468.88 | 490186.84 | 596380.4 | 108998.56 | 175450.88 |  |  |  | 5387297.96 | gallons | 5387297.96 | gallons
| Electricity Cost ($) |  | 16623.5259 | 21067.1684 | 20124.5868 | 18997.4332 | 17296.5231 | 12952.7384 | 15235.5716 | 15466.9711 | 16570.612 | 16453.4744 | 12697.8832 | 17775.5457 |  |  |  | 201262.0338 |  | 201262.0338
| Nat Gas Costs ($) |  | 1386.58 | 1485.56 | 3729.55 | 3256.46 | 3951.72 | 2309.6 | 1090.16 | 3320.63 | 2338.44 | 3287.62 | 2730.09 | 719.08 |  |  |  | 29605.49 |  | 29605.49
| Chilled Water ($) | No data | [15 empty] | 0 |  | 0
| Hot Water ($) | No data | [15 empty] | 0 |  | 0
230867.5238
67 | WSSU - Center for Design Innovation | [16 empty] | WSSU - Center for Design Innovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 47920 | 46518 | 44399 | 41897 | 44113 | 39258 | 48881 | 54626 | 34601 | 29667 | 26960 | 31878 |  |  |  | 490718 | kwhs | 1674.8205 | MMbtu | 1674.8205 | Mmbtu
| Water (CCF) |  | 0.36 | 0.6 | 1.1 | 0.8 | 0.9 | 1.05 | 0.76 | 0.5 | 0.8 | 0.68 | 2.12 | 1.9 |  |  |  | 11.57 | CCF | 8654.36 | gallons
| Electricity Cost ($) |  | 3837.92 | 3704.59 | 3562.8 | 3704.31 | 3394.29 | 4060.68 | 4435.71 | 3134.97 | 2814.49 | 2638.65 | 2962.44 | 2590.435 |  |  |  | 40841.285 |  | 40841.285
40841.285
68 | FSU - Jones Student Center - Renovation and Addition | [16 empty] | FSU - Jones Student Center - Renovation and Addition
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
69 | UNCSA - Campus Police Facility | [16 empty] | UNCSA - Campus Police Facility
70 | UNCSA - Central Storage Facility | [16 empty] | UNCSA - Central Storage Facility
71 | NCSU - Talley Student Center Renovation and Addition | [16 empty] | NCSU - Talley Student Center Renovation and Addition
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 388256.6608 | 401822.6825 | 401297.6684 | 373326.6197 | 344497.625 | 368648.9014 | 368706.3012 | 377279.1033 | 398226.4342 | 344496.569 | 337694.2513 | 346360.3197 |  |  | 4450613.1364 | kwhs | 15189.9426 | MMbtu
| Nat Gas (Therms) |  |  | 2568 | 3948 | 3553 | 3645 | 2396 | 3635 | 3761 | 3131 | 3758 | 1767 | 1580 | 2029 |  |  | 35771 | therms | 3576.2459 | MMbtu
| Steam (1000lbs) |  |  | 495.7705 | 589.2002 | 940.5303 | 1062.1602 | 1047.5391 | 1897.791 | 1572.4191 | 1016.0755 | 955.7054 | 605.1602 | 462.3594 | 385.1055 |  |  | 11029.8161 | 1000lbs | 11029.8161 | MMbtu
| Chilled Water (Dtherms) |  |  | 2989.47 | 2818.7938 | 984.3447 | 1134.2844 | 1098.0269 | 420.6158 | 312.2264 | 565.5972 | 704.3402 | 746.4359 | 2103.3341 | 3060.2535 |  |  | 16937.723 | dtherms | 16933.679 | MMbtu | 43153.4378 | Mmbtu
| Water (CCF) |  |  | 595.2834 | 713.028 | 726.2019 | 698.2714 | 426.4318 | 615.8422 | 705.9759 | 656.9572 | 816.873 | 395.6912 | 357.4049 | 422.0535 |  |  | 7130.0145 | CCF | 5333250.8125 | gallons
| Electricity Cost ($) |  |  | 33390.0728 | 34556.7507 | 34511.5995 | 32106.0893 | 29626.7957 | 31703.8055 | 31708.7419 | 32446.0029 | 34247.4733 | 29626.7049 | 29041.7056 | 30133.3478 |  |  | 383099.0901 |  | 383099.0901
| Nat Gas Costs ($) |  |  | 1844.29 | 2807.19 | 2513.78 | 2394.85 | 1576.31 | 2136.78 | 2270.12 | 1909.88 | 2378.54 | 1145.41 | 1029.6 | 1307.68 |  |  | 23314.43 |  | 23314.43
| Steam Costs ($) |  |  | 6638.3671 | 7889.3906 | 12593.7004 | 14222.3245 | 14026.548 | 25411.4217 | 21054.6914 | 13605.2507 | 12796.8951 | 8103.0945 | 6190.992 | 4628.9677 |  |  | 147161.6437 |  | 147161.6437
| Chilled Water ($) |  |  | 41762.8959 | 39378.5496 | 13751.2953 | 15845.9536 | 15339.4354 | 5876.0029 | 4361.8033 | 7901.3927 | 9839.6333 | 10427.7092 | 29383.5777 | 39630.2828 |  |  | 233498.5317 |  | 233498.5317
787073.6955
72 | Nash CC - CE and BLET | [16 empty] | Nash CC - CE and BLET
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 68480 | 102000 | 85760 | 62880 | 62400 | 66240 | 46000 | 60080 | 59840 | 82000 | 89840 |  |  |  | 785520 | kwhs | 2680.9798 | MMbtu
| Nat Gas (Therms) |  | 244 | 479 | 724 | 1416 | 2857 | 4292 | 4199 | 6262 | 5811 | 2043 | 1464 | 1040 |  |  |  | 30831 | therms | 3082.3639 | MMbtu | 5763.3437 | MMbtu
| Water (CCF) |  | 320 | 300 | 295 | 33 | 31 | 21 | 13 | 23 | 38 | 31 | 29 | 137 |  |  |  | 1271 | CCF | 950708 | gallons
| Electricity Cost ($) |  | 75.84 | 7149.64 | 10385.95 | 8599.12 | 6849.76 | 6747.39 | 7022.24 | 5657.86 | 6744.76 | 6727.04 | 8476.17 | 8942.58 |  |  |  | 83378.35 |  | 83378.35
| Nat Gas Costs ($) |  | 323.85 | 638.73 | 897.5 | 1458.84 | 2901.99 | 4313.7 | 4221.68 | 6326.38 | 5807.43 | 2093.56 | 1499.91 | 1082.29 |  |  |  | 31565.86 |  | 31565.86
114944.21
73 | UNCSA - Film School Production Design Facility | [16 empty] | UNCSA - Film School Production Design Facility
74 | UNCC - Holshouser Residence Hall Renovation | [16 empty] | UNCC - Holshouser Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0
75 | UNCC - Laurel Residence Hall | [16 empty] | UNCC - Phase XIII Residence Hall
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water mmBTU | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | Mmbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0
76 | ASU - Belk Residence Hall Renovation | [16 empty] | ASU - Belk Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 48240 | 51720 | 54840 | 46320 | 38280 | 31800 | 30720 | 36120 | 35040 | 38760 | 36240 | 28800 |  |  |  | 476880 | kwhs | 1627.5914 | MMbtu
| Steam (lbs) |  | 133472 | 125130 | 108446 | 133472 | 165171.6 | 250260 | 107611.8 | 125964.2 | 80083.2 | 69238.6 | 36704.8 | 35036.4 |  |  |  | 1370590.6 | lbs | 1370.5906 | MMbtu | 2998.182 | MMbtu
| Water (gallons) |  | 44000 | 110000 | 162000 | 144000 | 114000 | 37000 | 94000 | 104000 | 81000 | 110000 | 50000 | 53000 |  |  |  | 1103000 | gallons | 1103000 | gallons
| Electricity Cost ($) |  | 4302.14 | 4611.59 | 4889.04 | 4131.41 | 3416.46 | 2840.22 | 2744.19 | 3062.34 | 2834.92 | 3134.57 | 2931.58 | 2332.28 |  |  |  | 41230.74 |  | 41230.74
| Steam Costs ($) |  | 2803.2 | 2628 | 2277.6 | 2803.2 | 3468.96 | 5256 | 2260.08 | 2645.52 | 1681.92 | 1454.16 | 770.88 | 735.84 |  |  |  | 28785.36 |  | 28785.36
70016.1
77 | UNCW - S & BS Building Renovation | [16 empty] | UNCW - S & BS Building Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (MCF) | [16 empty] | 0 | MCF | 0 | MMbtu
| Heating Hot Water Usage (Mbtu) | [16 empty] | 0 | Mbtu | 0 | MMbtu
| Chilled water (ton-hrs) | [16 empty] | 0 | ton-hrs | 0 | MMbtu | 0 | MMbtu
| Water Usage (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0 |  |  | MCF=1000CF
| Heating Hot Water ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
0
78 | ECU - Gateway Residence Hall (Belk Replacement) | [16 empty] | ECU - Gateway Residence Hall (Belk Replacement)
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 270712.91 | 280841.83 | 227735.55 | 202331.36 | 182200.91 | 160156.85 | 175411.62 | 187663.05 | 196419.51 | 183772.96 | 197344.59 | 271022.3 |  |  | 2535613.44 | kwhs | 8654.0487 | MMbtu
| Steam (lbs) | No data. | [15 empty] | 0 | lbs | 0 | MMbtu | 8654.0487 | MMbtu
| Water (kgallons) |  |  |  | 1059.16 | 851.97 | 709.1 | 532.57 | 202.7 | 667.21 | 525.83 | 724.05 | 488.43 | 213 |  |  |  | 5974.02 | kgallons | 5974020 | gallons
| Electricity Cost ($) |  |  | 23755.0579 | 24643.8706 | 19983.7945 | 17754.5768 | 15988.1299 | 14053.7636 | 15392.3697 | 16467.4326 | 17235.812 | 16126.0772 | 17316.9878 | 23782.2068 |  |  | 222500.0794 |  | 222500.0794
| Steam Costs ($) | No data. | [15 empty] | 0 |  | 0
222500.0794
79 | UNCC - Oak Residence Hall Renovation | [16 empty] | UNCC - Oak Residence Hall Renovation
| Utility | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Chilled Water (MMBtu) | [16 empty] | 0 | MMbtu | 0 | MMbtu
| Hot Water (MMBtu) | [16 empty] | 0 | MMbtu | 0 | MMbtu | 0 | MMbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Hot Water ($) | [16 empty] | 0 |  | 0
0

## 15.16 Raw Meter
2015/2016 Meter Data Summary
1 | ASU - Cone Residence Hall Renovation | [17 empty] | ASU - Cone Residence Hall Renovation
App State - Plemmons, Cone, Summit Utility Data
ELECTRICITY
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 227800 | 214280 | 225000 | 221480 | 190120 | 186400 | 149800 | 169880 | 176080 | 194280 | 202520 | 204080 | 185200 | 182360 | 221240 | 184480 | 192240 | 159400 | 93960 | 150160 | 161304.8 | 184936.24 | 200038.48 | 212508.96 | 164809.92 | 171163.76 | 191234.64 | 181865.2 | 160043.52 | 158691.04 | 162637.92 | 156600.48 | 163100.8 | 182870.4 | 170412.48 | 195797.84 | 172848.4 | 181802.96 | 239736.72 | 193410.72 | 167832.32 | 158616.24 | 151638.48 | 173009.88 | 145604.08 | 167482.6 | 163268.2 | 150024.64 | 154229.68 | 183066.16 | 210823.36 | 180406.32 | 182160 | 137900.16 | 104936.88 | 162981.44 | 159770.64 | 159117.6 | 129846.64 | 117536.08 | 126492.56 | 131062.96 | 176404.16 | 167466.72 | 120254 | 123945.44 | 113920.48 | 131483.76 | 147519.64 | 134698.84 | 141380.32 | 111725.04
315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 30920 | 42883 | 87000 | 89330 | 74095 | 65520 | 51680 | 65760 | 67200 | 67922 | 67325 | 54118 | 61002 | 47297 | 97209 | 82790 | 74640 | 78640 | 59040 | 75280 | 68445.6 | 81539.28 | 78760.56 | 70425.12 | 83354.24 | 95440.72 | 106644.08 | 90944.4 | 79893.44 | 75534.88 | 61110.24 | 77534.56 | 66657.6 | 76348.8 | 74618.56 | 100114.48 | 92674.8 | 96643.12 | 114833.84 | 95351.84 | 74287.04 | 71859.28 | 63800.56 | 84077.36 | 66297.76 | 75581.2 | 80548.4 | 73478.08 | 82502.96 | 96093.52 | 107641.92 | 86785.04 | 87720 | 67851.52 | 49305.36 | 64223.68 | 71256.08 | 72487.2 | 59208.08 | 61667.76 | 85574.32 | 64583.12 | 90419.52 | 94077.84 | 56724 | 57251.68 | 55614.56 | 56960.72 | 68456.08 | 57964.48 | 68523.04 | 67612.88
452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2649.6 | 3444.48 | 4680.96 | 12305.92 | 75868.84 | 94233.52 | 103495.28 | 93234.4 | 90349.04 | 82741.08 | 67491.84 | 96344.96 | 85841.6 | 96620.8 | 94928.96 | 110927.68 | 86316.8 | 107513.92 | 140709.44 | 116877.44 | 96720.64 | 88444.48 | 70200.96 | 106069.76 | 76516.16 | 90139.2 | 97414.4 | 90465.28 | 92359.36 | 103320.32 | 119614.72 | 100688.64 | 105280 | 82288.32 | 57837.76 | 96834.88 | 87713.28 | 101035.2 | 86505.28 | 86756.16 | 95653.12 | 104193.92 | 115816.32 | 104813.44 | 91664 | 78922.88 | 80144.96 | 80595.52 | 79393.28 | 96367.68 | 92576.64 | 83022.08
204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 15780.47 | 14844.63 | 15586.66 | 15343 | 13172.29 | 12914.8 | 11564.69 | 14007.85 | 14518.63 | 16018.03 | 16696.88 | 16825.4 | 15269.98 | 15036 | 18239.12 | 15210.66 | 15849.97 | 13144.46 | 7847.46 | 13989.73 | 14719.5 | 17232.4816 | 18638.2484 | 19799.0325 | 15359.0554 | 15950.5038 | 17818.7533 | 16946.6228 | 14915.3845 | 14789.4924 | 12597.1118 | 14489.8107 | 15087.0346 | 16885.8919 | 15705.2025 | 17941.6669 | 15826.806 | 16105.9043 | 21296.4452 | 17214.78 | 14999.8414 | 14213.2466 | 14023.0962 | 15671.5612 | 12939.7978 | 14853.0983 | 14424.6939 | 13218.7814 | 13631.797 | 16400.7839 | 18881.0127 | 16163.1111 | 16319.824 | 12364.9812 | 9731.4952 | 14281.8277 | 12335.0568 | 14192.4192 | 11589.51 | 10494.7948 | 11291.262 | 11697.6702 | 15729.616 | 14934.8507 | 10736.5003 | 11064.7504 | 10173.2963 | 11123.4077 | 11925.7743 | 10893.0468 | 11431.2475 | 9042.492
315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 2171.15 | 3005.4 | 6059.14 | 6220.42 | 5153.51 | 4559.95 | 4010.19 | 5442.32 | 5560.96 | 5620.45 | 5571.26 | 4483.21 | 5050.33 | 3921.26 | 8033.24 | 6845.34 | 6173.9 | 6503.44 | 4947.92 | 7032.02 | 6267.55 | 7604.4363 | 7345.7837 | 6569.8954 | 7773.3804 | 8898.4197 | 9941.2685 | 8479.8905 | 7451.2315 | 7045.5273 | 4741.0025 | 7186.1608 | 6173.8085 | 7059.0927 | 6888.4709 | 9205.3588 | 8520.2409 | 8598.2021 | 10227.8989 | 8508.3279 | 6649.7124 | 6446.9613 | 5908.2048 | 7624.8998 | 5899.6245 | 6712.9535 | 7134.1322 | 6494.8624 | 7323.4779 | 8600.9712 | 9632.8714 | 7769.2196 | 7852.7635 | 6077.4119 | 4566.7965 | 5603.3298 | 5155.8262 | 6460.4635 | 5279.6211 | 5498.3377 | 7624.2295 | 5757.5883 | 8055.0809 | 8380.3984 | 5058.7196 | 5105.6409 | 4960.0661 | 4814.7908 | 5528.75 | 4683.6496 | 5534.148 | 5460.8274
452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07 | 392.9622 | 890.9878 | 1979.8021 | 7087.7942 | 8797.3266 | 9659.2982 | 8704.2166 | 8435.684 | 7727.5203 | 5244.5257 | 8933.1385 | 7953.5968 | 8926.5754 | 8747.6766 | 10137.8643 | 7867.493 | 9500.1636 | 12473.9959 | 10394.3221 | 8649.9062 | 7939.7522 | 6503.649 | 9620.539 | 6814.5477 | 8000.3182 | 8603.7338 | 7962.9562 | 8147.895 | 9261.5649 | 10717.5459 | 9026.3993 | 9436.6725 | 7382.2669 | 5369.4083 | 8501.8725 | 7829.287 | 9013.9174 | 7721.859 | 7744.1675 | 8535.3185 | 9294.8014 | 10328.333 | 9349.9009 | 8180.5801 | 7047.5987 | 7156.2676 | 6821.3914 | 6424.5957 | 7791.8936 | 7486.5245 | 6716.9106
STEAM
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 519706.6 | 395410.8 | 316161.8 | 308654 | 493012.2 | 947651.2 | 982687.6 | 474659.8 | 401250.2 | 322001.2 | 351198.2 | 274451.8 | 37539 | 404587 | 459644.2 | 527214.4 | 569758.6 | 608966 | 654847 | 620644.8 | 524711.8 | 1393948.2 | 601458.2 | 583105.8 | 642334 | 733261.8 | 677370.4 | 742438 | 886754.6 | 978516.6 | 1117828 | 953490.6 | 797495.2 | 533888 | 681541.4 | 413763.2 | 726588.2 | 731593.4 | 461312.6 | 842542 | 674867.8 | 809174 | 1115325.4 | 682375.6 | 902604.4 | 724919.8 | 504691 | 397913.4 | 470488.8 | 685712.4 | 530551.2 | 722417.2 | 623981.6 | 528048.6 | 789153.2 | 609800.2 | 358706 | 418768.4 | 278622.8 | 205213.2 | 271115 | 312825 | 280291.2 | 475494 | 413763.2 | 394576.6 | 684044 | 611468.6 | 436286.6 | 301146.2 | 307819.8 | 281125.4
315 | Cone Residence Hall Steam Use in Lbs. | 41710 | 62565 | 100104 | 153492.8 | 163503.2 | 216892 | 296141 | 200208 | 166840 | 135140.4 | 94264.6 | 101772.4 | 79249 | 165171.6 | 141814 | 164337.4 | 206881.6 | 207048.44 | 208216.32 | 242752.2 | 211052.6 | 160166.4 | 82585.8 | 59228.2 | 65901.8 | 85922.6 | 171011 | 170176.8 | 208550 | 219394.6 | 291970 | 254848.1 | 229405 | 171011 | 145985 | 52554.6 | 59228.2 | 95933 | 132637.8 | 192700.2 | 214389.4 | 207715.8 | 381229.4 | 204379 | 255265.2 | 206881.6 | 81751.6 | 45881 | 58394 | 104275 | 66736 | 96767.2 | 230239.2 | 235244.4 | 264441.4 | 285296.4 | 182689.8 | 178518.8 | 96767.2 | 83420 | 45881 | 66736 | 118456.4 | 211886.8 | 203544.8 | 191031.8 | 271115 | 274451.8 | 215223.6 | 182689.8 | 118456.4 | 75078
452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210652.184 | 60696.392 | 83545.13 | 170660.636 | 189229.928 | 343473.508 | 382747.644 | 356320.188 | 498426.158 | 606463.4 | 623147.4 | 367048 | 385400.4 | 272783.4 | 340353.6 | 437120.8 | 359540.2 | 462981 | 530551.2 | 387068.8 | 846713 | 451302.2 | 542230 | 358706 | 216892 | 246923.2 | 286964.8 | 338685.2 | 325338 | 401250.2 | 513867.2 | 392074 | 658183.8 | 706567.4 | 491343.8 | 368716.4 | 207715.8 | 210218.4 | 180187.2 | 238581.2 | 311990.8 | 301980.4 | 437120.8 | 430447.2 | 718246.2 | 713241 | 376224.2 | 385400.4 | 283628 | 251928.4
204 & 445 | Plemmons Student Union Total Steam Cost | 22867.09 | 17398.08 | 13911.12 | 13580.78 | 21692.54 | 41696.65 | 43238.25 | 20885.04 | 17655.01 | 14168.05 | 15452.72 | 5764.08 | 788.4 | 8497.2 | 9653.52 | 11072.64 | 11966.16 | 12789.6 | 13753.2 | 13034.88 | 11020.08 | 29275.92 | 12631.92 | 12246.48 | 13490.4 | 15400.08 | 14226.24 | 15592.8 | 18623.76 | 20550.96 | 23476.8 | 20025.36 | 16749.12 | 11212.8 | 14313.84 | 8689.92 | 15259.92 | 15365.04 | 9688.56 | 17695.2 | 14173.68 | 16994.4 | 23424.24 | 14331.36 | 18956.64 | 15224.88 | 10599.6 | 8357.04 | 9881.28 | 14401.44 | 11142.72 | 15172.32 | 13104.96 | 11090.16 | 16573.92 | 12807.12 | 7533.6 | 8795.04 | 5851.68 | 4309.92 | 5694 | 6570 | 5886.72 | 9986.4 | 8689.92 | 8286.96 | 14366.4 | 12842.16 | 9162.96 | 6324.72 | 6464.88 | 5904.24
315 | Cone Residence Hall Steam Costs | 1835.24 | 2752.86 | 4404.58 | 6753.68 | 7194.14 | 9543.25 | 13030.2 | 8809.15 | 7340.96 | 5946.18 | 4147.64 | 2137.44 | 1664.4 | 3468.96 | 2978.4 | 3451.44 | 4344.96 | 4348.46 | 4372.99 | 5098.32 | 4432.56 | 3363.84 | 1734.48 | 1243.92 | 1384.08 | 1804.56 | 3591.6 | 3574.08 | 4380 | 4607.76 | 6132 | 5352.36 | 4818 | 3591.6 | 3066 | 1103.76 | 1243.92 | 2014.8 | 2785.68 | 4047.12 | 4502.64 | 4362.48 | 8006.64 | 4292.4 | 5361.12 | 4344.96 | 1716.96 | 963.6 | 1226.4 | 2190 | 1401.6 | 2032.32 | 4835.52 | 4940.64 | 5553.84 | 5991.84 | 3836.88 | 3749.28 | 2032.32 | 1752 | 963.6 | 1401.6 | 2487.84 | 4450.08 | 4274.88 | 4012.08 | 5694 | 5764.08 | 4520.16 | 3836.88 | 2487.84 | 1576.8
452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4424.15 | 1274.76 | 1754.66 | 3584.31 | 3974.24 | 7213.61 | 8038.46 | 7483.56 | 10467.99 | 14829.71 | 15237.68 | 8975.34 | 9424.1 | 6670.31 | 8322.59 | 10688.82 | 8791.75 | 11321.17 | 12973.44 | 9464.91 | 19687.45 | 11035.59 | 13259.03 | 8771.36 | 5303.61 | 6037.95 | 7017.09 | 8281.79 | 7955.42 | 9811.68 | 12565.47 | 9587.3 | 16094.42 | 17277.53 | 12014.72 | 9016.13 | 5079.23 | 5140.42 | 4406.07 | 5833.97 | 7629.04 | 7384.25 | 10688.82 | 10525.62 | 17563.11 | 17440.72 | 9199.72 | 9424.1 | 6935.49 | 6160.34
WATER & SEWER
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 227000 | 183000 | 225000 | 344000 | 215000 | 164000 | 101000 | 391000 | 303000 | 172000 | 150000 | 200400 | 209000 | 258000 | 385000 | 387000 | 287000 | 151000 | 196000 | 287000 | 294000 | 310000 | 145000 | 210000 | 278000 | 501000 | 459000 | 439000 | 368000 | 227000 | 500000 | 275000 | 181000 | 279000 | 200000 | 219000 | 244000 | 333000 | 427000 | 475900 | 456359 | 390001 | 507000 | 540918 | 183918 | 228589 | 211785 | 332555.459 | 156555 | 317243 | 336965 | 237687 | 161409 | 46000 | 87000 | 105000 | 210475 | 265606 | 163212 | 268457 | 252014 | 322375 | 368441 | 253901 | 185426 | 92000 | 603000 | 290000 | 231245 | 300786 | 189327 | 314358
315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 20000 | 83000 | 139000 | 174000 | 119000 | 108000 | 53000 | 231000 | 190000 | 54000 | 27000 | 6000 | 12000 | 81000 | 174000 | 147000 | 146000 | 93000 | 112000 | 196000 | 164000 | 158000 | 65000 | 18000 | 27000 | 114000 | 166000 | 176000 | 172000 | 77000 | 129000 | 170000 | 133000 | 167000 | 113000 | 86000 | 150000 | 128000 | 190000 | 224300 | 173473 | 80000 | 185000 | 190346 | 140346 | 186283 | 77895 | 33085.173 | 78085 | 159621 | 217355 | 226089 | 160823 | 79000 | 145000 | 180000 | 144325 | 184882 | 51764 | 63279 | 52258 | 146625 | 200127 | 186747 | 161422 | 75000 | 146000 | 183000 | 135515 | 196342 | 105169 | 121026
452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5992 | 32528 | 100152 | 205440 | 208008 | 197736 | 89880 | 160072 | 212288 | 172056 | 219136 | 77896 | 11128 | 11128 | 139528 | 218280 | 274768 | 222064 | 95872 | 182328 | 224152 | 172792 | 245264 | 117648 | 78184.368 | 95304 | 233136 | 314680 | 307224 | 239768 | 115000 | 229000 | 308000 | 400200 | 342512 | 79024 | 74264 | 98728 | 214000 | 289432 | 263352 | 217152 | 96000 | 201000 | 258000 | 203240 | 310872 | 123504 | 88616
204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 2093.02 | 1370.77 | 1567.19 | 2355.2 | 1751.58 | 1112.4 | 702.32 | 2027.61 | 1806.48 | 1939.76 | 1447.95 | 1348.36 | 1842.05 | 1678.25 | 2296 | 3225.7 | 3158.8 | 2030.4 | 1351.5 | 1658.65 | 2290.3 | 3059.25 | 2194.5 | 2112 | 1325.3 | 2441.1 | 4465.2 | 3722.6 | 3126.7 | 2551.7 | 2913.5 | 2847 | 2453.7 | 2472.6 | 3117.5 | 2551.5 | 3401.1 | 3105.9 | 3993.7 | 4651.87 | 5036.2027 | 5584.5 | 5330.1 | 6721.467 | 3878.967 | 2495.034 | 2707.638 | 4023.6185 | 2575.653 | 2496.5935 | 2933.109 | 4512.8395 | 3101.9266 | 1851.3 | 918.7 | 1789 | 2180.185 | 2829.9542 | 2685.5568 | 2739.3533 | 2611.6672 | 2612.7125 | 2888.6671 | 4002.3674 | 2559.3004 | 1803.9 | 2809.4 | 2093.5 | 2539.474 | 2435.251 | 3124.9236 | 3712.1714
315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 91.64 | 273.77 | 1081.38 | 1295.16 | 1062.99 | 859.46 | 529.02 | 1387.37 | 1148.25 | 1097.17 | 662.24 | 199.4 | 114.9 | 301.5 | 861.15 | 1559.7 | 1444.65 | 1232.2 | 1012.75 | 1203.2 | 1681.8 | 1794.6 | 1224.5 | 535.15 | 221.45 | 602.15 | 1095.55 | 1536.15 | 1584.55 | 1415.95 | 969.05 | 1568.75 | 1608.35 | 1646.05 | 1822.75 | 1223.75 | 1805.75 | 1544.15 | 1671.75 | 2134.24 | 2191.1569 | 1597.75 | 1582.75 | 2376.999 | 2081.999 | 1987.448 | 1603.436 | 599.4195 | 440.441 | 1092.0445 | 1432.873 | 3212.0065 | 2584.3402 | 1804.45 | 1124.25 | 2339.75 | 1863.145 | 1993.0774 | 1524.0396 | 725.8751 | 553.8384 | 835.9875 | 1462.8937 | 2601.4278 | 2071.6788 | 1566 | 1072.3 | 1747.6 | 1924.178 | 1536.197 | 1960.6492 | 1658.5158
452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.74 | 100.84 | 2320.58 | 6556.74 | 603.22 | 573.43 | 413.45 | 592.27 | 955.3 | 722.64 | 1604.7 | 1894.11 | 568.17 | 194.27 | 770.52 | 1875.28 | 2525.21 | 2638.7704 | 1900.79 | 1666.76 | 2584.974 | 2497.664 | 2537.948 | 2148.846 | 1009.822 | 633.346 | 1406.862 | 1949.418 | 4373.154 | 3588.0332 | 2602.75 | 1725.65 | 3868.55 | 3882.17 | 4533.0684 | 2690.0036 | 902.6716 | 702.3944 | 1252.7 | 2029.2392 | 3633.3048 | 2831.1208 | 2061.2 | 1427.8 | 2430.1 | 2773.848 | 2317.552 | 2771.3272 | 1451.5128
2 | UNCC - Prospector Hall Renovation Phase II | 2011-12-01: UNCC - Prospector Hall Renovation Phase II
| Prospector Hall Renovation | 2010-08-01: 06-07223-01A
|  | Jul '15 | Aug '15 | Sep '15 | Oct '15 | Nov '15 | Dec '15 | Jan '16 | Feb '16 | Mar '16 | Apr '16 | May '16 | Jun '16
Consumption
| Electric (KWH) | 2010-07-01: 68670; 2010-08-01: 73539; 2010-09-01: 87810; 2010-10-01: 96658.1; 2010-11-01: 90305.9; 2010-12-01: 85231; 2011-01-01: 88739; 2011-02-01: 83201; 2011-03-01: 94822.2; 2011-04-01: 93120; 2011-05-01: 88476.7; 2011-06-01: 82379.9
| Nat Gas (Therms) | 2010-07-01: 1044; 2010-08-01: 1159; 2010-09-01: 1776; 2010-10-01: 1873; 2010-11-01: 2255; 2010-12-01: 2066; 2011-01-01: 2594; 2011-02-01: 3202; 2011-03-01: 2402; 2011-04-01: 1922; 2011-05-01: 1608; 2011-06-01: 788
| Water (CF) | 2010-07-01: 8689; 2010-08-01: 11420; 2010-09-01: 16370; 2010-10-01: 14780; 2010-11-01: 11420; 2010-12-01: 7375; 2011-01-01: 8690; 2011-02-01: 10980; 2011-03-01: 10430; 2011-04-01: 19410; 2011-05-01: 6230; 2011-06-01: 3760
| CHW BTUX10^6 | 2010-07-01: 935; 2010-08-01: 865; 2010-09-01: 703; 2010-10-01: 243; 2010-11-01: 165; 2010-12-01: 171; 2011-01-01: 11; 2011-02-01: 45; 2011-03-01: 227; 2011-04-01: 311; 2011-05-01: 447; 2011-06-01: 655
Costs $
| Electric | 2010-07-01: 4584.4429; 2010-08-01: 4911.7624; 2010-09-01: 5868.6686; 2010-10-01: 5906.6012; 2010-11-01: 5080.9622; 2010-12-01: 4799.2881; 2011-01-01: 5024.4851; 2011-02-01: 4857.9844; 2011-03-01: 5581.3641; 2011-04-01: 5343.6397; 2011-05-01: 5181.2631; 2011-06-01: 5320.456
| Nat Gas | 2010-07-01: 753.53; 2010-08-01: 834.11; 2010-09-01: 1233.44; 2010-10-01: 1334.41; 2010-11-01: 1590.89; 2010-12-01: 1442.35; 2011-01-01: 1770.16; 2011-02-01: 2162.73; 2011-03-01: 1627.88; 2011-04-01: 1312.38; 2011-05-01: 1121; 2011-06-01: 562.26
| Water | 2010-07-01: 647.6186; 2010-08-01: 863.0414; 2010-09-01: 1253.2063; 2010-10-01: 1211.0968; 2010-11-01: 942.6225; 2010-12-01: 632.1002; 2011-01-01: 805.3182; 2011-02-01: 910.2529; 2011-03-01: 856.8407; 2011-04-01: 1568.2432; 2011-05-01: 491.9156; 2011-06-01: 246.9166
| CHW | 2010-07-01: 6221.5035; 2010-08-01: 4679.6377; 2010-09-01: 3519.7932; 2010-10-01: 1246.9226; 2010-11-01: 554.6476; 2010-12-01: 502.6282; 2011-01-01: 51.1746; 2011-02-01: 541.1947; 2011-03-01: 2138.5115; 2011-04-01: 1073.8311; 2011-05-01: 1518.7688; 2011-06-01: 2002.2446
Metered data is whole building data - not just the partial renovation
Metered data includes process loads
Prospector Gets Chill Water from adjacent building - Costs are assumed to be the same as RUP1 CHW costs
3 | UNCC - Miltimore Residence Hall | 2011-12-01: UNCC - Miltimore Residence Hall
| Miltimore Residence Hall | 2010-08-01: 05-06656-01A
| 185544 | 2010-07-01: Jul '15; 2010-08-01: Aug '15; 2010-09-01: Sep '15; 2010-10-01: Oct '15; 2010-11-01: Nov '15; 2010-12-01: Dec '15; 2011-01-01: Jan '16; 2011-02-01: Feb '16; 2011-03-01: Mar '16; 2011-04-01: Apr '16; 2011-05-01: May '16; 2011-06-01: Jun '16
Consumption
| Electric (KWH) | 2010-07-01: 181002; 2010-08-01: 164911; 2010-09-01: 153590; 2010-10-01: 135645.7; 2010-11-01: 141852.6; 2010-12-01: 130677.7; 2011-01-01: 133798; 2011-02-01: 129641.4; 2011-03-01: 161554; 2011-04-01: 166720.5; 2011-05-01: 116672.5; 2011-06-01: 113155
| Nat Gas (Therms) | 2010-07-01: 2307; 2010-08-01: 2201; 2010-09-01: 2860; 2010-10-01: 2962; 2010-11-01: 4916; 2010-12-01: 6029; 2011-01-01: 8502; 2011-02-01: 7404; 2011-03-01: 6551; 2011-04-01: 5382; 2011-05-01: 3886; 2011-06-01: 1952
| Water (CF) | 2010-07-01: 68321; 2010-08-01: 52430; 2010-09-01: 84445; 2010-10-01: 61521; 2010-11-01: 45121; 2010-12-01: 35543; 2011-01-01: 59045; 2011-02-01: 72881; 2011-03-01: 49465; 2011-04-01: 56214; 2011-05-01: 36023; 2011-06-01: 32652
Costs $
| Electric | 2010-07-01: 12083.7824; 2010-08-01: 11014.6134; 2010-09-01: 10264.9904; 2010-10-01: 8289.0628; 2010-11-01: 7981.1806; 2010-12-01: 7358.3547; 2011-01-01: 7575.7677; 2011-02-01: 7569.5713; 2011-03-01: 9509.289; 2011-04-01: 9567.1636; 2011-05-01: 6832.4307; 2011-06-01: 7308.0472
| Nat Gas | 2010-07-01: 1638.51; 2010-08-01: 1564.24; 2010-09-01: 2026; 2010-10-01: 2097.47; 2010-11-01: 3442.25; 2010-12-01: 4166.87; 2011-01-01: 5751.7; 2011-02-01: 4972.02; 2011-03-01: 4401.74; 2011-04-01: 3635.34; 2011-05-01: 2677.93; 2011-06-01: 1360.31
| Water | 2010-07-01: 5092.1798; 2010-08-01: 3962.2818; 2010-09-01: 6464.6921; 2010-10-01: 5041.1288; 2010-11-01: 3724.3494; 2010-12-01: 3046.3371; 2011-01-01: 5471.8085; 2011-02-01: 6041.9075; 2011-03-01: 4063.6264; 2011-04-01: 4541.8455; 2011-05-01: 2844.346; 2011-06-01: 2144.2346
| BTU/GSF | 2010-07-01: 4571.8472; 2010-08-01: 4218.8178; 2010-09-01: 4365.8058; 2010-10-01: 4090.7986; 2010-11-01: 5258.0578; 2010-12-01: 5652.4184; 2011-01-01: 7042.6356; 2011-02-01: 6374.4258; 2011-03-01: 6501.5427; 2011-04-01: 5966.5112; 2011-05-01: 4239.8923; 2011-06-01: 3132.868; 2011-07-01: 61415.6211
4 | NCCU - Nursing Building | 2011-12-01: NCCU - Nursing Building
Agency - Building Name: NCCU - Chidley North
| Utility | 2010-07-01: Jun-15; 2010-08-01: 2015-07-01; 2010-09-01: 2015-08-01; 2010-10-01: 2015-09-01; 2010-11-01: 2015-10-01; 2010-12-01: 2015-11-01; 2011-01-01: 2015-12-01; 2011-02-01: 2016-01-01; 2011-03-01: 2016-02-01; 2011-04-01: 2016-03-01; 2011-05-01: 2016-04-01; 2011-06-01: 2016-05-01; 2011-07-01: 2016-06-01; 2011-08-01: 2016-07-01; 2011-09-01: 2016-08-01; 2011-10-01: 2016-09-14
| Electricity (KWhs) | 2010-07-01: 85624; 2010-08-01: 106024; 2010-09-01: 108048; 2010-10-01: 105904; 2010-11-01: 95632; 2010-12-01: 87664; 2011-01-01: 64040; 2011-02-01: 68928; 2011-03-01: 69072; 2011-04-01: 106000; 2011-05-01: 131912; 2011-06-01: 116648; 2011-07-01: 53704; 2011-08-01: 147744; 2011-09-01: 31128
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) | 2010-07-01: 275; 2010-08-01: 299; 2010-09-01: 299; 2010-10-01: 1048; 2010-11-01: 1363; 2010-12-01: 1305; 2011-01-01: 1441; 2011-02-01: 413; 2011-03-01: 1758; 2011-04-01: 1804; 2011-05-01: 1243; 2011-06-01: 1424; 2011-07-01: 277; 2011-08-01: 289
| Water (CCF) | 2010-07-01: 120430; 2010-08-01: 127683; 2010-09-01: 150658; 2010-10-01: 189718; 2010-11-01: 177482; 2010-12-01: 150751; 2011-01-01: 121168; 2011-02-01: 114305; 2011-03-01: 113391; 2011-04-01: 312047; 2011-05-01: 136449; 2011-06-01: 35873; 2011-07-01: 23436; 2011-08-01: 36393
| Electricity Cost ($) | 2010-07-01: 5281; 2010-08-01: 6594.96; 2010-09-01: 6720.85; 2010-10-01: 6587.49; 2010-11-01: 5948.55; 2010-12-01: 5452.92; 2011-01-01: 3983.45; 2011-02-01: 4287.49; 2011-03-01: 4296.45; 2011-04-01: 6593.46; 2011-05-01: 8205.25; 2011-06-01: 7255.79; 2011-07-01: 3340.52; 2011-08-01: 9190.04; 2011-09-01: 1936.24
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 2010-07-01: 229; 2010-08-01: 247.28; 2010-09-01: 246.83; 2010-10-01: 782.85; 2010-11-01: 1002.29; 2010-12-01: 945.52; 2011-01-01: 977.62; 2011-02-01: 305.32; 2011-03-01: 1088.3; 2011-04-01: 1115.43; 2011-05-01: 794.14; 2011-06-01: 932.98; 2011-07-01: 208.18; 2011-08-01: 216.39
Note: August 2016 is a partial bill (up to 08/08/2016)
5 | NCCU - Chidley Residence Hall | 2011-12-01: NCCU - Chidley Residence Hall
Agency - Building Name: NCCU - Nursing Building
| Utility | 2010-07-01: Jun-15; 2010-08-01: 2015-07-01; 2010-09-01: 2015-08-01; 2010-10-01: 2015-09-01; 2010-11-01: 2015-10-01; 2010-12-01: 2015-11-01; 2011-01-01: 2015-12-01; 2011-02-01: 2016-01-01; 2011-03-01: 2016-02-01; 2011-04-01: 2016-03-01; 2011-05-01: 2016-04-01; 2011-06-01: 2016-05-01; 2011-07-01: 2016-06-01; 2011-08-01: 2016-07-01; 2011-09-01: 2016-08-01; 2011-10-01: 2016-09-14
| Electricity (KWhs) | 2010-07-01: 71978; 2010-08-01: 85948; 2010-09-01: 85846; 2010-10-01: 75525; 2010-11-01: 65435; 2010-12-01: 63722; 2011-01-01: 50560; 2011-02-01: 44272; 2011-03-01: 51578; 2011-04-01: 67404; 2011-05-01: 69770; 2011-06-01: 75377; 2011-07-01: 85576; 2011-08-01: 101534; 2011-09-01: 24528
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) | 2010-07-01: 44; 2010-08-01: 42; 2010-09-01: 36; 2010-10-01: 40; 2010-11-01: 48; 2010-12-01: 42; 2011-01-01: 44; 2011-02-01: 50; 2011-03-01: 44; 2011-04-01: 45; 2011-05-01: 49; 2011-06-01: 45; 2011-07-01: 51; 2011-08-01: 39
| Water (CCF) | 2010-07-01: 13138; 2010-08-01: 12157; 2010-09-01: 13940; 2010-10-01: 11790; 2010-11-01: 5472; 2010-12-01: 5359; 2011-01-01: 7986; 2011-02-01: 18983; 2011-03-01: 3178; 2011-04-01: 13821; 2011-05-01: 20524; 2011-06-01: 20347; 2011-07-01: 30042; 2011-08-01: 29190
| Electricity Cost ($) | 2010-07-01: 4439; 2010-08-01: 5346.18; 2010-09-01: 5339.83; 2010-10-01: 4697.84; 2010-11-01: 4070.22; 2010-12-01: 3963.67; 2011-01-01: 3144.96; 2011-02-01: 2753.83; 2011-03-01: 3208.28; 2011-04-01: 4192.7; 2011-05-01: 4339.87; 2011-06-01: 4688.64; 2011-07-01: 5323.04; 2011-08-01: 6315.67; 2011-09-01: 1525.7
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 2010-07-01: 52.39; 2010-08-01: 50.84; 2010-09-01: 46.19; 2010-10-01: 49.24; 2010-11-01: 55.33; 2010-12-01: 50.47; 2011-01-01: 49.86; 2011-02-01: 53.7; 2011-03-01: 47.53; 2011-04-01: 48.18; 2011-05-01: 51.03; 2011-06-01: 49.5; 2011-07-01: 53.61; 2011-08-01: 45.4
Note: August 2016 is a partial bill (up to 08/08/2016)
6 | UNC-CH - Loudermilk | 2011-12-01: UNC-CH - Loudermilk
| Loudermilk Center of Excellence (375) | 2010-09-01: Aug 15 - Jul 16
Energy and Water Usage (Acct. #01012081)
| UTILITY | 2010-07-01: 2015-08-01; 2010-08-01: 2015-09-01; 2010-09-01: 2015-10-01; 2010-10-01: 2015-11-01; 2010-11-01: 2015-12-01; 2010-12-01: 2016-01-01; 2011-01-01: 2016-02-01; 2011-02-01: 2016-03-01; 2011-03-01: 2016-04-01; 2011-04-01: 2016-05-01; 2011-05-01: 2016-06-01; 2011-06-01: 2016-07-01
Consumption:
| ELECTRIC (kWhs) | 2010-07-01: 151445; 2010-08-01: 168628; 2010-09-01: 183405; 2010-10-01: 162532; 2010-11-01: 200968; 2010-12-01: 168714; 2011-01-01: 143137; 2011-02-01: 187325; 2011-03-01: 151869; 2011-04-01: 161325; 2011-05-01: 187114; 2011-06-01: 157789
| STEAM (MLBS) | 2010-07-01: 676; 2010-08-01: 558; 2010-09-01: 557; 2010-10-01: 498; 2010-11-01: 478; 2010-12-01: 524; 2011-01-01: 1005; 2011-02-01: 693; 2011-03-01: 383; 2011-04-01: 441; 2011-05-01: 535; 2011-06-01: 473
| CHILLED WATER (Ton-Hrs.) | 2010-07-01: 167354; 2010-08-01: 155825; 2010-09-01: 141384; 2010-10-01: 38112; 2010-11-01: 26509; 2010-12-01: 34916; 2011-01-01: 7; 2011-02-01: 1984; 2011-03-01: 22678; 2011-04-01: 33930; 2011-05-01: 80849; 2011-06-01: 138870
| NATURAL GAS (Therms) | 2010-07-01: 159; 2010-08-01: 201; 2010-09-01: 366; 2010-10-01: 434; 2010-11-01: 513; 2010-12-01: 311; 2011-01-01: 240; 2011-02-01: 329; 2011-03-01: 358; 2011-04-01: 258; 2011-05-01: 310; 2011-06-01: 169
| WATER (kGal) | 2010-07-01: 391; 2010-08-01: 328; 2010-09-01: 372; 2010-10-01: 261; 2010-11-01: 161; 2010-12-01: 134; 2011-01-01: 161; 2011-02-01: 176; 2011-03-01: 190; 2011-04-01: 202; 2011-05-01: 155; 2011-06-01: 152
| SEWER (kGal) | 2010-07-01: 391; 2010-08-01: 328; 2010-09-01: 372; 2010-10-01: 261; 2010-11-01: 161; 2010-12-01: 134; 2011-01-01: 161; 2011-02-01: 176; 2011-03-01: 190; 2011-04-01: 202; 2011-05-01: 155; 2011-06-01: 152
| STORMWATER (ksf) | 2010-07-01: 135; 2010-08-01: 135; 2010-09-01: 135; 2010-10-01: 135; 2010-11-01: 135; 2010-12-01: 135; 2011-01-01: 135; 2011-02-01: 135; 2011-03-01: 135; 2011-04-01: 135; 2011-05-01: 135; 2011-06-01: 135
Costs:
| ELECTRIC ($) | 2010-07-01: 9086.7; 2010-08-01: 9864.74; 2010-09-01: 11664.56; 2010-10-01: 9946.96; 2010-11-01: 9465.59; 2010-12-01: 8520.06; 2011-01-01: 9060.57; 2011-02-01: 9628.51; 2011-03-01: 9294.38; 2011-04-01: 9372.98; 2011-05-01: 8906.63; 2011-06-01: 9498.9
| STEAM ($) | 2010-07-01: 7594.25; 2010-08-01: 6268.63; 2010-09-01: 6257.39; 2010-10-01: 5594.58; 2010-11-01: 5369.9; 2010-12-01: 5886.67; 2011-01-01: 11290.27; 2011-02-01: 7785.23; 2011-03-01: 4302.66; 2011-04-01: 4954.24; 2011-05-01: 6010.24; 2011-06-01: 5202.91
| CHILLED WATER ($) | 2010-07-01: 16082.72; 2010-08-01: 14974.78; 2010-09-01: 13587; 2010-10-01: 3662.56; 2010-11-01: 2547.51; 2010-12-01: 3355.43; 2011-01-01: 0.67; 2011-02-01: 190.66; 2011-03-01: 2179.36; 2011-04-01: 3260.67; 2011-05-01: 7769.59; 2011-06-01: 12706.61
| NATURAL GAS ($) | 2010-07-01: 103.76; 2010-08-01: 131.17; 2010-09-01: 521.9; 2010-10-01: 618.32; 2010-11-01: 704.68; 2010-12-01: 411.34; 2011-01-01: 305.94; 2011-02-01: 402.56; 2011-03-01: 438.04; 2011-04-01: 322.76; 2011-05-01: 396.3; 2011-06-01: 108.02
| WATER ($) | 2010-07-01: 3249.21; 2010-08-01: 2725.68; 2010-09-01: 3091.32; 2010-10-01: 1140.57; 2010-11-01: 703.57; 2010-12-01: 585.58; 2011-01-01: 703.57; 2011-02-01: 769.12; 2011-03-01: 830.3; 2011-04-01: 882.74; 2011-05-01: 1288.05; 2011-06-01: 1263.12
| SEWER ($) | 2010-07-01: 2658.8; 2010-08-01: 2230.4; 2010-09-01: 2529.6; 2010-10-01: 1774.8; 2010-11-01: 1094.8; 2010-12-01: 911.2; 2011-01-01: 1094.8; 2011-02-01: 1196.8; 2011-03-01: 1292; 2011-04-01: 1373.6; 2011-05-01: 1054; 2011-06-01: 1033.6
| STORMWATER ($) | 2010-07-01: 324; 2010-08-01: 324; 2010-09-01: 324; 2010-10-01: 324; 2010-11-01: 324; 2010-12-01: 324; 2011-01-01: 324; 2011-02-01: 324; 2011-03-01: 324; 2011-04-01: 324; 2011-05-01: 324; 2011-06-01: 340.2
7 | DoAg&CS - Davis Event Center | 2011-12-01: DoAg&CS - Davis Arena
NC Department of Agriculture & Consumer Services - Western Ag Center - Davis Events Center
| Utility | 2010-07-01: 2015-07-01; 2010-08-01: 2015-08-01; 2010-09-01: 2015-09-01; 2010-10-01: 2015-10-01; 2010-11-01: 2015-11-01; 2010-12-01: 2015-12-01; 2011-01-01: 2016-01-01; 2011-02-01: 2016-02-01; 2011-03-01: 2016-03-01; 2011-04-01: 2016-04-01; 2011-05-01: 2016-05-01; 2011-06-01: 2016-06-01; 2011-07-01: Annual Total
| Electricity Usage (KWhs) | 2010-07-01: 41520; 2010-08-01: 43760; 2010-09-01: 43320; 2010-10-01: 58920; 2010-11-01: 42800; 2010-12-01: 34560; 2011-01-01: 29680; 2011-02-01: 27280; 2011-03-01: 43440; 2011-04-01: 3900; 2011-05-01: 41360; 2011-06-01: 46600; 2011-07-01: 457140
| Water Usage (gallons) | 2010-07-01: 44880; 2010-08-01: 17204; 2010-09-01: 166804; 2010-10-01: 65824; 2010-11-01: 30668; 2010-12-01: 28424; 2011-01-01: 77044; 2011-02-01: 48620; 2011-03-01: 55352; 2011-04-01: 22440; 2011-05-01: 41140; 2011-06-01: 40392; 2011-07-01: 638792
| Natural Gas Therms | 2010-07-01: 315; 2010-08-01: 116; 2010-09-01: 77; 2010-10-01: 260; 2010-11-01: 256; 2010-12-01: 1382; 2011-01-01: 2629; 2011-02-01: 1370; 2011-03-01: 5683; 2011-04-01: 1508; 2011-05-01: 1463; 2011-06-01: 533; 2011-07-01: 15592
| Elecricity Cost ($) | 2010-07-01: 4459.02; 2010-08-01: 4658.28; 2010-09-01: 4596.15; 2010-10-01: 5791.06; 2010-11-01: 4348.2; 2010-12-01: 3926.63; 2011-01-01: 3285.66; 2011-02-01: 3175.9; 2011-03-01: 4419.01; 2011-04-01: 4245.91; 2011-05-01: 4427; 2011-06-01: 4966.67; 2011-07-01: 52299.49
| Water-Sewer Costs ($) | 2010-07-01: 1231.94; 2010-08-01: 950.74; 2010-09-01: 2420.74; 2010-10-01: 1444.74; 2010-11-01: 1087.54; 2010-12-01: 1079.74; 2011-01-01: 1558.74; 2011-02-01: 1269.94; 2011-03-01: 1338.34; 2011-04-01: 1003.94; 2011-05-01: 1193.94; 2011-06-01: 1206.32; 2011-07-01: 15786.66
| Natural Gas ($) | 2010-07-01: 143.98; 2010-08-01: 100.21; 2010-09-01: 72.4; 2010-10-01: 202.82; 2010-11-01: 191.27; 2010-12-01: 878.2; 2011-01-01: 1607.87; 2011-02-01: 803.64; 2011-03-01: 3151.46; 2011-04-01: 885.69; 2011-05-01: 894.51; 2011-06-01: 278.03; 2011-07-01: 9210.08
Notes: Davis Arena & Virginia Boone Bldg on same water meter
8 | NCSU - Student Health Center Addition and Renovation | 2011-12-01: NCSU - Student Health Center Addition and Renovation
NCSU - Student Health Center Addition and Renovation
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 68624 | 67811 | 62411 | 53655 | 52772 | 55746 | 54644 | 57649 | 55716 | 55280 | 57553 | 53503 |  | 695364 | kwh |  | 2370.8519 | MMbtu
| Chilled Water (Dtherms) |  | 801.25 | 669.8 | 226.01 | 128.13 | 144.41 | 24.11 | 49.41 | 185.8 | 224.7 | 345.7 | 580.5 | 617 |  | 3996.82 | dthrms |  | 3996.82 | MMbtu
| Steam (1,000 lbs) |  | 295 | 304 | 355 | 316 | 314 | 433 | 365 | 305 | 287 | 241 | 78 | 373 |  | 3666 | 1000 lbs |  | 3666 | MMbtu
| Water (CCF) |  | 50.0949 | 48.5713 | 50.2727 | 49.5519 | 39.9971 | 41.561 | 48 | 55.7 | 62 | 48 | 38 | 40.4396 |  | 572.1887 | CCF |  | 427997.122 | gallons
| Electric Cost ($) |  | 5901.664 | 5831.746 | 5367.346 | 4614.33 | 4538.392 | 4794.156 | 4699.384 | 4957.814 | 4791.576 | 4754.08 | 4949.558 | 4654.761 |  | 59854.807 | $
| Chilled Water Cost ($) |  | 11193.4625 | 9357.106 | 3157.3597 | 1789.9761 | 2017.4077 | 336.8167 | 690.2577 | 2595.626 | 3139.059 | 4829.429 | 8109.585 | 7990.15 |  | 55206.2354 | $
| Steam Cost ($) |  | 3950.05 | 4070.56 | 4753.45 | 4231.24 | 4204.46 | 5797.87 | 4887.35 | 4083.95 | 3842.93 | 3226.99 | 1044.42 | 4483.46 |  | 48576.73 | $
| Water Cost ($) |  | 460.8733 | 446.8563 | 462.5092 | 455.8779 | 367.9735 | 382.3614 | 441.6 | 512.44 | 570.4 | 441.6 | 349.6 | 377.3012 |  | 5269.3929 | $
9 | ECSU - Gilchrist Ed & Psych Bldg | [17 empty] | ECSU - Gilchrist Ed & Psych Bldg
UNC - ECSU - Gilchrist Education & Psychology Building
| Utility | Jun-15 | 2015-07-15 | 2015-08-15 | 2015-09-15 | 2015-10-15 | 2015-11-15 | 2015-12-15 | 2016-01-16 | 2016-02-16 | 2016-03-16 | 2016-04-16 | 2016-05-16 | 2016-06-16 | 2016-07-16 | 2016-08-16 | 2016-09-14
| Electricity (KWhs) |  | 57984 | 59712 | 61440 | 54720 | 48768 | 35904 | 35904 | 55104 | 67008 | 56256 | 78528 | 130368
| Steam (lbs) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water (Dtherms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas (Therms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water (CCF)
| Electricity Cost ($) |  | 6660.13 | 7047.97 | 6843.95 | 6044.45 | 5473.96 | 3779.56 | 3434.3 | 4934.12 | 6173.75 | 6107.88 | 7718.11 | 12387.32
| Steam Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | DoAg&CS - SENC Ag Center | [17 empty] | DoAg&CS - SENC Ag Center
NC Department of Agriculture & Consumer Services - Southeastern Ag Center - Multi-purpose Pavilion
| Utility | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | Annual Total
| Electricity Usage (KWhs) | 52360 | 43759 | 44567 | 53275 | 42179 | 32440 | 44607 | 36358 | 250 | 51400 | 47064 | 56146 | 504405
| Water Usage (gallons) | 9679.85 | 7992.35 | 7385.2 | 920.92 | 10200.26 | 4696.43 | N/A | 280.61 | 4744.9 | 10673.47 | 6088.01 | 5843.11 | 68505.11
| Natural Gas Therms | 23 | 31 | 27 | 99 | 601 | 978 | 3984 | 2928 | 754 | 428 | 74 | 35 | 9962
| Elecricity Cost ($) | 7055.76 | 6534.48 | 6312.33 | 7261.31 | 6112.41 | 5032.46 | 6292.22 | 5457.24 | 50.67 | 7175.17 | 6720.76 | 7891.28 | 71896.09
| Water-Sewer Costs ($) | 555.95 | 472.79 | 489.63 | 230.21 | 535.39 | 287.5 | 117.72 | 101.15 | 248.15 | 451.38 | 350.08 | 419.38 | 4259.33
| Natural Gas ($) | 61 | 66.01 | 63 | 115.39 | 456.26 | 717.3 | 2708.28 | 2001.65 | 526.83 | 336.53 | 94.71 | 68.86 | 7215.82
NOTES:
Pavilion, Farmers Market Building and Meeting Center all on the same water meter.
Error have been identified with incorectly read water meeter bginning in 2014. Corections and credits are currently being tracked.
11 | UNCC - EPIC | [17 empty] | UNCC - EPIC
| EPIC |  | 2015-08-01: 07-07078-02A
|  | Jul '15 | Aug '15 | Sep '15 | Oct '15 | Nov '15 | Dec '15 | Jan '16 | Feb '16 | Mar '16 | Apr '16 | May '16 | Jun '16
Consumption
| Electric (KWH) | 439536 | 433347 | 433663 | 441674 | 417461 | 430847 | 426042.9 | 403208.3 | 436202.6 | 417591 | 422135.4 | 408032
| Nat Gas (Therms) | 156 | 149 | 169 | 872 | 1662 | 2824 | 2299 | 437 | 1635 | 1516 | 260 | 157
| Water (CF) | 4410 | 5359 | 9127 | 8827 | 11326 | 11084 | 12616 | 9158 | 17051.4 | 13434.3 | 7685.1 | 6763.5
| CHW BTUX10^6 | 3176 | 2770 | 2066 | 1356 | 948 | 1080 | 439 | 557 | 1095.8 | 1149 | 1621.1 | 2159.9
| HW BTUX10^6 | 339 | 369 | 348 | 524 | 646 | 569 | 759 | 627 | 446.5 | 397.3 | 372.6 | 191
Costs $
| Electric | 29343.6392 | 28943.7919 | 28983.3096 | 26989.8974 | 23487.9842 | 24260.6431 | 24122.947 | 23542.7416 | 25675.4805 | 23963.2284 | 24720.5714 | 26352.4999
| Nat Gas | 131.31 | 126.4 | 140.42 | 633.01 | 1178.32 | 1963.47 | 1571.35 | 314.16 | 1115.1 | 1039.81 | 199.7 | 129.64
| Water | 328.6912 | 404.9946 | 698.718 | 723.2985 | 934.8636 | 949.993 | 1169.1479 | 759.2073 | 1400.7989 | 1085.4327 | 606.8091 | 444.1544
| CHW | 16372.3879 | 14377.94 | 10936.4472 | 6758.9774 | 4955.9043 | 4723.8498 | 2613.6698 | 3309.6247 | 5343.2288 | 3718.4897 | 6603.2634 | 9545.3459
| HW | 1520.1754 | 2150.2358 | 1921.8172 | 2152.0815 | 2174.9931 | 2580.1328 | 3320.2591 | 2365.5364 | 1809.0395 | 1858.7424 | 1890.108 | 1708.3104
12 | NCDVA - NC State Veterans Home - Black Mountain | [17 empty] | DOA - VA - VA Home Swananoa
| NCDVA - NC State Veterans Home - Black Mountain |  | 2015-11-01: May 2015 - June 2016
| Utility | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-15 | 2016-04-01 | 2016-05-01 | 2016-06-01
| Electricity Usage (KWhs) | 166900 | 178234 | 197842 | 181087 | 169500 | 136848 | 140900 | 169923 | 157756 | 144687 | 144392 | 142200 | 177000 | 177800
| Gas usage therms | 2193 | 2219 | 2035 | 1902 | 2130 | 2136 | 2861 | 2903 | 2537 | 2419 | 2588 | 1943 | 1945 | 2482
| Water Usage (ccf) | 493 | 509 | 490 | 374 | 457 | 427 | 522 | 552 | 488 | 488 | 493 | 493 | 398 | 420
| Elecricity Cost ($) | 13776.57 | 14631.04 | 15986.9 | 14888.92 | 13812.05 | 11373.94 | 11466.82 | 13405.55 | 12517.76 | 11631.02 | 11456.99 | 11253.54 | 13873.41 | 14147.48
| Gas cost ($) | 1587.16 | 1605.37 | 1472.23 | 1379.22 | 1538.44 | 1539.93 | 1900.37 | 1917.73 | 1552.41 | 1478.3 | 1578.03 | 1252.45 | 1255.66 | 1588.24
| Water-Sewer Costs ($) | 4584.74 | 4590.17 | 4460.77 | 3564.17 | 4194.97 | 3966.97 | 4688.97 | 4916.97 | 4445.57 | 4468.57 | 4468.57 | 4468.57 | 3746.59 | 3913.77
13 | Pitt CC - Russell Classroom Building | [17 empty] | Pitt CC - Russell Classroom Building
14 | UNCG - Bailey Residence Hall Renovation | [17 empty] | UNCG - Bailey Residence Hall Renovation
| Bailey Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
305 West Drive
| Electricity (kWhs) | 17165 | 25595 | 24164 | 25172 | 21933 | 22308 | 21584 | 23656 | 24638 | 23837 | 18322 | 17851
| Lighting submeter (kWhs) | 3781.2 | 6651.12 | 5938.59 | 6355.2 | 6174.17 | 5095.76 | 6131.89 | 6627.24 | 6618.38 | 6269.45 | 4419.16 | 4027.08
| Mechanical submeter (kWhs) | 11497.37 | 13859.87 | 12833.26 | 13303.45 | 10901 | 13455.31 | 10501.55 | 11759.52 | 12953.69 | 12236.77 | 11925.21 | 11781.19
| Calculated plug load (kWhs) | 1886.43 | 5084.01 | 5392.15 | 5513.35 | 4857.83 | 3756.93 | 4950.56 | 5269.24 | 5065.93 | 5330.78 | 1977.63 | 2042.73
| Steam Usage (lbs) | 5030 | 8310 | 11460 | 14760 | 17321.9512 | 19080 | 53994.9375 | 47894.7812 | 23680 | 20580 | 6800 | 6400
| Water Usage (gallons) | 10000 | 77300 | 97800 | 138700 | 91100 | 57700 | 160600 | 82700 | 69300 | 68600 | 33100 | 25800
| Chilled water (ton-hrs) | 20523 | 18946 | 17090 | 10892 | 8437 | 7533 | 3846 | 5104 | 9942 | 10519 | 10997 | 15490
| Electricity Cost ($) | 1201.9698 | 1819.1866 | 1662.833 | 1602.7892 | 1396.5508 | 1312.5068 | 1280.4776 | 1397.0632 | 1472.6165 | 1384.1102 | 1090.2448 | 1164.71
| Water Cost ($) | 79.1257 | 611.6414 | 787.107 | 1116.2754 | 733.1845 | 464.377 | 1292.5294 | 665.5802 | 557.7353 | 552.1016 | 266.393 | 207.6417
| Steam Cost ($) | 39.3039 | 64.9335 | 89.5473 | 115.3332 | 135.352 | 149.0892 | 421.911 | 374.245 | 185.0332 | 160.8101 | 53.1345 | 50.009
Note 1: Inaccurate Steam Meter
Note 2: Missing Data
Note 3: Chilled water costs are based on a per square foot allocation, not on metered consumption.
15 | UNCG - Coit Residence Hall Renovation | [17 empty] | UNCG - Coit Residence Hall Renovation
| Coit Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
312 Gray Drive
| Electricity (kWhs) | 14811 | 22427 | 21884 | 23712 | 21302 | 21171 | 21753 | 25110 | 22206 | 21916 | 19196 | 17919.5
| Lighting submeter (kWhs) | 3947.53 | 6643.16 | 6107.76 | 6310.01 | 5986.73 | 5328.59 | 5892.48 | 6431.89 | 6093.45 | 6206.5 | 3903.94 | 2902.15
| Mechanical submeter (kWhs) | 8927.03 | 11220.61 | 10535.62 | 11829.76 | 10550.43 | 12269.77 | 10190.28 | 10711.96 | 11471.17 | 10966.49 | 10719.46 | 9995.67
| Calculated plug load (kWhs) | 1936.44 | 4563.23 | 5240.62 | 5572.23 | 4764.84 | 3572.64 | 5670.24 | 7966.15 | 4641.38 | 4743.01 | 4572.6 | 5021.68
| Steam Usage (lbs) | 5855 | 10655 | 7500 | 15020 | 14550 | 15470 | 45020.2344 | 40077.6953 | 21613.75 | 16057 | 16140 | 4780
| Water Usage (gallons) | 24400 | 29000 | 72000 | 75300 | 64800 | 34800 | 74000 | 84500 | 73400 | 79700 | 24300 | 20300
| Chilled water (ton-hrs) | 18529 | 22885 | 22789 | 17791 | 14628 | 12298 | 12333 | 10937 | 12907 | 13883 | 13340 | 16784
| Electricity Cost ($) | 1037.1322 | 1594.0183 | 1505.936 | 1509.8259 | 1356.3728 | 1245.6106 | 34.7646 | 588.5076 | 1327.2556 | 1272.5662 | 734.8829 | 1083
| Water Costs ($) | 193.0666 | 229.4644 | 579.4652 | 606.0241 | 521.5187 | 280.0749 | 595.5615 | 680.0668 | 590.7326 | 641.4358 | 195.5695 | 163.377
| Steam Cost ($) | 45.7504 | 83.2571 | 58.6043 | 117.3648 | 113.6922 | 120.881 | 351.7836 | 313.1631 | 168.8877 | 125.4678 | 126.1163 | 37.3504
Note 1: Inaccurate Steam Meter
Note 2: Missing Data
Note 3: Chilled water costs are based on a per square foot allocation, not on metered consumption.
16 | UNCG - Cotten Residence Hall Renovation | [17 empty] | UNCG - Cotten Residence Hall Renovation
| Cotten Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
314 Gray Drive
| Electricity (kWhs) | 17928 | 27420 | 26490 | 27592 | 24206 | 23917 | 22057 | 24845 | 25664 | 28515 | 19449 | 18617
| Lighting submeter (kWhs) | 3685.18 | 6311.79 | 5885.91 | 6318.63 | 5926 | 5399.55 | 5911.08 | 6398.31 | 6346.36 | 6013.96 | 4338.37 | 3917.24
| Mechanical submeter (KWhs) | 12185.35 | 16380.75 | 15084.64 | 15362.93 | 13201.65 | 14589.56 | 11156.07 | 13125.19 | 14145.5 | 13905.78 | 12531.44 | 12558.84
| Calculated plug load (kWhs) | 2057.47 | 4727.46 | 5519.45 | 5910.44 | 5078.35 | 3927.89 | 4989.85 | 5321.5 | 5172.14 | 8595.26 | 2579.19 | 2140.92
| Steam Usage (lbs) | 6680 | 13000 | 19100 | 35130 | 10000 | 14470 | 42376.293 | 36995.6191 | 22197.1875 | 51990 | 8710 | 7980
| Water Usage (gallons) | 13500 | 80300 | 122000 | 119200 | 99400 | 66000 | 98100 | 114700 | 98500 | 87300 | 27800 | 52000
| Chilled water (ton-hrs) | 19231 | 21446 | 20118 | 14783 | 11547 | 9616 | 5516 | 6976 | 12798 | 12870 | 12322 | 16624
| Electricity Cost ($) | 1255.3985 | 1948.9 | 1822.8954 | 1756.8791 | 1541.2806 | 1407.1735 | 1308.5385 | 1467.2825 | 1533.9407 | 1655.7412 | 1157.3066 | 1214.6886
| Water Costs ($) | 106.8197 | 635.3791 | 981.8717 | 959.3369 | 799.984 | 531.1765 | 789.5214 | 923.1203 | 792.7406 | 702.6016 | 223.738 | 418.5027
| Steam Cost ($) | 52.1969 | 101.5807 | 149.2455 | 274.5023 | 78.139 | 113.0671 | 331.1241 | 289.0801 | 173.4466 | 406.2447 | 68.0591 | 62.3549
Note 1: Inaccurate Steam Meter
Note 2: Missing Data
Note 3: Chilled water costs are based on a per square foot allocation, not on metered consumption.
17 | UNCG - Gray Residence Hall Renovation | [17 empty] | UNCG - Gray Residence Hall Renovation
| Gray Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
316 Gray Drive
| Electricity (kWhs) | 17881 | 25823 | 25262 | 27592 | 22992 | 23272 | 21878 | 22370 | 24352 | 24196 | 19926 | 18382
| Lighting submeter (kWhs) | 4208.7 | 6294.85 | 6027.33 | 6540.63 | 6135.3625 | 5386.385 | 6135 | 6565 | 6396 | 6375 | 5170 | 4024
| Mechanical submeter (kWhs) | 11490.77 | 14955.22 | 14015.6 | 14281.01 | 12160.86 | 13684.38 | 11253.98 | 10824.42 | 13202.02 | 12989.3 | 12557.63 | 12227.29
| Calculated plug load (kWhs) | 2181.53 | 4572.93 | 5219.07 | 6770.36 | 4695.7775 | 4201.235 | 4489.02 | 4980.58 | 4753.98 | 4831.7 | 2198.37 | 2130.71
| Steam Usage (lbs) | 2990 | 7420 | 11540 | 13660 | 17000 | 19470 | 55596 | 52406 | 19280 | 17918 | 5670 | 5140
| Water Usage (gallons) | 9500 | 64700 | 87500 | 100100 | 75300 | 41800 | 78400 | 89900 | 70300 | 75800 | 23400 | 39600
| Chilled water (ton-hrs) | 18910 | 21330 | 21444 | 13159 | 9189 | 8344 | 3436 | 4313 | 10606 | 11178 | 13308 | 19159
| Electricity Cost ($) | 1252.1073 | 1835.3919 | 1738.3913 | 1756.8791 | 1463.981 | 1369.2244 | 1297.9193 | 1321.1153 | 1455.5223 | 1404.9558 | 1185.6903 | 1199.3557
| Water Costs ($) | 75.1694 | 511.9431 | 704.2112 | 805.6176 | 606.0241 | 336.4118 | 630.9733 | 723.5267 | 565.7834 | 610.0481 | 188.3262 | 318.7059
| Steam Cost ($) | 23.3636 | 57.9791 | 90.1724 | 106.7379 | 132.8363 | 152.1366 | 434.4216 | 409.4952 | 150.652 | 140.0095 | 44.3048 | 40.1634
Note 1: Inaccurate Steam Meter
Note 2: Missing Data
Note 3: Chilled water costs are based on a per square foot allocation, not on metered consumption.
18 | UNCG - Hinshaw Residence Hall Renovation | [17 empty] | UNCG - Hinshaw Residence Hall Renovation
| Hinshaw Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
309 West Drive
| Electricity (kWhs) | 20706 | 31693 | 32266 | 32710 | 29305 | 29247 | 27937 | 29569 | 30145 | 30013 | 23424 | 23243
| Lighting submeter (kWhs) | 4051.43 | 6501.68 | 6671.79 | 6789.42 | 6478.71 | 5496.73 | 6490.72 | 6751.18 | 6579.78 | 6720.08 | 4523.29 | 3894.96
| Mechanical submeter (kWhs) | 11976.08 | 16853.4 | 16444.83 | 15883.53 | 13652.52 | 14708.87 | 12464.67 | 13454.38 | 14503.03 | 14671.66 | 13493.64 | 14583.25
| Site Lighting (kWh) | 2583 | 2923 | 3112 | 3510 | 3735 | 3915 | 3851 | 3311 | 3715 | 3107 | 2948 | 2670
| Calculated plug load (kWhs) | 4678.49 | 8337.92 | 9149.38 | 10037.05 | 9173.77 | 9041.4 | 8981.61 | 9363.44 | 9062.19 | 8621.26 | 5407.07 | 4764.79
| Steam Usage (lbs) | 4390 | 11340 | 16340 | 19400 | 20070 | 11480 | 35100 | 33730 | 21480 | 21780 | 6750 | 7200
| Water Usage (gallons) | 4400 | 54200 | 73200 | 76200 | 70400 | 33200 | 74500 | 83800 | 71000 | 76300 | 18800 | 23800
| Chilled water (ton-hrs) | 18284 | 22007 | 21871 | 12915 | 10214 | 7974 | 4325 | 5323 | 10817 | 11584 | 12586 | 19547
| Electricity Cost ($) | 1449.9264 | 2252.6071 | 2220.3679 | 2082.76 | 1865.9518 | 1720.7677 | 1657.3713 | 1746.27 | 1801.7707 | 1742.7235 | 1393.8377 | 1516.5176
| Water Costs ($) | 34.8153 | 428.8611 | 589.123 | 613.2674 | 566.5882 | 267.1979 | 599.5856 | 674.4332 | 571.4171 | 614.0722 | 151.3048 | 191.5455
| Steam Cost ($) | 34.303 | 88.6096 | 127.6791 | 151.5897 | 156.825 | 89.7036 | 274.2679 | 263.5628 | 167.8426 | 170.1867 | 52.7438 | 56.2601
Note 1: Inaccurate Steam Meter
Note 2: Missing Data
Note 3: Chilled water costs are based on a per square foot allocation, not on metered consumption.
19 | UNCG - Jamison Residence Hall Renovation | [17 empty] | UNCG - Jamison Residence Hall Renovation
| Jamison Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
301 West Drive
| Electricity (kWhs) | 17284 | 25723 | 27480 | 27696 | 23456 | 23047 | 21494 | 21134 | 24628 | 24142 | 19087 | 16828
| Lighting submeter (kWhs) | 3520.69 | 6430.37 | 6354.16 | 6746.45 | 6150.01 | 5320.67 | 5507.29 | 5779.87 | 6264.76 | 5975.38 | 4248.73 | 2879.43
| Mechanical submeter (kWhs) | 11746.47 | 14562.5 | 13417.24 | 13974.57 | 12303.8 | 14003.44 | 11182.94 | 10157.46 | 13362.19 | 12994.94 | 12377.35 | 12109.03
| Calculated plug load (kWhs) | 2016.84 | 4730.13 | 7708.6 | 6974.98 | 5002.19 | 3722.89 | 4803.77 | 5196.67 | 5001.05 | 5171.68 | 2460.92 | 1839.54
| Steam Usage (lbs) | 1690 | 1710 | 1180 | 12260 | 14520 | 11850 | 35390 | 26280 | 22015 | 3950 | 420 | 6300
| Water Usage (gallons) | 5200 | 56500 | 85000 | 98400 | 87400 | 71800 | 91900 | 113400 | 97500 | 80500 | 21800 | 26000
| Chilled water (ton-hrs) | 18738.5 | 15540 | 14419 | 10251 | 9091 | 7664 | 4935 | 5032 | 7646 | 9019 | 9143 | 12709
| Electricity Cost ($) | 1210.3027 | 1828.2843 | 1891.0218 | 1763.5011 | 1493.5255 | 1355.9864 | 1275.1383 | 1248.1203 | 1472.0188 | 1401.8202 | 1135.7659 | 1097.9631
| Water Costs ($) | 41.1453 | 447.06 | 684.0909 | 791.9358 | 703.4064 | 577.8556 | 739.623 | 912.6578 | 784.6925 | 647.8743 | 175.4492 | 209.2513
| Steam Cost ($) | 13.2055 | 13.3618 | 9.2204 | 95.7984 | 113.4578 | 92.5947 | 276.5339 | 205.3493 | 172.023 | 30.8649 | 3.2818 | 49.2276
Note 1: Inaccurate Steam Meter
Note 2: Missing Data
Note 3: Chilled water costs are based on a per square foot allocation, not on metered consumption.
20 | UNCG - Shaw Residence Hall Renovation | [17 empty] | UNCG - Shaw Residence Hall Renovation
| Shaw Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
1310 Walker Ave
| Electricity (kWhs) | 35665 | 47881 | 46903 | 48407 | 42494 | 44158 | 41997 | 44103 | 45877 | 44951 | 36651 | 38142
| Lighting submeter (kWhs) | 8978.72 | 12658.43 | 12557.48 | 13674.17 | 12529.84 | 12243.8 | 12662.58 | 13528.06 | 13622.13 | 13240.52 | 9214.98 | 9909.02
| Mechanical submeter (kWhs) | 15840.6 | 18735.1 | 17261.83 | 17384.17 | 14962.59 | 17147.39 | 14270.27 | 14799.97 | 16259.59 | 15792.96 | 15006.53 | 16462.89
| Calculated plug load (kWhs) | 10845.68 | 16487.47 | 17083.69 | 17348.66 | 15001.57 | 14766.81 | 15064.15 | 15774.97 | 15995.28 | 15917.52 | 12429.49 | 11770.09
| Steam Usage (lbs) | 1490 | 2150 | 10110 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | 35290 | 14330
| Water Usage (gallons) | 1911.7647 | 127100 | 157900 | 154500 | 123500 | 83700 | 127900 | 139000 | 114800 | 114500 | 46500 | 49500
| Chilled water (ton-hrs) | 47976 | 46657 | 44307 | 31922 | 26803 | 22795 | 16977 | 20489 | 31565 | 33938 | 34826 | 49966
| Electricity Cost ($) | 2497.4222 | 3403.1831 | 3227.6053 | 3082.2429 | 2705.7415 | 2598.0669 | 2491.4853 | 2604.6111 | 2742.0744 | 2610.1077 | 2180.9062 | 2488.6208
| Water Costs ($) | 113.1497 | 1005.6872 | 1270.7995 | 1243.4358 | 993.9439 | 673.6283 | 1029.3556 | 1118.6898 | 923.9251 | 921.5107 | 374.238 | 398.3824
| Steam Cost ($) | 11.6427 | 16.7999 | 78.9985 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | 275.7525 | 111.9732
Note 1: Inaccurate Steam Meter
Note 2: Missing Data
Note 3: Chilled water costs are based on a per square foot allocation, not on metered consumption.
21 | WCU - Harrill Residence Hall Renovation | [17 empty] | WCU - Harrill Residence Hall Renovation
Western Carolina University - Harrill Residence Hall
| Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14
| Electricity (KWhs) |  | 56876 | 74032 | 80325 | 73896 | 72153 | 43317 | meter down | meter down | 76832 | 69878 | 53689 | 52885
Steam (lbs)
Chilled Water (Dtherms)
Natural Gas (Therms)
| Water (CCF) |  | 31.0406 | 166.2986 | 263.3239 | 214.0092 | 243.7932 | 80.997 | 171.98 | 228.2194 | 198.8632 | 249.0201 | 37.4573 | 12.1248
| Electricity Cost ($) |  | 4159.8538 | 5809.9573 | 5936.4191 | 4395.7775 | 4292.0934 | 2698.2592 | meter down | meter down | 4556.1376 | 4268.1482 | 3248.0234 | 4009.5292 |  |  |  | 43374.1987
Steam Costs ($)
Chilled Water Costs ($)
Natural Gas Costs ($)
|  | FY2014/15 | 2015-08-01: FY2015/16; 2015-09-01: FY15/16 kWh cost; 2015-10-01: Total cost; 2015-12-01: Gallons; 2016-01-01: Water cost; 2016-02-01: CCF
| July | 60739 | 2015-08-01: 56876; 2015-09-01: 0.073139; 2015-10-01: 4159.8538; 2015-12-01: 23220; 2016-01-01: 87.7716; 2016-02-01: 31.0406
| August | 78737 | 2015-08-01: 74032; 2015-09-01: 0.078479; 2015-10-01: 5809.9573; 2015-12-01: 124400; 2016-01-01: 470.232; 2016-02-01: 166.2986
| September | 86657 | 2015-08-01: 80325; 2015-09-01: 0.073905; 2015-10-01: 5936.4191; 2015-12-01: 196980; 2016-01-01: 744.5844; 2016-02-01: 263.3239
| October | 75803 | 2015-08-01: 73896; 2015-09-01: 0.059486; 2015-10-01: 4395.7775; 2015-12-01: 160090; 2016-01-01: 605.1402; 2016-02-01: 214.0092
| November | 77415 | 2015-08-01: 72153; 2015-09-01: 0.059486; 2015-10-01: 4292.0934; 2015-12-01: 182370; 2016-01-01: 689.3586; 2016-02-01: 243.7932
| December | 51474 | 2015-08-01: 43317; 2015-09-01: 0.062291; 2015-10-01: 2698.2592; 2015-12-01: 60590; 2016-01-01: 229.0302; 2016-02-01: 80.997
| January | 78316 | 2015-08-01: meter down; 2015-09-01: 0.058346; 2015-12-01: 128650; 2016-01-01: 486.297; 2016-02-01: 171.98
| February | 82982 | 2015-08-01: meter down; 2015-09-01: 0.059426; 2015-12-01: 170720; 2016-01-01: 645.3216; 2016-02-01: 228.2194
| March | 73544 | 2015-08-01: 76832; 2015-09-01: 0.0593; 2015-10-01: 4556.1376; 2015-12-01: 148760; 2016-01-01: 562.3128; 2016-02-01: 198.8632
| April | 74750 | 2015-08-01: 69878; 2015-09-01: 0.06108; 2015-10-01: 4268.1482; 2015-12-01: 186280; 2016-01-01: 704.1384; 2016-02-01: 249.0201
| May | 59697 | 2015-08-01: 53689; 2015-09-01: 0.060497; 2015-10-01: 3248.0234; 2015-12-01: 28020; 2016-01-01: 105.9156; 2016-02-01: 37.4573
| June | 56519 | 2015-08-01: 52885; 2015-09-01: 0.075816; 2015-10-01: 4009.5292; 2015-12-01: 9070; 2016-01-01: 34.2846; 2016-02-01: 12.1248
|  | 695335 | 2015-08-01: 653883; 2015-10-01: 43374.1987
22 | UNCP Health Science Builidng | [17 empty] | UNCP Health Science Builidng
| University of North Carolina at Pembroke - Health Science Building Energy & Natural Gas Usage | [13 empty] | Building Square Feet
| Utility | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | Total | 87593
| Electricity Usage (KWhs) | 85778.96 | 113621.46 | 152143.24 | 180402.2 | 114532.16 | 95786.24 | 90504.5062 | 111469.9 | 86489.4 | 99097.3 | 111892.5 | 111500 | 1353217.8662 | 15.4489
| Electricity Cost | 6927.5088 | 9176.0691 | 12287.0881 | 14569.2817 | 9249.6172 | 7735.6967 | 7309.1439 | 9002.3091 | 6984.8839 | 8003.0979 | 9036.4383 | 9004.74 | 109285.8749 | 1.2477
| Natural Gas (Therms) | 0 | 0 | 0 | 0 | 0 | 0 | 10503 | 4632 | 3618 | 2624 | 1926 | 1450 | 24753 | 0.28259
| Natural Gas Cost | 0 | 0 | 0 | 0 | 0 | 0 | 4218.0048 | 1860.2112 | 1452.9888 | 1053.7984 | 773.4816 | 582.32 | 9940.8048 | 0.11349
| Natural Gas Transportation Cost | 0 | 0 | 0 | 0 | 0 | 0 | 1825.4214 | 805.0416 | 628.8084 | 456.0512 | 334.7388 | 252.01 | 4302.0714 | 0.049114
| Total Natural Gas Charges | 0 | 0 | 0 | 0 | 0 | 0 | 6043.4262 | 2665.2528 | 2081.7972 | 1509.8496 | 1108.2204 | 834.33 | 14242.8762 | 0.1626
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | Total
| Electricity Usage (KWhs) | 132276 | 137730 | 134465 | 124059 | 117931 | 93622 | 110748 | 109838 | 79601 | 106369 | 52332 | 111294 | 1310265 | 14.9586
| Electricity Cost | 10682.6098 | 11123.0748 | 10859.3934 | 10019.0048 | 9524.1076 | 7560.9127 | 8944.0085 | 8870.5169 | 6428.5768 | 8590.3604 | 4226.3323 | 8988.1034 | 105817.0014 | 1.2081
| Natural Gas (Therms) | 1577 | 1398 | 1304 | 1202 | 2179 | 2368 | 4126 | 4009 | 2298 | 2457 | 1910 | 1177 | 26005 | 0.29688
| Natural Gas Cost | 633.3232 | 561.4368 | 523.6864 | 482.7232 | 875.0864 | 950.9888 | 1657.0016 | 1610.0144 | 922.8768 | 986.7312 | 767.056 | 472.6832 | 10443.608 | 0.11923
| Natural Gas Transportation Cost | 274.0826 | 242.9724 | 226.6352 | 208.9076 | 378.7102 | 411.5584 | 717.0988 | 696.7642 | 399.3924 | 427.0266 | 331.958 | 204.5626 | 4519.669 | 0.051599
| Total Natural Gas Charges | 907.4058 | 804.4092 | 750.3216 | 691.6308 | 1253.7966 | 1362.5472 | 2374.1004 | 2306.7786 | 1322.2692 | 1413.7578 | 1099.014 | 677.2458 | 14963.277 | 0.17083
| Water Usage (Gallons) | 147700 | 141500 | 131000 | 67100 | 31250 | 18300 | 9750 | 10120 | 26800 | 50000 | 94225 | 120500 | 848245 | 9.6839
| Water Cost | 4181.387 | 4005.865 | 3708.61 | 1899.601 | 884.6875 | 518.073 | 276.0225 | 286.4972 | 758.708 | 1415.5 | 2667.5097 | 3411.355 | 24013.816 | 0.27415
The water usage has been estimated based on normal cooling tower evaperation and additional building water usage per month. We will be replacing the borken meter soon.
| Utility | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | Total
| Electricity Usage (KWhs) | 124350 | 124506 | 157696 | 138410 | 115773 | 107197 | 96118 | 110983 | 90056 | 131594 | 122952 | 119384 | 1439019 | 16.4285
| Electricity Cost | 10042.506 | 10055.1046 | 12735.529 | 11177.9916 | 9349.8275 | 8657.2297 | 7762.4897 | 8962.9871 | 7272.9226 | 10627.5314 | 9929.6035 | 9641.4518 | 116215.1744 | 1.3268
| Natural Gas (Therms) | 878 | 1123 | 1488 | 1741 | 1756 | 2813 | 2829 | 3202 | 3083 | 2150 | 1769 | 1707 | 24539 | 0.28015
| Natural Gas Cost | 352.6048 | 450.9968 | 597.5808 | 699.1856 | 705.2096 | 1129.7008 | 1136.1264 | 1285.9232 | 1238.1328 | 863.44 | 710.4304 | 685.5312 | 9854.8624 | 0.11251
| Natural Gas Transportation Cost | 152.5964 | 195.1774 | 258.6144 | 302.5858 | 305.1928 | 488.8994 | 491.6802 | 556.5076 | 535.8254 | 373.67 | 307.4522 | 296.6766 | 4264.8782 | 0.04869
| Total Natural Gas Charges | 505.2012 | 646.1742 | 856.1952 | 1001.7714 | 1010.4024 | 1618.6002 | 1627.8066 | 1842.4308 | 1773.9582 | 1237.11 | 1017.8826 | 982.2078 | 14119.7406 | 0.1612
| Water Usage (Gallons) | 147700 | 141500 | 131000 | 67100 | 31250 | 18300 | 9750 | 10120 | 26800 | 50000 | 94225 | 120500 | 848245 | 9.6839
| Water Cost | 4181.387 | 4005.865 | 3708.61 | 1899.601 | 884.6875 | 518.073 | 276.0225 | 286.4972 | 758.708 | 1415.5 | 2667.5097 | 3411.355 | 24013.816 | 0.27415
The water usage has been estimated based on normal cooling tower evaperation and additional building water usage per month. We will be replacing the borken meter soon.
| Utility | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | Total
| Electricity Usage (KWhs) | 161839 | 131675 | 169020 | 131395 | 123099 | 115651 | 90881 | 101201 | 89476 | 129462 | 103558 | 113370 | 1460627 | 16.6752
| Electricity Cost | 13070.1176 | 10634.073 | 13650.0552 | 10611.4602 | 9941.4752 | 9339.9748 | 7339.5496 | 8172.9928 | 7226.0818 | 10455.3511 | 8363.3441 | 9155.7612 | 117960.2365 | 1.3467
| Natural Gas (Therms) | 1765 | 1268 | 1379 | 1519 | 1787 | 2640 | 2405 | 3310 | 2511 | 2617 | 1485 | 1321 | 24007 | 0.27407
| Natural Gas Cost | 708.824 | 509.2288 | 553.8064 | 610.0304 | 717.6592 | 1060.224 | 965.848 | 1329.296 | 1008.4176 | 1050.9872 | 596.376 | 530.5136 | 9641.2112 | 0.11007
| Natural Gas Transportation Cost | 306.757 | 220.3784 | 239.6702 | 264.0022 | 310.5806 | 458.832 | 417.989 | 575.278 | 436.4118 | 454.8346 | 258.093 | 229.5898 | 4172.4166 | 0.047634
| Total Natural Gas Charges | 1015.581 | 729.6072 | 793.4766 | 874.0326 | 1028.2398 | 1519.056 | 1383.837 | 1904.574 | 1444.8294 | 1505.8218 | 854.469 | 760.1034 | 13813.6278 | 0.1577
| Water Usage (Gallons) |  | 2016-07-01: 0 | 0
| Water Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
The water usage has been estimated based on normal cooling tower evaperation and additional building water usage per month. We will be replacing the borken meter soon.
23 | FSU - Renaissance Residence Hall | [17 empty] | FSU - Renaissance Residence Hall
24 | UNCA - Overlook Residence Hall | [17 empty] | UNCA - Overlook Residence Hall
UNC-Asheville Overlook Residence Hall
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
|  | Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total FY
| Duke | Electricity (KWhs)
Steam (lbs)
Chilled Water (Dtherms)
| PSNC | Natural Gas (Therms)
| City | Water (CCF) | 137 | 189 | 479 | 583 | 578 | 545 | 145 | 693 | 669 | 868 | 665 | 98 |  |  |  |  | 5649
Electricity Cost ($)
Steam Costs ($)
|  | Water Costs ($) | 1768.97 | 2158.17 | 4362.17 | 5152.57 | 5122.17 | 4863.77 | 1823.77 | 5988.57 | 5806.17 | 7318.57 | 5775.77 | 1466.57 |  |  |  |  | 51607.24
Natural Gas Costs ($)
We do not have separate electricity bills for our campus. The majority of the campus is on one main meter.
25 | ECSU - Viking Tower Residence Hall | [17 empty] | ECSU - Viking Tower Residence Hall
UNC - ECSU - VIKING TOWER
| Utility | Jun-15 | 2015-07-15 | 2015-08-15 | 2015-09-15 | 2015-10-15 | 2015-11-15 | 2015-12-15 | 2016-01-16 | 2016-02-16 | 2016-03-16 | 2016-04-16 | 2016-05-16 | 2016-06-16 | 2016-07-16 | 2016-08-16 | 2016-09-14
| Electricity (KWhs) | 42143 | 40760 | 51843 | 57560 | 58807 | 54797 | 49241 | 50985 | 51811 | 53229.2 | 56043.7 | 51204.8 | 43161.1
| Steam (lbs) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water (Dtherms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas (Therms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) | 87009 | 9563 | 176523 | 176523 | 219217 | 114451 | 114451 | 114451 | 200352 | 110648 | 266982 | 251199 | 251089
| Electricity Cost ($) | 4513.52 | 3713.22 | 4608.81 | 5289.79 | 5345.56 | 5030.38 | 4554.79 | 4797.65 | 4787.3 | 4897.09 | 5195.25 | 4741.56 | 4009.67
| Steam Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | UNCW - Teaching Lab | [17 empty] | UNCW Teaching Lab
27 | UNCA - Rhoades Hall Renovation | [17 empty] | UNCA - Rhoades Hall Renovation
UNC-Asheville Rhoades Hall Renovation
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
|  | Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14 | Total FY
| Duke | Electricity (KWhs)
Steam (lbs)
Chilled Water (Dtherms)
| PSNC | Natural Gas (Therms) | 850 | 205 | 237 | 1123 | 1576 | 3001 | 4718 | 5697 | 6373 | 4261 | 3275 | 1851 |  |  |  |  | 33167
| City | Water (CCF) | 2: 398; 4: 211; 6: 222; 8: 108; 10: 157; 12: 222 |  |  |  |  | 1318
Electricity Cost ($)
Steam Costs ($)
|  | Water Costs ($) | 1352.29 | 2571.1 | 71.33 | 1928.86 |  | 2551.74 | 142.66 | 1451.37 | 142.66 | 1753.86 | 195.45 | 1859.81 |  |  |  |  | 14021.13
|  | Natural Gas Costs ($) | 623.39 | 181.27 | 203.98 | 799.84 | 1094.39 | 1918.77 | 2902.32 | 3269.8 | 3521.96 | 2416.7 | 1935.26 | 1137.99 |  |  |  |  | 20005.67
We do not have separate electricity bills for our campus. The majority of the campus is on one main meter.
28 | ECU - Ross Hall | [17 empty] | ECU - Ross Hall
ECU - Ledyard E. Ross Hall
| Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14
| Electricity (KWhs) | 190063.41 | 195786.52 | 193318.21 | 190165.6 | 186489.03 | 179960.13 | 192952.99 | 196114.78 | 190897.88 | 201911.74 | 192422.26 | 199238.14 | 200415.37 | 227631.31
Steam (lbs)
| Chilled Water (Tons) | 115647 | 130223 | 117883 | 112675 | 61763 | 47561 | 40723 | 20532 | 22875 | 50367 | 48735 | 67625 | 117328 | 170787
| Natural Gas (CCF) | 2089 | 459 | 1155 | 1487 | 1719 | 1745 | 2025 | 3795 | 3764 | 2144 | 1803 | 1378 | 1420
Water (CCF)
| Electricity Cost ($) | 16678.0642 | 17180.2671 | 16963.6729 | 16687.0314 | 16364.4124 | 15791.5014 | 16931.6249 | 17209.0719 | 16751.289 | 17717.7552 | 16885.0533 | 17483.1468 | 17586.4487 | 19974.6475 | 0 | 0
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 1993.87 | 523.21 | 1152.14 | 1327.57 | 1516.17 | 1537.3 | 1764.91 | 3203.75 | 3178.55 | 1861.65 | 1584.45 | 1238.97 | 1267.24
29 | Gaston College - Lena Sue Beam Renovation | [17 empty] | Gaston College - Lena Sue Beam Renovation
Gaston College - Lena Sue Beam Building
| Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14
| Electricity (KWhs) | 22840 | 21920 | 27480 | 29080 | 31240 | 28480 | 23520 | 18840 | 21560 | 24650 | 23200 | 23680 | 28000 | 17560
| Steam (lbs) | 0 | 0 | 0 | 1050 | 59050 | 143150 | 147350 | 264700 | 192850 | 72800 | 22800 | 0 | 0 | 0
Chilled Water (Dtherms)
| Natural Gas (Therms) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) (gallons) | 3017 | 2421 | 9665 | 11022 | 10187 | 9900 | 6974 | 7940 | 10850 | 9965 | 10166 | 33768 | 6367 | 3449
| Electricity Cost ($) | 2093.8227 | 1878.875 | 2414.2801 | 2541.3274 | 2401.7624 | 2232.6611 | 1792.4451 | 1403.256 | 1665.4733 | 1771.4673 | 1739.1022 | 1381.8701 | 3247.4624 | 1608.9174
| Steam Costs ($) | 0 | 0 | 0 | 28 | 680.8 | 1513.6 | 1511.2 | 2528.8 | 1861.6 | 740.8 | 264.8 | 0 | 0 | 0
Chilled Water Costs ($)
| Natural Gas Costs ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
missing a meter reading for one critical piece of information related to Chilled Water
| Electricity cost per kwh | 0.091674 | 0.085715 | 0.087856 | 0.087391 | 0.076881 | 0.078394 | 0.076209 | 0.074483 | 0.077248 | 0.071865 | 0.074961 | 0.058356 | 0.11598 | 0.091624
30 | NCSU - Hunt Library | [17 empty] | NCSU - Hunt Library
NCSU - Hunt Library
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 371394.5312 | 372462.4023 | 382747.0703 | 368691.8945 | 374088.8672 | 375130.8594 | 352869.1406 | 421780.2734 | 383250.9766 | 384455.0781 | 360948.2422 | 375840.8203 |  | 4523660.1562 | kwh |  | 15423.4736 | MMbtu
| Chilled Water (Dtherms) |  | 1188.704 | 1065.488 | 520.544 | 403.264 | 439.44 | 134.784 | 217.952 | 506 | 525 | 781 | 1117 | 1530 |  | 8429.176 | dthrms |  | 8429.176 | MMbtu
| Steam (1,000 lbs) |  | 263.0938 | 282.7969 | 420.2031 | 527.4062 | 593.6875 | 1087.7031 | 909.1094 | 662 | 517 | 415 | 327 | 335 |  | 6340 | 1000 lbs |  | 6340 | MMbtu
| Water (CCF) |  | 382 | 317 | 190 | 189 | 170 | 107 | 197 | 203 | 240 | 156 | 116 | 93 |  | 2360 | CCF |  | 1765280 | gallons
| Electric Cost ($) |  | 31939.9297 | 32031.7666 | 32916.248 | 31707.5029 | 32171.6426 | 32261.2539 | 30346.7461 | 36273.1035 | 32959.584 | 33063.1367 | 31041.5488 | 32698.1514 |  | 389410.6143 | $
| Chilled Water Cost ($) |  | 16606.1949 | 14884.8674 | 7271.9997 | 5633.5981 | 6138.9768 | 1882.9325 | 3044.7894 | 7068.82 | 7334.25 | 10910.57 | 15604.49 | 19813.5 |  | 116194.9887 | $
| Steam Cost ($) |  | 3522.8253 | 3786.6502 | 5626.5198 | 7061.9697 | 7949.4756 | 14564.3448 | 12172.9745 | 8864.18 | 6922.63 | 5556.85 | 4378.53 | 4026.7 |  | 84433.65 | $
| Water Cost ($) |  | 3514.4 | 2916.4 | 1748 | 1738.8 | 1564 | 984.4 | 1812.4 | 1867.6 | 2208 | 1435.2 | 1067.2 | 867.69 |  | 21724.09 | $
31 | UNCC - Rose Football Center | [17 empty] | UNCC - Rose Football Center
| Judy W. Rose Football Center |  | 2015-08-01: 08-07833-02A
|  | Jul '15 | Aug '15 | Sep '15 | Oct '15 | Nov '15 | Dec '15 | Jan '16 | Feb '16 | Mar '16 | Apr '16 | May '16 | Jun '16
Consumption
| Electric (KWH) | 153348 | 204930 | 186979 | 216712.2 | 210352.9 | 124355.6 | 116637.7 | 112030 | 126273.9 | 136211 | 123814.9 | 136677.8
| Nat Gas (Therms) | 1240 | 976 | 1627 | 2150 | 3202 | 2860 | 4149 | 3704 | 2627 | 1905 | 1628 | 1023
| Water (CF) | 78754 | 34591 | 25069 | 44991 | 15285 | 12019 | 21527 | 10314 | 11210 | 28835 | 20732 | 19184
excludes irrigation
Costs $
| Electric | 10237.5878 | 13687.5328 | 12496.5013 | 13242.8896 | 11835.2747 | 7002.3624 | 6604.1355 | 6541.2675 | 7432.6541 | 7816.3928 | 7250.6951 | 8827.253
| Nat Gas | 890.87 | 705.88 | 1162.04 | 1528.51 | 2249.76 | 1988.22 | 2818.11 | 2498.35 | 1778.31 | 1778.31 | 1134.67 | 723.38
| Water | 5869.7842 | 2614.1386 | 1919.1588 | 3686.6343 | 1261.6449 | 1030.1304 | 1994.9466 | 855.0409 | 920.9189 | 2329.742 | 1636.9814 | 1259.8002
32 | NC Division of Veterans Affairs - NC State Veterans Home - Kinston | [17 empty] | NC Division of Veterans Affairs - NC State Veterans Home - Kinston
NC Division of Veterans Affairs - NC State Veterans Home - Kinston
| Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14
| Electricity (KWhs) |  | 200600 | 218000 | 2084000 | 169200 | 166000 | 178800 | 151800 | 153400 | 164400 | 161800 | 186400 | 228400
| Steam (lbs) |  | N/A | N/A | N./A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Chilled Water (Dtherms) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Natural Gas (Therms) |  | 1388 | 1948 |  |  | 1946 | 1778 | 2078 | 1884 | 2185 | 1682 |  | 1881
| Water (CCF) |  | 313000 | 343200 | 411900 | 468800 | 426700 | 3067000 | 295400 | 311700 | 274500 | 279200 | 257100 | 261900
| Electricity Cost ($) |  | 17162.63 | 18673.51 | 18211.23 | 15024.62 | 14372.26 | 14668.42 | 13084.35 | 13290.26 | 14102.62 | 13922.34 | 16067.44 | 19309.93
| Steam Costs ($) |  | N/A | N/A | N./A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Chilled Water Costs ($) |  | N/A | N/A | N./A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Natural Gas Costs ($) |  | 1064.19 | 1507.59 |  |  | 1477.19 | 1330.66 | 1526.77 | 1371.28 | 1586.6 | 1228.24 |  | 1402.88
| Water Cost $ |  | 11695.82 | 1857.99 | 22226.91 | 2532.47 | 2306.39 | 1988.66 | 1601.31 | 1688.84 | 1776.64 | 1514.31 | 1395.64 | 1421.41
33 | Randolph CC - Klaussner Building Renovation | [17 empty] | Randolph CC - Klaussner Building Renovation
| Randolph | Community | 2015-08-01: College; 2015-10-01: 2015-2016; 2015-12-01: Continuing; 2016-01-01: Education; 2016-02-01: Industrial; 2016-03-01: Center
|  | July | August | September | October | November | December | January | February | March | April | May | June | Totals
| 83301 1830392826 CEIC 413 Ind. Pk. Ave. |  | 2015-12-01: Domestic Water
| Usage (CF) | 810 | 410 | 270 | 240 | 230 | 90 | 160 | 510 | 260 | 390 | 150 | 130 | 3650
| Days in Period | 30 | 30 | 32 | 30 | 29 | 34 | 27 | 30 | 32 | 29 | 33 | 31
| Water | 31.99 | 21.03 | 17.2 | 16.38 | 16.1 | 13.91 | 14.18 | 23.77 | 16.92 | 20.49 | 13.91 | 13.91 | 219.79
| Sewer | 35.73 | 24.49 | 20.55 | 19.71 | 19.43 | 17.18 | 17.46 | 27.3 | 20.27 | 23.92 | 17.18 | 17.18 | 260.4
| Total | 67.72 | 45.52 | 37.75 | 36.09 | 35.53 | 31.09 | 31.64 | 51.07 | 37.19 | 44.41 | 31.09 | 31.09 | 480.19
| 053 029 3190 TJ9935 CEIC |  | 2015-12-01: Power
| kWh Usage | 74600 | 75300 | 90000 | 64800 | 59400 | 53600 | 54300 | 38300 | 54900 | 58000 | 71300 | 77300 | 771800
| KW | 239 | 224 | 235 | 235 | 197 | 130 | 95 | 112 | 138 | 115 | 133 | 143 | 166.3333
| Days in period | 30 | 29 | 34 | 29 | 28 | 32 | 36 | 24 | 32 | 30 | 32 | 31
| Amount | 6220.14 | 6304.81 | 7173.55 | 4624.78 | 4310.92 | 3838.18 | 3646.13 | 3067.15 | 4092.07 | 4098.29 | 4910.81 | 5484.81 | 57771.64
| Lighting | 786.25 | 786.25 | 786.25 | 786.25 | 786.25 | 760.35 | 744.98 | 745.05 | 745.05 | 745.05 | 745.05 | 745.05 | 9161.83
| 7% Sales Tax | 490.45 | 496.37 | 557.19 | 378.77 | 356.8 | 321.9 | 307.38 | 266.85 | 338.6 | 339.03 | 395.91 | 436.09 | 4685.34
| Total Bill | 7496.84 | 7587.43 | 8516.99 | 5789.8 | 5453.97 | 4920.43 | 4698.49 | 4079.05 | 5175.72 | 5182.37 | 6051.77 | 6665.95 | 71618.81
| 1003287462001 859461 CEIC 413 Industrial Pk |  | 2015-12-01: Natural Gas
| Therms Used | 401 | 287 | 599 | 605 | 871 | 1332 | 1226 | 829 | 787 | 907 | 734 | 513 | 9091
| Amount | 302.98 | 223.1 | 441.72 | 456.88 | 618.98 | 934.86 | 841.65 | 576.24 | 530.48 | 641.9 | 523.8 | 374.12 | 6466.71
| State Sales Tax | 21.21 | 15.62 | 30.92 | 31.98 | 43.33 | 65.44 | 58.92 | 40.34 | 37.13 | 44.93 | 36.67 | 26.19 | 452.68
| Total Bill | 324.19 | 238.72 | 472.64 | 488.86 | 662.31 | 1000.3 | 900.57 | 616.58 | 567.61 | 686.83 | 560.47 | 400.31 | 6919.39
34 | ASU - Plemmons Student Union Addition | [17 empty] | ASU - Plemmons Student Union Addition
App State - Plemmons, Cone, Summit Utility Data
ELECTRICITY
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 227800 | 214280 | 225000 | 221480 | 190120 | 186400 | 149800 | 169880 | 176080 | 194280 | 202520 | 204080 | 185200 | 182360 | 221240 | 184480 | 192240 | 159400 | 93960 | 150160 | 161304.8 | 184936.24 | 200038.48 | 212508.96 | 164809.92 | 171163.76 | 191234.64 | 181865.2 | 160043.52 | 158691.04 | 162637.92 | 156600.48 | 163100.8 | 182870.4 | 170412.48 | 195797.84 | 172848.4 | 181802.96 | 239736.72 | 193410.72 | 167832.32 | 158616.24 | 151638.48 | 173009.88 | 145604.08 | 167482.6 | 163268.2 | 150024.64 | 154229.68 | 183066.16 | 210823.36 | 180406.32 | 182160 | 137900.16 | 104936.88 | 162981.44 | 159770.64 | 159117.6 | 129846.64 | 117536.08 | 126492.56 | 131062.96 | 176404.16 | 167466.72 | 120254 | 123945.44 | 113920.48 | 131483.76 | 147519.64 | 134698.84 | 141380.32 | 111725.04
315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 30920 | 42883 | 87000 | 89330 | 74095 | 65520 | 51680 | 65760 | 67200 | 67922 | 67325 | 54118 | 61002 | 47297 | 97209 | 82790 | 74640 | 78640 | 59040 | 75280 | 68445.6 | 81539.28 | 78760.56 | 70425.12 | 83354.24 | 95440.72 | 106644.08 | 90944.4 | 79893.44 | 75534.88 | 61110.24 | 77534.56 | 66657.6 | 76348.8 | 74618.56 | 100114.48 | 92674.8 | 96643.12 | 114833.84 | 95351.84 | 74287.04 | 71859.28 | 63800.56 | 84077.36 | 66297.76 | 75581.2 | 80548.4 | 73478.08 | 82502.96 | 96093.52 | 107641.92 | 86785.04 | 87720 | 67851.52 | 49305.36 | 64223.68 | 71256.08 | 72487.2 | 59208.08 | 61667.76 | 85574.32 | 64583.12 | 90419.52 | 94077.84 | 56724 | 57251.68 | 55614.56 | 56960.72 | 68456.08 | 57964.48 | 68523.04 | 67612.88
452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2649.6 | 3444.48 | 4680.96 | 12305.92 | 75868.84 | 94233.52 | 103495.28 | 93234.4 | 90349.04 | 82741.08 | 67491.84 | 96344.96 | 85841.6 | 96620.8 | 94928.96 | 110927.68 | 86316.8 | 107513.92 | 140709.44 | 116877.44 | 96720.64 | 88444.48 | 70200.96 | 106069.76 | 76516.16 | 90139.2 | 97414.4 | 90465.28 | 92359.36 | 103320.32 | 119614.72 | 100688.64 | 105280 | 82288.32 | 57837.76 | 96834.88 | 87713.28 | 101035.2 | 86505.28 | 86756.16 | 95653.12 | 104193.92 | 115816.32 | 104813.44 | 91664 | 78922.88 | 80144.96 | 80595.52 | 79393.28 | 96367.68 | 92576.64 | 83022.08
204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 15780.47 | 14844.63 | 15586.66 | 15343 | 13172.29 | 12914.8 | 11564.69 | 14007.85 | 14518.63 | 16018.03 | 16696.88 | 16825.4 | 15269.98 | 15036 | 18239.12 | 15210.66 | 15849.97 | 13144.46 | 7847.46 | 13989.73 | 14719.5 | 17232.4816 | 18638.2484 | 19799.0325 | 15359.0554 | 15950.5038 | 17818.7533 | 16946.6228 | 14915.3845 | 14789.4924 | 12597.1118 | 14489.8107 | 15087.0346 | 16885.8919 | 15705.2025 | 17941.6669 | 15826.806 | 16105.9043 | 21296.4452 | 17214.78 | 14999.8414 | 14213.2466 | 14023.0962 | 15671.5612 | 12939.7978 | 14853.0983 | 14424.6939 | 13218.7814 | 13631.797 | 16400.7839 | 18881.0127 | 16163.1111 | 16319.824 | 12364.9812 | 9731.4952 | 14281.8277 | 12335.0568 | 14192.4192 | 11589.51 | 10494.7948 | 11291.262 | 11697.6702 | 15729.616 | 14934.8507 | 10736.5003 | 11064.7504 | 10173.2963 | 11123.4077 | 11925.7743 | 10893.0468 | 11431.2475 | 9042.492
315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 2171.15 | 3005.4 | 6059.14 | 6220.42 | 5153.51 | 4559.95 | 4010.19 | 5442.32 | 5560.96 | 5620.45 | 5571.26 | 4483.21 | 5050.33 | 3921.26 | 8033.24 | 6845.34 | 6173.9 | 6503.44 | 4947.92 | 7032.02 | 6267.55 | 7604.4363 | 7345.7837 | 6569.8954 | 7773.3804 | 8898.4197 | 9941.2685 | 8479.8905 | 7451.2315 | 7045.5273 | 4741.0025 | 7186.1608 | 6173.8085 | 7059.0927 | 6888.4709 | 9205.3588 | 8520.2409 | 8598.2021 | 10227.8989 | 8508.3279 | 6649.7124 | 6446.9613 | 5908.2048 | 7624.8998 | 5899.6245 | 6712.9535 | 7134.1322 | 6494.8624 | 7323.4779 | 8600.9712 | 9632.8714 | 7769.2196 | 7852.7635 | 6077.4119 | 4566.7965 | 5603.3298 | 5155.8262 | 6460.4635 | 5279.6211 | 5498.3377 | 7624.2295 | 5757.5883 | 8055.0809 | 8380.3984 | 5058.7196 | 5105.6409 | 4960.0661 | 4814.7908 | 5528.75 | 4683.6496 | 5534.148 | 5460.8274
452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07 | 392.9622 | 890.9878 | 1979.8021 | 7087.7942 | 8797.3266 | 9659.2982 | 8704.2166 | 8435.684 | 7727.5203 | 5244.5257 | 8933.1385 | 7953.5968 | 8926.5754 | 8747.6766 | 10137.8643 | 7867.493 | 9500.1636 | 12473.9959 | 10394.3221 | 8649.9062 | 7939.7522 | 6503.649 | 9620.539 | 6814.5477 | 8000.3182 | 8603.7338 | 7962.9562 | 8147.895 | 9261.5649 | 10717.5459 | 9026.3993 | 9436.6725 | 7382.2669 | 5369.4083 | 8501.8725 | 7829.287 | 9013.9174 | 7721.859 | 7744.1675 | 8535.3185 | 9294.8014 | 10328.333 | 9349.9009 | 8180.5801 | 7047.5987 | 7156.2676 | 6821.3914 | 6424.5957 | 7791.8936 | 7486.5245 | 6716.9106
STEAM
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 519706.6 | 395410.8 | 316161.8 | 308654 | 493012.2 | 947651.2 | 982687.6 | 474659.8 | 401250.2 | 322001.2 | 351198.2 | 274451.8 | 37539 | 404587 | 459644.2 | 527214.4 | 569758.6 | 608966 | 654847 | 620644.8 | 524711.8 | 1393948.2 | 601458.2 | 583105.8 | 642334 | 733261.8 | 677370.4 | 742438 | 886754.6 | 978516.6 | 1117828 | 953490.6 | 797495.2 | 533888 | 681541.4 | 413763.2 | 726588.2 | 731593.4 | 461312.6 | 842542 | 674867.8 | 809174 | 1115325.4 | 682375.6 | 902604.4 | 724919.8 | 504691 | 397913.4 | 470488.8 | 685712.4 | 530551.2 | 722417.2 | 623981.6 | 528048.6 | 789153.2 | 609800.2 | 358706 | 418768.4 | 278622.8 | 205213.2 | 271115 | 312825 | 280291.2 | 475494 | 413763.2 | 394576.6 | 684044 | 611468.6 | 436286.6 | 301146.2 | 307819.8 | 281125.4
315 | Cone Residence Hall Steam Use in Lbs. | 41710 | 62565 | 100104 | 153492.8 | 163503.2 | 216892 | 296141 | 200208 | 166840 | 135140.4 | 94264.6 | 101772.4 | 79249 | 165171.6 | 141814 | 164337.4 | 206881.6 | 207048.44 | 208216.32 | 242752.2 | 211052.6 | 160166.4 | 82585.8 | 59228.2 | 65901.8 | 85922.6 | 171011 | 170176.8 | 208550 | 219394.6 | 291970 | 254848.1 | 229405 | 171011 | 145985 | 52554.6 | 59228.2 | 95933 | 132637.8 | 192700.2 | 214389.4 | 207715.8 | 381229.4 | 204379 | 255265.2 | 206881.6 | 81751.6 | 45881 | 58394 | 104275 | 66736 | 96767.2 | 230239.2 | 235244.4 | 264441.4 | 285296.4 | 182689.8 | 178518.8 | 96767.2 | 83420 | 45881 | 66736 | 118456.4 | 211886.8 | 203544.8 | 191031.8 | 271115 | 274451.8 | 215223.6 | 182689.8 | 118456.4 | 75078
452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210652.184 | 60696.392 | 83545.13 | 170660.636 | 189229.928 | 343473.508 | 382747.644 | 356320.188 | 498426.158 | 606463.4 | 623147.4 | 367048 | 385400.4 | 272783.4 | 340353.6 | 437120.8 | 359540.2 | 462981 | 530551.2 | 387068.8 | 846713 | 451302.2 | 542230 | 358706 | 216892 | 246923.2 | 286964.8 | 338685.2 | 325338 | 401250.2 | 513867.2 | 392074 | 658183.8 | 706567.4 | 491343.8 | 368716.4 | 207715.8 | 210218.4 | 180187.2 | 238581.2 | 311990.8 | 301980.4 | 437120.8 | 430447.2 | 718246.2 | 713241 | 376224.2 | 385400.4 | 283628 | 251928.4
204 & 445 | Plemmons Student Union Total Steam Cost | 22867.09 | 17398.08 | 13911.12 | 13580.78 | 21692.54 | 41696.65 | 43238.25 | 20885.04 | 17655.01 | 14168.05 | 15452.72 | 5764.08 | 788.4 | 8497.2 | 9653.52 | 11072.64 | 11966.16 | 12789.6 | 13753.2 | 13034.88 | 11020.08 | 29275.92 | 12631.92 | 12246.48 | 13490.4 | 15400.08 | 14226.24 | 15592.8 | 18623.76 | 20550.96 | 23476.8 | 20025.36 | 16749.12 | 11212.8 | 14313.84 | 8689.92 | 15259.92 | 15365.04 | 9688.56 | 17695.2 | 14173.68 | 16994.4 | 23424.24 | 14331.36 | 18956.64 | 15224.88 | 10599.6 | 8357.04 | 9881.28 | 14401.44 | 11142.72 | 15172.32 | 13104.96 | 11090.16 | 16573.92 | 12807.12 | 7533.6 | 8795.04 | 5851.68 | 4309.92 | 5694 | 6570 | 5886.72 | 9986.4 | 8689.92 | 8286.96 | 14366.4 | 12842.16 | 9162.96 | 6324.72 | 6464.88 | 5904.24
315 | Cone Residence Hall Steam Costs | 1835.24 | 2752.86 | 4404.58 | 6753.68 | 7194.14 | 9543.25 | 13030.2 | 8809.15 | 7340.96 | 5946.18 | 4147.64 | 2137.44 | 1664.4 | 3468.96 | 2978.4 | 3451.44 | 4344.96 | 4348.46 | 4372.99 | 5098.32 | 4432.56 | 3363.84 | 1734.48 | 1243.92 | 1384.08 | 1804.56 | 3591.6 | 3574.08 | 4380 | 4607.76 | 6132 | 5352.36 | 4818 | 3591.6 | 3066 | 1103.76 | 1243.92 | 2014.8 | 2785.68 | 4047.12 | 4502.64 | 4362.48 | 8006.64 | 4292.4 | 5361.12 | 4344.96 | 1716.96 | 963.6 | 1226.4 | 2190 | 1401.6 | 2032.32 | 4835.52 | 4940.64 | 5553.84 | 5991.84 | 3836.88 | 3749.28 | 2032.32 | 1752 | 963.6 | 1401.6 | 2487.84 | 4450.08 | 4274.88 | 4012.08 | 5694 | 5764.08 | 4520.16 | 3836.88 | 2487.84 | 1576.8
452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4424.15 | 1274.76 | 1754.66 | 3584.31 | 3974.24 | 7213.61 | 8038.46 | 7483.56 | 10467.99 | 14829.71 | 15237.68 | 8975.34 | 9424.1 | 6670.31 | 8322.59 | 10688.82 | 8791.75 | 11321.17 | 12973.44 | 9464.91 | 19687.45 | 11035.59 | 13259.03 | 8771.36 | 5303.61 | 6037.95 | 7017.09 | 8281.79 | 7955.42 | 9811.68 | 12565.47 | 9587.3 | 16094.42 | 17277.53 | 12014.72 | 9016.13 | 5079.23 | 5140.42 | 4406.07 | 5833.97 | 7629.04 | 7384.25 | 10688.82 | 10525.62 | 17563.11 | 17440.72 | 9199.72 | 9424.1 | 6935.49 | 6160.34
WATER & SEWER
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 227000 | 183000 | 225000 | 344000 | 215000 | 164000 | 101000 | 391000 | 303000 | 172000 | 150000 | 200400 | 209000 | 258000 | 385000 | 387000 | 287000 | 151000 | 196000 | 287000 | 294000 | 310000 | 145000 | 210000 | 278000 | 501000 | 459000 | 439000 | 368000 | 227000 | 500000 | 275000 | 181000 | 279000 | 200000 | 219000 | 244000 | 333000 | 427000 | 475900 | 456359 | 390001 | 507000 | 540918 | 183918 | 228589 | 211785 | 332555.459 | 156555 | 317243 | 336965 | 237687 | 161409 | 46000 | 87000 | 105000 | 210475 | 265606 | 163212 | 268457 | 252014 | 322375 | 368441 | 253901 | 185426 | 92000 | 603000 | 290000 | 231245 | 300786 | 189327 | 314358
315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 20000 | 83000 | 139000 | 174000 | 119000 | 108000 | 53000 | 231000 | 190000 | 54000 | 27000 | 6000 | 12000 | 81000 | 174000 | 147000 | 146000 | 93000 | 112000 | 196000 | 164000 | 158000 | 65000 | 18000 | 27000 | 114000 | 166000 | 176000 | 172000 | 77000 | 129000 | 170000 | 133000 | 167000 | 113000 | 86000 | 150000 | 128000 | 190000 | 224300 | 173473 | 80000 | 185000 | 190346 | 140346 | 186283 | 77895 | 33085.173 | 78085 | 159621 | 217355 | 226089 | 160823 | 79000 | 145000 | 180000 | 144325 | 184882 | 51764 | 63279 | 52258 | 146625 | 200127 | 186747 | 161422 | 75000 | 146000 | 183000 | 135515 | 196342 | 105169 | 121026
452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5992 | 32528 | 100152 | 205440 | 208008 | 197736 | 89880 | 160072 | 212288 | 172056 | 219136 | 77896 | 11128 | 11128 | 139528 | 218280 | 274768 | 222064 | 95872 | 182328 | 224152 | 172792 | 245264 | 117648 | 78184.368 | 95304 | 233136 | 314680 | 307224 | 239768 | 115000 | 229000 | 308000 | 400200 | 342512 | 79024 | 74264 | 98728 | 214000 | 289432 | 263352 | 217152 | 96000 | 201000 | 258000 | 203240 | 310872 | 123504 | 88616
204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 2093.02 | 1370.77 | 1567.19 | 2355.2 | 1751.58 | 1112.4 | 702.32 | 2027.61 | 1806.48 | 1939.76 | 1447.95 | 1348.36 | 1842.05 | 1678.25 | 2296 | 3225.7 | 3158.8 | 2030.4 | 1351.5 | 1658.65 | 2290.3 | 3059.25 | 2194.5 | 2112 | 1325.3 | 2441.1 | 4465.2 | 3722.6 | 3126.7 | 2551.7 | 2913.5 | 2847 | 2453.7 | 2472.6 | 3117.5 | 2551.5 | 3401.1 | 3105.9 | 3993.7 | 4651.87 | 5036.2027 | 5584.5 | 5330.1 | 6721.467 | 3878.967 | 2495.034 | 2707.638 | 4023.6185 | 2575.653 | 2496.5935 | 2933.109 | 4512.8395 | 3101.9266 | 1851.3 | 918.7 | 1789 | 2180.185 | 2829.9542 | 2685.5568 | 2739.3533 | 2611.6672 | 2612.7125 | 2888.6671 | 4002.3674 | 2559.3004 | 1803.9 | 2809.4 | 2093.5 | 2539.474 | 2435.251 | 3124.9236 | 3712.1714
315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 91.64 | 273.77 | 1081.38 | 1295.16 | 1062.99 | 859.46 | 529.02 | 1387.37 | 1148.25 | 1097.17 | 662.24 | 199.4 | 114.9 | 301.5 | 861.15 | 1559.7 | 1444.65 | 1232.2 | 1012.75 | 1203.2 | 1681.8 | 1794.6 | 1224.5 | 535.15 | 221.45 | 602.15 | 1095.55 | 1536.15 | 1584.55 | 1415.95 | 969.05 | 1568.75 | 1608.35 | 1646.05 | 1822.75 | 1223.75 | 1805.75 | 1544.15 | 1671.75 | 2134.24 | 2191.1569 | 1597.75 | 1582.75 | 2376.999 | 2081.999 | 1987.448 | 1603.436 | 599.4195 | 440.441 | 1092.0445 | 1432.873 | 3212.0065 | 2584.3402 | 1804.45 | 1124.25 | 2339.75 | 1863.145 | 1993.0774 | 1524.0396 | 725.8751 | 553.8384 | 835.9875 | 1462.8937 | 2601.4278 | 2071.6788 | 1566 | 1072.3 | 1747.6 | 1924.178 | 1536.197 | 1960.6492 | 1658.5158
452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.74 | 100.84 | 2320.58 | 6556.74 | 603.22 | 573.43 | 413.45 | 592.27 | 955.3 | 722.64 | 1604.7 | 1894.11 | 568.17 | 194.27 | 770.52 | 1875.28 | 2525.21 | 2638.7704 | 1900.79 | 1666.76 | 2584.974 | 2497.664 | 2537.948 | 2148.846 | 1009.822 | 633.346 | 1406.862 | 1949.418 | 4373.154 | 3588.0332 | 2602.75 | 1725.65 | 3868.55 | 3882.17 | 4533.0684 | 2690.0036 | 902.6716 | 702.3944 | 1252.7 | 2029.2392 | 3633.3048 | 2831.1208 | 2061.2 | 1427.8 | 2430.1 | 2773.848 | 2317.552 | 2771.3272 | 1451.5128
35 | ASU - Summit Residence Hall and Appalachian Hall | 2011-12-01: ASU - Summit Residence Hall and Appalachian Hall
App State - Plemmons, Cone, Summit Utility Data
ELECTRICITY
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 227800 | 214280 | 225000 | 221480 | 190120 | 186400 | 149800 | 169880 | 176080 | 194280 | 202520 | 204080 | 185200 | 182360 | 221240 | 184480 | 192240 | 159400 | 93960 | 150160 | 161304.8 | 184936.24 | 200038.48 | 212508.96 | 164809.92 | 171163.76 | 191234.64 | 181865.2 | 160043.52 | 158691.04 | 162637.92 | 156600.48 | 163100.8 | 182870.4 | 170412.48 | 195797.84 | 172848.4 | 181802.96 | 239736.72 | 193410.72 | 167832.32 | 158616.24 | 151638.48 | 173009.88 | 145604.08 | 167482.6 | 163268.2 | 150024.64 | 154229.68 | 183066.16 | 210823.36 | 180406.32 | 182160 | 137900.16 | 104936.88 | 162981.44 | 159770.64 | 159117.6 | 129846.64 | 117536.08 | 126492.56 | 131062.96 | 176404.16 | 167466.72 | 120254 | 123945.44 | 113920.48 | 131483.76 | 147519.64 | 134698.84 | 141380.32 | 111725.04
315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 30920 | 42883 | 87000 | 89330 | 74095 | 65520 | 51680 | 65760 | 67200 | 67922 | 67325 | 54118 | 61002 | 47297 | 97209 | 82790 | 74640 | 78640 | 59040 | 75280 | 68445.6 | 81539.28 | 78760.56 | 70425.12 | 83354.24 | 95440.72 | 106644.08 | 90944.4 | 79893.44 | 75534.88 | 61110.24 | 77534.56 | 66657.6 | 76348.8 | 74618.56 | 100114.48 | 92674.8 | 96643.12 | 114833.84 | 95351.84 | 74287.04 | 71859.28 | 63800.56 | 84077.36 | 66297.76 | 75581.2 | 80548.4 | 73478.08 | 82502.96 | 96093.52 | 107641.92 | 86785.04 | 87720 | 67851.52 | 49305.36 | 64223.68 | 71256.08 | 72487.2 | 59208.08 | 61667.76 | 85574.32 | 64583.12 | 90419.52 | 94077.84 | 56724 | 57251.68 | 55614.56 | 56960.72 | 68456.08 | 57964.48 | 68523.04 | 67612.88
452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2649.6 | 3444.48 | 4680.96 | 12305.92 | 75868.84 | 94233.52 | 103495.28 | 93234.4 | 90349.04 | 82741.08 | 67491.84 | 96344.96 | 85841.6 | 96620.8 | 94928.96 | 110927.68 | 86316.8 | 107513.92 | 140709.44 | 116877.44 | 96720.64 | 88444.48 | 70200.96 | 106069.76 | 76516.16 | 90139.2 | 97414.4 | 90465.28 | 92359.36 | 103320.32 | 119614.72 | 100688.64 | 105280 | 82288.32 | 57837.76 | 96834.88 | 87713.28 | 101035.2 | 86505.28 | 86756.16 | 95653.12 | 104193.92 | 115816.32 | 104813.44 | 91664 | 78922.88 | 80144.96 | 80595.52 | 79393.28 | 96367.68 | 92576.64 | 83022.08
204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 15780.47 | 14844.63 | 15586.66 | 15343 | 13172.29 | 12914.8 | 11564.69 | 14007.85 | 14518.63 | 16018.03 | 16696.88 | 16825.4 | 15269.98 | 15036 | 18239.12 | 15210.66 | 15849.97 | 13144.46 | 7847.46 | 13989.73 | 14719.5 | 17232.4816 | 18638.2484 | 19799.0325 | 15359.0554 | 15950.5038 | 17818.7533 | 16946.6228 | 14915.3845 | 14789.4924 | 12597.1118 | 14489.8107 | 15087.0346 | 16885.8919 | 15705.2025 | 17941.6669 | 15826.806 | 16105.9043 | 21296.4452 | 17214.78 | 14999.8414 | 14213.2466 | 14023.0962 | 15671.5612 | 12939.7978 | 14853.0983 | 14424.6939 | 13218.7814 | 13631.797 | 16400.7839 | 18881.0127 | 16163.1111 | 16319.824 | 12364.9812 | 9731.4952 | 14281.8277 | 12335.0568 | 14192.4192 | 11589.51 | 10494.7948 | 11291.262 | 11697.6702 | 15729.616 | 14934.8507 | 10736.5003 | 11064.7504 | 10173.2963 | 11123.4077 | 11925.7743 | 10893.0468 | 11431.2475 | 9042.492
315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 2171.15 | 3005.4 | 6059.14 | 6220.42 | 5153.51 | 4559.95 | 4010.19 | 5442.32 | 5560.96 | 5620.45 | 5571.26 | 4483.21 | 5050.33 | 3921.26 | 8033.24 | 6845.34 | 6173.9 | 6503.44 | 4947.92 | 7032.02 | 6267.55 | 7604.4363 | 7345.7837 | 6569.8954 | 7773.3804 | 8898.4197 | 9941.2685 | 8479.8905 | 7451.2315 | 7045.5273 | 4741.0025 | 7186.1608 | 6173.8085 | 7059.0927 | 6888.4709 | 9205.3588 | 8520.2409 | 8598.2021 | 10227.8989 | 8508.3279 | 6649.7124 | 6446.9613 | 5908.2048 | 7624.8998 | 5899.6245 | 6712.9535 | 7134.1322 | 6494.8624 | 7323.4779 | 8600.9712 | 9632.8714 | 7769.2196 | 7852.7635 | 6077.4119 | 4566.7965 | 5603.3298 | 5155.8262 | 6460.4635 | 5279.6211 | 5498.3377 | 7624.2295 | 5757.5883 | 8055.0809 | 8380.3984 | 5058.7196 | 5105.6409 | 4960.0661 | 4814.7908 | 5528.75 | 4683.6496 | 5534.148 | 5460.8274
452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07 | 392.9622 | 890.9878 | 1979.8021 | 7087.7942 | 8797.3266 | 9659.2982 | 8704.2166 | 8435.684 | 7727.5203 | 5244.5257 | 8933.1385 | 7953.5968 | 8926.5754 | 8747.6766 | 10137.8643 | 7867.493 | 9500.1636 | 12473.9959 | 10394.3221 | 8649.9062 | 7939.7522 | 6503.649 | 9620.539 | 6814.5477 | 8000.3182 | 8603.7338 | 7962.9562 | 8147.895 | 9261.5649 | 10717.5459 | 9026.3993 | 9436.6725 | 7382.2669 | 5369.4083 | 8501.8725 | 7829.287 | 9013.9174 | 7721.859 | 7744.1675 | 8535.3185 | 9294.8014 | 10328.333 | 9349.9009 | 8180.5801 | 7047.5987 | 7156.2676 | 6821.3914 | 6424.5957 | 7791.8936 | 7486.5245 | 6716.9106
STEAM
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 519706.6 | 395410.8 | 316161.8 | 308654 | 493012.2 | 947651.2 | 982687.6 | 474659.8 | 401250.2 | 322001.2 | 351198.2 | 274451.8 | 37539 | 404587 | 459644.2 | 527214.4 | 569758.6 | 608966 | 654847 | 620644.8 | 524711.8 | 1393948.2 | 601458.2 | 583105.8 | 642334 | 733261.8 | 677370.4 | 742438 | 886754.6 | 978516.6 | 1117828 | 953490.6 | 797495.2 | 533888 | 681541.4 | 413763.2 | 726588.2 | 731593.4 | 461312.6 | 842542 | 674867.8 | 809174 | 1115325.4 | 682375.6 | 902604.4 | 724919.8 | 504691 | 397913.4 | 470488.8 | 685712.4 | 530551.2 | 722417.2 | 623981.6 | 528048.6 | 789153.2 | 609800.2 | 358706 | 418768.4 | 278622.8 | 205213.2 | 271115 | 312825 | 280291.2 | 475494 | 413763.2 | 394576.6 | 684044 | 611468.6 | 436286.6 | 301146.2 | 307819.8 | 281125.4
315 | Cone Residence Hall Steam Use in Lbs. | 41710 | 62565 | 100104 | 153492.8 | 163503.2 | 216892 | 296141 | 200208 | 166840 | 135140.4 | 94264.6 | 101772.4 | 79249 | 165171.6 | 141814 | 164337.4 | 206881.6 | 207048.44 | 208216.32 | 242752.2 | 211052.6 | 160166.4 | 82585.8 | 59228.2 | 65901.8 | 85922.6 | 171011 | 170176.8 | 208550 | 219394.6 | 291970 | 254848.1 | 229405 | 171011 | 145985 | 52554.6 | 59228.2 | 95933 | 132637.8 | 192700.2 | 214389.4 | 207715.8 | 381229.4 | 204379 | 255265.2 | 206881.6 | 81751.6 | 45881 | 58394 | 104275 | 66736 | 96767.2 | 230239.2 | 235244.4 | 264441.4 | 285296.4 | 182689.8 | 178518.8 | 96767.2 | 83420 | 45881 | 66736 | 118456.4 | 211886.8 | 203544.8 | 191031.8 | 271115 | 274451.8 | 215223.6 | 182689.8 | 118456.4 | 75078
452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210652.184 | 60696.392 | 83545.13 | 170660.636 | 189229.928 | 343473.508 | 382747.644 | 356320.188 | 498426.158 | 606463.4 | 623147.4 | 367048 | 385400.4 | 272783.4 | 340353.6 | 437120.8 | 359540.2 | 462981 | 530551.2 | 387068.8 | 846713 | 451302.2 | 542230 | 358706 | 216892 | 246923.2 | 286964.8 | 338685.2 | 325338 | 401250.2 | 513867.2 | 392074 | 658183.8 | 706567.4 | 491343.8 | 368716.4 | 207715.8 | 210218.4 | 180187.2 | 238581.2 | 311990.8 | 301980.4 | 437120.8 | 430447.2 | 718246.2 | 713241 | 376224.2 | 385400.4 | 283628 | 251928.4
204 & 445 | Plemmons Student Union Total Steam Cost | 22867.09 | 17398.08 | 13911.12 | 13580.78 | 21692.54 | 41696.65 | 43238.25 | 20885.04 | 17655.01 | 14168.05 | 15452.72 | 5764.08 | 788.4 | 8497.2 | 9653.52 | 11072.64 | 11966.16 | 12789.6 | 13753.2 | 13034.88 | 11020.08 | 29275.92 | 12631.92 | 12246.48 | 13490.4 | 15400.08 | 14226.24 | 15592.8 | 18623.76 | 20550.96 | 23476.8 | 20025.36 | 16749.12 | 11212.8 | 14313.84 | 8689.92 | 15259.92 | 15365.04 | 9688.56 | 17695.2 | 14173.68 | 16994.4 | 23424.24 | 14331.36 | 18956.64 | 15224.88 | 10599.6 | 8357.04 | 9881.28 | 14401.44 | 11142.72 | 15172.32 | 13104.96 | 11090.16 | 16573.92 | 12807.12 | 7533.6 | 8795.04 | 5851.68 | 4309.92 | 5694 | 6570 | 5886.72 | 9986.4 | 8689.92 | 8286.96 | 14366.4 | 12842.16 | 9162.96 | 6324.72 | 6464.88 | 5904.24
315 | Cone Residence Hall Steam Costs | 1835.24 | 2752.86 | 4404.58 | 6753.68 | 7194.14 | 9543.25 | 13030.2 | 8809.15 | 7340.96 | 5946.18 | 4147.64 | 2137.44 | 1664.4 | 3468.96 | 2978.4 | 3451.44 | 4344.96 | 4348.46 | 4372.99 | 5098.32 | 4432.56 | 3363.84 | 1734.48 | 1243.92 | 1384.08 | 1804.56 | 3591.6 | 3574.08 | 4380 | 4607.76 | 6132 | 5352.36 | 4818 | 3591.6 | 3066 | 1103.76 | 1243.92 | 2014.8 | 2785.68 | 4047.12 | 4502.64 | 4362.48 | 8006.64 | 4292.4 | 5361.12 | 4344.96 | 1716.96 | 963.6 | 1226.4 | 2190 | 1401.6 | 2032.32 | 4835.52 | 4940.64 | 5553.84 | 5991.84 | 3836.88 | 3749.28 | 2032.32 | 1752 | 963.6 | 1401.6 | 2487.84 | 4450.08 | 4274.88 | 4012.08 | 5694 | 5764.08 | 4520.16 | 3836.88 | 2487.84 | 1576.8
452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4424.15 | 1274.76 | 1754.66 | 3584.31 | 3974.24 | 7213.61 | 8038.46 | 7483.56 | 10467.99 | 14829.71 | 15237.68 | 8975.34 | 9424.1 | 6670.31 | 8322.59 | 10688.82 | 8791.75 | 11321.17 | 12973.44 | 9464.91 | 19687.45 | 11035.59 | 13259.03 | 8771.36 | 5303.61 | 6037.95 | 7017.09 | 8281.79 | 7955.42 | 9811.68 | 12565.47 | 9587.3 | 16094.42 | 17277.53 | 12014.72 | 9016.13 | 5079.23 | 5140.42 | 4406.07 | 5833.97 | 7629.04 | 7384.25 | 10688.82 | 10525.62 | 17563.11 | 17440.72 | 9199.72 | 9424.1 | 6935.49 | 6160.34
WATER & SEWER
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 227000 | 183000 | 225000 | 344000 | 215000 | 164000 | 101000 | 391000 | 303000 | 172000 | 150000 | 200400 | 209000 | 258000 | 385000 | 387000 | 287000 | 151000 | 196000 | 287000 | 294000 | 310000 | 145000 | 210000 | 278000 | 501000 | 459000 | 439000 | 368000 | 227000 | 500000 | 275000 | 181000 | 279000 | 200000 | 219000 | 244000 | 333000 | 427000 | 475900 | 456359 | 390001 | 507000 | 540918 | 183918 | 228589 | 211785 | 332555.459 | 156555 | 317243 | 336965 | 237687 | 161409 | 46000 | 87000 | 105000 | 210475 | 265606 | 163212 | 268457 | 252014 | 322375 | 368441 | 253901 | 185426 | 92000 | 603000 | 290000 | 231245 | 300786 | 189327 | 314358
315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 20000 | 83000 | 139000 | 174000 | 119000 | 108000 | 53000 | 231000 | 190000 | 54000 | 27000 | 6000 | 12000 | 81000 | 174000 | 147000 | 146000 | 93000 | 112000 | 196000 | 164000 | 158000 | 65000 | 18000 | 27000 | 114000 | 166000 | 176000 | 172000 | 77000 | 129000 | 170000 | 133000 | 167000 | 113000 | 86000 | 150000 | 128000 | 190000 | 224300 | 173473 | 80000 | 185000 | 190346 | 140346 | 186283 | 77895 | 33085.173 | 78085 | 159621 | 217355 | 226089 | 160823 | 79000 | 145000 | 180000 | 144325 | 184882 | 51764 | 63279 | 52258 | 146625 | 200127 | 186747 | 161422 | 75000 | 146000 | 183000 | 135515 | 196342 | 105169 | 121026
452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5992 | 32528 | 100152 | 205440 | 208008 | 197736 | 89880 | 160072 | 212288 | 172056 | 219136 | 77896 | 11128 | 11128 | 139528 | 218280 | 274768 | 222064 | 95872 | 182328 | 224152 | 172792 | 245264 | 117648 | 78184.368 | 95304 | 233136 | 314680 | 307224 | 239768 | 115000 | 229000 | 308000 | 400200 | 342512 | 79024 | 74264 | 98728 | 214000 | 289432 | 263352 | 217152 | 96000 | 201000 | 258000 | 203240 | 310872 | 123504 | 88616
204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 2093.02 | 1370.77 | 1567.19 | 2355.2 | 1751.58 | 1112.4 | 702.32 | 2027.61 | 1806.48 | 1939.76 | 1447.95 | 1348.36 | 1842.05 | 1678.25 | 2296 | 3225.7 | 3158.8 | 2030.4 | 1351.5 | 1658.65 | 2290.3 | 3059.25 | 2194.5 | 2112 | 1325.3 | 2441.1 | 4465.2 | 3722.6 | 3126.7 | 2551.7 | 2913.5 | 2847 | 2453.7 | 2472.6 | 3117.5 | 2551.5 | 3401.1 | 3105.9 | 3993.7 | 4651.87 | 5036.2027 | 5584.5 | 5330.1 | 6721.467 | 3878.967 | 2495.034 | 2707.638 | 4023.6185 | 2575.653 | 2496.5935 | 2933.109 | 4512.8395 | 3101.9266 | 1851.3 | 918.7 | 1789 | 2180.185 | 2829.9542 | 2685.5568 | 2739.3533 | 2611.6672 | 2612.7125 | 2888.6671 | 4002.3674 | 2559.3004 | 1803.9 | 2809.4 | 2093.5 | 2539.474 | 2435.251 | 3124.9236 | 3712.1714
315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 91.64 | 273.77 | 1081.38 | 1295.16 | 1062.99 | 859.46 | 529.02 | 1387.37 | 1148.25 | 1097.17 | 662.24 | 199.4 | 114.9 | 301.5 | 861.15 | 1559.7 | 1444.65 | 1232.2 | 1012.75 | 1203.2 | 1681.8 | 1794.6 | 1224.5 | 535.15 | 221.45 | 602.15 | 1095.55 | 1536.15 | 1584.55 | 1415.95 | 969.05 | 1568.75 | 1608.35 | 1646.05 | 1822.75 | 1223.75 | 1805.75 | 1544.15 | 1671.75 | 2134.24 | 2191.1569 | 1597.75 | 1582.75 | 2376.999 | 2081.999 | 1987.448 | 1603.436 | 599.4195 | 440.441 | 1092.0445 | 1432.873 | 3212.0065 | 2584.3402 | 1804.45 | 1124.25 | 2339.75 | 1863.145 | 1993.0774 | 1524.0396 | 725.8751 | 553.8384 | 835.9875 | 1462.8937 | 2601.4278 | 2071.6788 | 1566 | 1072.3 | 1747.6 | 1924.178 | 1536.197 | 1960.6492 | 1658.5158
452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.74 | 100.84 | 2320.58 | 6556.74 | 603.22 | 573.43 | 413.45 | 592.27 | 955.3 | 722.64 | 1604.7 | 1894.11 | 568.17 | 194.27 | 770.52 | 1875.28 | 2525.21 | 2638.7704 | 1900.79 | 1666.76 | 2584.974 | 2497.664 | 2537.948 | 2148.846 | 1009.822 | 633.346 | 1406.862 | 1949.418 | 4373.154 | 3588.0332 | 2602.75 | 1725.65 | 3868.55 | 3882.17 | 4533.0684 | 2690.0036 | 902.6716 | 702.3944 | 1252.7 | 2029.2392 | 3633.3048 | 2831.1208 | 2061.2 | 1427.8 | 2430.1 | 2773.848 | 2317.552 | 2771.3272 | 1451.5128
36 | UNCW - MARBIONC | 2011-12-01: UNCW - MARBIONC
37 | DOA - NC State Bar HQ | 2011-12-01: DOA - NC State Bar HQ
The North Carolina State Bar-Electricity and Water Usage 6/2015 thru 8/2016
| Utility | 2010-07-01: 2015-06-01; 2010-08-01: 2015-07-01; 2010-09-01: 2015-08-01; 2010-10-01: 2015-09-01; 2010-11-01: 2015-10-01; 2010-12-01: 2015-11-01; 2011-01-01: 2015-12-01; 2011-02-01: 2016-01-01; 2011-03-01: 2016-02-01; 2011-04-01: 2016-03-01; 2011-05-01: 2016-04-01; 2011-06-01: 2016-05-01; 2011-07-01: 2016-06-01; 2011-08-01: 2016-07-01; 2011-09-01: 2016-08-01
| Electricity Usage (KWhs) | 2010-07-01: 71200; 2010-08-01: 77200; 2010-09-01: 67600; 2010-10-01: 68400; 2010-11-01: 81800; 2010-12-01: 67800; 2011-01-01: 84600; 2011-02-01: 87200; 2011-03-01: 81400; 2011-04-01: 83000; 2011-05-01: 85600; 2011-06-01: 78800; 2011-07-01: 74800; 2011-09-01: 0
| Water Usage (CCF) | 2010-07-01: 24; 2010-08-01: 37; 2010-09-01: 20; 2010-10-01: 19; 2010-11-01: 19; 2010-12-01: 23; 2011-01-01: 25; 2011-02-01: 23; 2011-03-01: 25; 2011-04-01: 27; 2011-05-01: 28; 2011-06-01: 29; 2011-07-01: 32; 2011-08-01: 28; 2011-09-01: 0
0
| Elecricity Cost ($) | 2010-07-01: 6484.38; 2010-08-01: 6845.41; 2010-09-01: 6114.04; 2010-10-01: 6267.63; 2010-11-01: 7319.38; 2010-12-01: 6252.8; 2011-01-01: 7471.3; 2011-02-01: 7540.61; 2011-03-01: 7276.39; 2011-04-01: 7457.85; 2011-05-01: 7520.86; 2011-06-01: 7030.4; 2011-07-01: 6664.63; 2011-09-01: 0
| Water-Sewer Costs ($) | 2010-07-01: 431.71; 2010-08-01: 550.57; 2010-09-01: 423.54; 2010-10-01: 416.07; 2010-11-01: 416.07; 2010-12-01: 445.96; 2011-01-01: 460.91; 2011-02-01: 445.96; 2011-03-01: 460.91; 2011-04-01: 475.85; 2011-05-01: 483.32; 2011-06-01: 490.79; 2011-07-01: 513.21; 2011-08-01: 535.55; 2011-09-01: 0
38 | FSU - Science and Technology Building | 2011-12-01: FSU - Science and Technology Building
39 | UNCW - Student Rec Facility Addition | 2011-12-01: UNCW - Student Rec Facility Addition
40 | WSSU - Reaves Student Activities Center | 2011-12-01: WSSU - Reaves Student Activities Center
Winston-Salem State University, D. J. Reeves Student Activities Center
| Utility |  | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
| Electricity (KWH) building meter |  | 68049 | 94819 | 105441 | 110223 | 95645 | 74913 | 102885 | 104979 | 103536 | 106757 | 64417 | 69747
| Steam from Central Plant (lbs) - natural gas therms |  | 0 | 0 | 0 | 0 | 0 | 7394.553 | 9386.719 | 7926.583 | 7099.156 | 5846.022 | 2908.071 | 0
| Chilled Water from Central Plant (Dtherms) kwh |  | 124193.4309 | 144505.6921 | 109863.1534 | 63533.9859 | 42945.056 | 59940.8656 | 56182.7266 | 88921.1862 | 75964.8736 | 138779.1636 | 115908.7776 | 144395.1586
| Natural Gas (Therms) other than from central steam plant |  | 2270 | 1660 | 2451 | 2683 | 2616 | 866 | 993 | 1519 | 710 | 640 | 1246 | 1849
| Water (CCF) |  | 23.01 | 78.56 | 101.36 | 90.88 | 89.03 | 30.44 | 79.81 | 99.14 | 47.85 | 102.66 | 32.37 | 23.2
| Electricity Cost ($) building meter x blended rate ($.0712/kwh) |  | 4845.0888 | 6751.1128 | 7507.3992 | 7847.8776 | 6809.924 | 5333.8056 | 7325.412 | 7474.5048 | 7371.7632 | 7601.0984 | 4586.4904 | 4965.9864
| Steam from Central Plant Cost ($) for Natural Gas |  | 0 | 0 | 0 | 0 | 0 | 3140.6445 | 4000.468 | 3244.9456 | 2574.7563 | 2300.8264 | 1213.8501 | 0
| Chilled Water from Central Plant Cost ($) kwh x $.0712/kwh |  | 8842.5723 | 10288.8053 | 7822.2565 | 4523.6198 | 3057.688 | 4267.7896 | 4000.2101 | 6331.1885 | 5408.699 | 9881.0764 | 8252.705 | 10280.9353
| Natural Gas Costs ($) other than from central steam. |  | 1612.59 | 1185.16 | 1739.42 | 1960.98 | 1814.46 | 616.05 | 685.88 | 1037.54 | 477.13 | 459.41 | 873.7 | 1291.14
| Water Costs ($) |  | 246.91 | 601.78 | 735.99 | 695.22 | 697.01 | 334.83 | 613.28 | 752.5 | 411.1 | 779 | 325.88 | 267.08
41 | Haywood Community College - Creative Arts Building | [17 empty] | Haywood Community College - Creative Arts Building
Haywood Community College - Creative Arts Building
| Utility | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01
| Electricity (KWhs) | 27170.48 | 22042 | 20689.61 | 19381 | 17218.59 | 20494.68 | 22876.24 | 22344 | 18131 | 22855.6 | 23879.83 | 27520.965
| Natural Gas (Therms) | 270 | 593 | 1089 | 1466 | 2214 | 1547 | 1029 | 498 | 217 | 0 | 0 | 39
| Water (gallons) | 27350 | 9686.76 | 7171.124 | 4935 | 7080 | 7742 | 7905.5 | 9036.81 | 6305.3 | 11924 | 13898.476 | 2851
| Electricity Cost ($) | 2717.048 | 2204.2 | 2068.961 | 1938.1 | 1721.859 | 2049.468 | 2287.624 | 2234.4 | 1813.1 | 2285.56 | 2387.983 | 2752.0965
| Natural Gas Costs ($) | 224.54 | 450.62 | 751.28 | 958.61 | 1357.35 | 963.8 | 672 | 359.33 | 167.13 | 15.63 | 16 | 45.4
42 | UNCC - Belk Residence Hall | [17 empty] | UNCC - Belk Residence Hall
| Belk Residence Hall |  | 2015-07-01: 10-08450-02A
| 178136 | Jul '15 | Aug '15 | Sep '15 | Oct '15 | Nov '15 | Dec '15 | Jan '16 | Feb '16 | Mar '16 | Apr '16 | May '16 | Jun '16
Consumption
| Electric (KWH) | 198506 | 163733 | 163642 | 152567.2 | 142257 | 131679.1 | 136880 | 135495 | 143859.8 | 156668.8 | 148419.1 | 158055
| Nat Gas (Therms) | 2684 | 2067 | 2465 | 2291 | 1827 | 2694 | 3702 | 3920 | 2632 | 2129 | 2308 | 1587
| Water (CF) | 14453.2086 | 85831.5508 | 89032.0856 | 83711.2299 | 59041.4439 | 36978.6096 | 81380 | 33919 | 94720 | 68565 | 29394 | 79588
Costs $
| Electric | 13252.3581 | 10935.9333 | 10936.8029 | 9323.105 | 8003.9337 | 7414.7427 | 7750.2735 | 7911.3544 | 8467.7842 | 8990.3524 | 8691.5358 | 10207.8866
| Nat Gas | 1902.68 | 1470.35 | 1749.23 | 1627.3 | 1293.11 | 1874.09 | 2516.86 | 2642.76 | 1781.65 | 1451.36 | 1599.43 | 1110.06
| Water | 1077.2433 | 6486.5304 | 6815.8567 | 6859.4317 | 4873.362 | 3169.3811 | 7541.6339 | 2811.9189 | 7781.3948 | 5539.7523 | 2320.9257 | 5226.4898
| BTU/GSF | 5308.879 | 4296.4757 | 4518.1575 | 4208.3537 | 3750.3979 | 4034.4966 | 4699.974 | 4795.8242 | 4232.9997 | 4195.9736 | 4138.4446 | 3918.2628 | 52098.2392
43 | NCSU - Early College High School / Cherry Building Renovation | [17 empty] | NCSU - Cherry Building Renovation
NCSU - Early College High School/Cherry
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 30902.9541 | 29335.022 | 22770.0195 | 23882.9956 | 21528.0151 | 27824.9512 | 28780.0293 | 28239.9902 | 28801.0254 | 29156.0059 | 30916.9922 | 31935.9741 |  | 334073.9746 | kwh |  | 1139.0292 | MMbtu
| Water (CCF) |  | 18.8182 | 14.5333 | 11.919 | 12.0143 | 7.6 | 7.669 | 9.5453 | 10.3675 | 11.4182 | 12.4032 | 10.8429 | 7 |  | 134.131 | CCF |  | 100329.9897 | gallons
| Natural Gas (therms) |  | 52.8824 | 113.5378 | 230.9699 | 184.7368 | 558.4539 | 1281.6964 | 1331.601 | 707.8276 | 295.1786 | 218.9464 | 176.0179 | 130.8942 |  | 5282.7429 | therms |  | 5282.7429 | thrms
| Electric Cost ($) |  | 2657.6541 | 2522.8119 | 1958.2217 | 2053.9376 | 1851.4093 | 2392.9458 | 2475.0825 | 2428.6392 | 2476.8882 | 2507.4165 | 2658.8613 | 2778.4297 |  | 28762.2978 | $
| Water Cost ($) |  | 173.1273 | 133.7067 | 109.6552 | 110.5314 | 69.92 | 70.5545 | 87.8169 | 95.3813 | 105.0473 | 114.1097 | 99.7549 | 65.31 |  | 1234.9152 | $
| Natural Gas ($) |  | 51.7275 | 101.4221 | 255.4112 | 260.3684 | 428.602 | 818.2254 | 835.5763 | 465.7004 | 217.8637 | 168.2168 | 138.6907 | 108.6458 |  | 3850.4501 | $
44 | UNCC - Hunt Residence Hall | [17 empty] | UNCC - Hunt Residence Hall
| Hunt Residence Hall |  | 2015-08-01: 10-08610-03A
| 132405 | Jul '15 | Aug '15 | Sep '15 | Oct '15 | Nov '15 | Dec '15 | Jan '16 | Feb '16 | Mar '16 | Apr '16 | May '16 | Jun '16
Consumption
| Electric (KWH) | 72541 | 83889 | 100939 | 102210 | 97671 | 93457 | 93202 | 92374 | 91453 | 90879 | 73565 | 27670
| Nat Gas (Therms) | 111 | 237 | 226 | 710 | 870 | 725 | 669 | 1016 | 893 | 856 | 691 | 228
| Water (CF) | 3009 | 20503 | 42490 | 40544 | 37565 | 27110 | 33128 | 42047 | 35614 | 42330 | 22460 | 8959
| Chill water mmBTU (BTUX10^6) | 489 | 472 | 428 | 211 | 136 | 120 | 53 | 79 | 191 | 244 | 260 | 384
| Hot water mmBTU | 41 | 21 | 17 | 86 | 87 | 73 | 28 | 15 | 27 | 91 | 85 | 82
Costs $
| Electric | 4842.8728 | 5603.052 | 6746.1284 | 6245.8678 | 5495.3514 | 5262.4874 | 5277.1843 | 5393.5824 | 5383.0484 | 5215.0411 | 4308.0226 | 1787.0502
| Nat Gas | 99.78 | 188.07 | 490.77 | 519.5 | 627.29 | 520.43 | 472.85 | 701.26 | 619.02 | 596.7 | 494.27 | 178.32
| Water | 224.2703 | 1549.4691 | 3252.8245 | 3322.24 | 3100.6668 | 2323.5574 | 3070.0326 | 3485.7382 | 2925.7453 | 3420.079 | 1773.4229 | 588.3314
| Chill water | 2690.5656 | 2554.7929 | 2087.9207 | 915.3609 | 589.2054 | 554.9729 | 442.9162 | 460.0509 | 887.3198 | 1159.8199 | 1224.8985 | 2269.6413
| Hot water | 723.0144 | 399.0989 | 428.9759 | 1925.198 | 1778.2184 | 1559.7605 | 378.2253 | 232.8643 | 595.2236 | 1534.994 | 1609.4198 | 1536.4864
| BTU/GSF | 5956.0431 | 6064.1914 | 6132.7281 | 5413.2436 | 4858.2263 | 4413.5439 | 3518.7887 | 3857.71 | 4677.6001 | 5518.5163 | 5023.2527 | 4404.7433 | 59838.5877
45 | NCSU - Wolf Ridge at Centennial Bldg 6 - Lakeview Hall | [17 empty] | NCSU - Wolf Ridge 6
NCSU - Wolf Ridge Building 6
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 36510.9863 | 36674.9878 | 37328.0029 | 35902.9846 | 34626.0376 | 36817.0166 | 35030.9448 | 35036.0107 | 35270.0195 | 31382.019 | 29618.9575 | 30471.0083 |  | 414668.9758 | kwh |  | 1413.8188 | MMbtu
| Chilled Water (Dtherms) |  | 391 | 326 | 246 | 213 | 222 | 175 | 163 | 222 | 230 | 262 | 333 | 388 |  | 3171 | dthrms |  | 3171 | MMbtu
| Steam (1,000 lbs) |  | 104.82 | 96.8701 | 192.7798 | 213.35 | 211.9201 | 322.6202 | 230.6999 | 219.1299 | 195 | 141 | 89 | 58 |  | 2075.19 | 1000 lbs |  | 2075.19 | MMbtu
| Water (CCF) |  | 57 | 81 | 70 | 71 | 58 | 57 | 69 | 74 | 72 | 41 | 22 | 20 |  | 692 | CCF |  | 517616 | gallons
| Electric Cost ($) |  | 3139.9448 | 3154.049 | 3210.2083 | 3087.6567 | 2977.8392 | 3166.2634 | 3012.6613 | 3013.0969 | 3033.2217 | 2698.8536 | 2547.2303 | 2650.9777 |  | 35692.0029 | $
| Chilled Water Cost ($) |  | 5462.27 | 4554.22 | 3436.62 | 2975.61 | 3101.34 | 2444.75 | 2277.11 | 3101.34 | 3213.1 | 3660.14 | 4652.01 | 5024.6 |  | 43903.11 | $
| Steam Cost ($) |  | 1403.5394 | 1297.0912 | 2581.3212 | 2856.7567 | 2837.6105 | 4319.8839 | 3089.0717 | 2934.1496 | 2611.05 | 1887.99 | 1191.71 | 697.16 |  | 27707.3343 | $
| Water Cost ($) |  | 524.4 | 745.2 | 644 | 653.2 | 533.6 | 524.4 | 634.8 | 680.8 | 662.4 | 377.2 | 202.4 | 186.6 |  | 6369 | $
46 | NCSU - Wolf Ridge at Centennial Bldg 1 - Tower Hall | [17 empty] | NCSU - Wolf Ridge 1
NCSU - Wolf Ridge Building 1
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 127816.9556 | 137784.9655 | 139607.8339 | 133268.1427 | 123161.9263 | 138121.1548 | 135089.8437 | 133420.166 | 132151.7944 | 118179.3657 | 125991.9128 | 127717.041 |  | 1572311.1024 | kwh |  | 5360.8136 | MMbtu
| Chilled Water (Dtherms) |  | 938.4351 | 831.1128 | 391.9482 | 294.2559 | 312.6807 | 112.0356 | 147.8418 | 333.7402 | 375.0562 | 561.2676 | 888.5132 | 1188.3989 |  | 6375.2861 | dthrms |  | 6375.2861 | MMbtu
| Steam (1,000 lbs) |  | 152.2565 | 173.6534 | 311.1538 | 351.6681 | 416.4682 | 705.8845 | 594.0203 | 337.192 | 316.9561 | 271.7266 | 182.9589 | 175.4545 |  | 3989.3929 | 1000 lbs |  | 3989.3929 | MMbtu
| Water (CCF) |  | 185 | 310 | 280 | 295 | 205 | 255 | 345 | 300 | 330 | 150 | 90 | 85 |  | 2830 | CCF |  | 2116840 | gallons
| Natural Gas (thms) |  | 980 | 1242 | 1114 | 1123 | 737 | 1103 | 1196 | 1165 | 1261 | 580 | 1580 |  |  | 12081 | thms |  | 12081 | thms
| Electric Cost ($) |  | 10992.2582 | 11849.507 | 12006.2737 | 11461.0603 | 10591.9257 | 11878.4193 | 11617.7266 | 11474.1343 | 11365.0543 | 10163.4254 | 10835.3045 | 11111.3826 |  | 135346.4719 | $
| Chilled Water Cost ($) |  | 13109.9378 | 11610.6457 | 5475.5169 | 4110.7544 | 4368.1489 | 1565.138 | 2065.3499 | 4662.3511 | 5239.5344 | 7840.9081 | 12412.5292 | 15389.7661 |  | 87850.5804 | $
| Steam Cost ($) |  | 2038.7142 | 2325.2186 | 4166.35 | 4708.8352 | 5576.5097 | 9451.7939 | 7953.9317 | 4515.0015 | 4244.0417 | 3638.4187 | 2449.8198 | 2108.9631 |  | 53177.5981 | $
| Water Cost ($) |  | 1702 | 2852 | 2576 | 2714 | 1886 | 2346 | 3174 | 2760 | 3036 | 1380 | 828 | 793.05 |  | 26047.05 | $
| Natural Gas ($) |  | 735.37 | 918.08 | 823.2 | 773.14 | 520.2 | 701.82 | 763.72 | 742.69 | 832.05 | 410.25 | 567.77 |  |  | 7788.29 | $
1 data point that is not yet available to Energy Management: Wolf Ridge 1 Natural Gas for July 2016.
47 | UNCG - Spartan Village 1 - Lee | [17 empty] | UNCG - Spartan Village 1
Spartan Village # 1
| Lee Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
700 Highland Avenue
| Electricity (kWhs) | 87080 | 66054 | 71936 | 55367 | 60814 | 55142 | 84371 | 80199 | 59713 | 60841 | 44681 | 46658
| Water Usage (gallons) | 123420 | 98736 | 168300 | 189244 | 202708 | 132396 | 45628 | 191488 | 178772 | 179520 | 160820 | 5984
| Natural Gas (Therms) | 451 | 285 | 482 | 470 | 586 | 521 | 378 | 708 | 676 | 630 | 499 | 161
| Electricity Cost ($) | 7073.86 | 5781.09 | 6135.4 | 5150.7 | 5485.92 | 5136.86 | 6910.1 | 6645.51 | 5393.3 | 5462.25 | 4474.48 | 4595.32
| Water Costs ($) | 1702.41 | 1530.64 | 2090.5 | 2259.06 | 2367.4 | 1801.54 | 1103.22 | 2277.12 | 2174.78 | 2180.8 | 2030.3 | 784.16
| Natural Gas Cost ($) | 361.68 | 237.22 | 384.92 | 379.77 | 467.28 | 406.12 | 298.86 | 530.01 | 507.13 | 472.19 | 388.46 | 141.5
48 | UNCG - Spartan Village 3 - Haywood | [17 empty] | UNCG - Spartan Village 3
Spartan Village # 3
| Haywood Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
1001 Union Street
| Electricity (kWhs) | 34899 | 35352 | 42931 | 35078 | 40217 | 37592 | 55586 | 4273.14 | 39018 | 36408 | 28469 | 34907
| Water Usage (gallons) | 2992 | 2992 | 79288 | 94996 | 97240 | 68816 | 20944 | 94248 | 92004 | 153340 | 108460 | 16456
| Natural Gas (Therms) | 82 | 74 | 230 | 242 | 323 | 302 | 201 | 406 | 402 | 355 | 280 | 107
| Electricity Cost ($) | 3164.91 | 3189.93 | 3651.01 | 3188.84 | 3505.1 | 3343.56 | 4434.09 | 144 | 3415.07 | 3255.53 | 2770.26 | 3163.79
| Water Costs ($) | 769.15 | 770.08 | 1374.12 | 1500.54 | 1518.6 | 1289.84 | 904.56 | 1494.52 | 1476.46 | 1970.1 | 1608.9 | 868.44
| Natural Gas Cost ($) | 85.02 | 79.02 | 195.98 | 402.92 | 268.12 | 245.3 | 169.94 | 313.98 | 311.11 | 276.6 | 228.31 | 101.93
49 | UNCG - Spartan Village 4 - Union | [17 empty] | UNCG - Spartan Village 4
Spartan Village # 4
| Union Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
917 Union Street
| Electricity (kWhs) | 47471 | 47413 | 58833 | 49656 | 54502 | 48126 | 70496 | 64777 | 46794 | 49320 | 35860 | 39368
| Water Usage (gallons) | 6732 | 17204 | 153340 | 169048 | 183260 | 117436 | 39644 | 169048 | 166056 | 171292 | 148104 | 4488
| Natural Gas (Therms) | 143 | 120 | 397 | 400 | 486 | 435 | 311 | 602 | 575 | 531 | 396 | 140
| Electricity Cost ($) | 4231.56 | 4224.36 | 4918.76 | 4382.7 | 4680.93 | 4288.54 | 5643.88 | 5289.3 | 4187.09 | 4341.49 | 3518.75 | 3733.18
| Water Costs ($) | 798.01 | 874.46 | 1970.1 | 2096.52 | 2210.9 | 1681.14 | 1055.06 | 2096.52 | 2072.44 | 2114.58 | 1927.96 | 772.12
| Natural Gas Cost ($) | 130.75 | 113.51 | 321.19 | 326.65 | 391.56 | 342.97 | 250.06 | 454.18 | 434.87 | 397.41 | 313.14 | 126.11
50 | WSSU - Martin-Schexnider Residence Hall | [17 empty] | WSSU - Martin-Schexnider Residence Hall
Winston-Salem State University, Martin Schexnider Residence Hall
| Utility |  | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
| Electricity (KWH) building meter |  | 36421 | 49419.8 | 52487 | 51882 | 46191 | 36899 | 49331 | 46857 | 50816 | 52531 | 28283 | 29786
| Steam from Central Plant (lbs) - natural gas therms |  | 2198.592 | 2148.672 | 2502.336 | 3130.368 | 3577.968 | 4276.368 | 5428.464 | 4584.048 | 4105.536 | 3380.832 | 1681.776 | 2077.872
| Chilled Water from Central Plant (Dtherms) kwh |  | 72135.6381 | 83933.6689 | 63812.1406 | 36902.6331 | 24943.904 | 34815.6304 | 32632.7794 | 51648.3558 | 44122.9024 | 80607.5124 | 67323.6384 | 83869.4674
| Natural Gas (Therms) other than from central steam plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) |  | 206.02 | 407.3 | 545.46 | 451.07 | 436.15 | 208.76 | 509.03 | 557.9 | 322.89 | 761.14 | 852.68 | 329.01
| Electricity Cost ($) building meter x blended rate ($.0712/kwh) |  | 2593.1752 | 3518.6898 | 3737.0744 | 3693.9984 | 3288.7992 | 2627.2088 | 3512.3672 | 3336.2184 | 3618.0992 | 3740.2072 | 2013.7496 | 2120.7632
| Steam from Central Plant Cost ($) for Natural Gas |  | 881.5978 | 885.0581 | 961.9934 | 1166.1149 | 1070.6314 | 1816.2763 | 2313.5237 | 1876.595 | 1489.0157 | 1330.5984 | 701.9856 | 853.224
| Chilled Water from Central Plant Cost ($) kwh x $.0712/kwh |  | 5136.0574 | 5976.0772 | 4543.4244 | 2627.4675 | 1776.006 | 2478.8729 | 2323.4539 | 3677.3629 | 3141.5507 | 5739.2549 | 4793.4431 | 5971.5061
| Natural Gas Cost ($) other than from central steam. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Costs ($) |  | 1369.51 | 2332.22 | 2982.47 | 2649.65 | 2588.01 | 1451.58 | 2929.57 | 3192.57 | 1992.36 | 4220.11 | 4672.55 | 2035.08
51 | Cape Fear Community College - Union Station | [17 empty] | Cape Fear Community College - Union Station
Cape Fear CC- Union Station
| Utility | Jun-15 | 2015-07-01: 2015-07-01; 2015-08-01: 2015-08-01; 2015-09-01: 2015-09-01; 2015-10-01: 2015-10-01; 2015-11-01: 2015-11-01; 2015-12-01: 2015-12-01; 2016-01-01: 2016-01-01
| Electricity (KWhs) | 402725 | 2015-07-01: 382700; 2015-08-01: 391650; 2015-09-01: 307450; 2015-10-01: 295100; 2015-11-01: 297825; 2015-12-01: 303025; 2016-01-01: 227825
| Steam (lbs) | NA | bar: 2015-07-01 to 2016-01-01
| Chilled Water (Dtherms) | NA | bar: 2015-07-01 to 2016-01-01
| Natural Gas (Therms) | 10246 | 2015-07-01: 10824; 2015-08-01: 9645; 2015-09-01: 10015; 2015-10-01: 12258; 2015-11-01: 12572; 2015-12-01: 13897; 2016-01-01: 18428
| Water (CCF) | 593 | 2015-07-01: 593; 2015-08-01: 805; 2015-09-01: 559; 2015-10-01: 559; 2015-11-01: 345; 2015-12-01: 345; 2016-01-01: 284
| Electricity Cost ($) | 30185.84 | 2015-07-01: 29058.39; 2015-08-01: 29743.3; 2015-09-01: 22657.74; 2015-10-01: 21425.02; 2015-11-01: 20909.88; 2015-12-01: 19677.22; 2016-01-01: 16754.24
| Steam Costs ($) | NA | bar: 2015-07-01 to 2016-01-01
| Chilled Water Costs ($) | NA | bar: 2015-07-01 to 2016-01-01
| Natural Gas Costs ($) | 7600.68 | 2015-07-01: 8138.83; 2015-08-01: 7254.87; 2015-09-01: 7532.28; 2015-10-01: 9213.96; 2015-11-01: 9240.74; 2015-12-01: 10257.22; 2016-01-01: 13219.12
| WATER COSTS | 4536.15 | 2015-07-01: 4536.15; 2015-08-01: 5790.61; 2015-09-01: 4288; 2015-10-01: 4288; 2015-11-01: 2967.09; 2015-12-01: 2967.09; 2016-01-01: 2592.62
| Utility | 2016-02-01 | 2015-07-01: 2016-03-01; 2015-08-01: 2016-04-01; 2015-09-01: 2016-05-01
| Electricity (KWhs) | 301550 | 2015-07-01: 301125; 2015-08-01: 337450; 2015-09-01: 358325
| Steam (lbs) | NA | bar: 2015-07-01 to 2015-09-01
| Chilled Water (Dtherms) | NA | bar: 2015-07-01 to 2015-09-01
| Natural Gas (Therms) | 15704 | 2015-07-01: 15110; 2015-08-01: 12862; 2015-09-01: 10686
| Water (CCF) | 284 | 2015-07-01: 305; 2015-08-01: 305; 2015-09-01: 510
| Electricity Cost ($) | 20472.96 | 2015-07-01: 20183.69; 2015-08-01: 23005.53; 2015-09-01: 25594.84
| Steam Costs ($) | NA | bar: 2015-07-01 to 2015-09-01
| Chilled Water Costs ($) | NA | bar: 2015-07-01 to 2015-09-01
| Natural Gas Costs ($) | 10073.26 | 2015-07-01: 10365.37; 2015-08-01: 9408.26; 2015-09-01: 7016.14
| WATER COSTS | 2592.62 | 2015-07-01: 2720.19; 2015-08-01: 2720.19; 2015-09-01: 3983.49
52 | ECU - Smith-Williams Center | [17 empty] | ECU - Smith-Williams Center
ECU - Smith-Williams Center
| Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14
| Electricity (KWhs) | 37952 | 45087 | 43438 | 32746 | 46886 | 38945 | 44107 | 33601 | 34815 | 43808 | 40223 | 31585 | 36781 | 38470
Steam (lbs)
| Chilled Water (Tons) |  | 27120 | 24886.1458 | 20179.375 | 11632.2917 | 10289.9864 | 10582.6866 | 3631.086 | 4267.5363 | 8632.7583 | 13117.6303 | 17418.6778 | 24730 | 29075
Natural Gas (Therms)
| Water (CCF) | Water meter inop - is being replaced
| Electricity Cost ($) | 3330.288 | 3956.3842 | 3811.6845 | 2873.4615 | 4114.2465 | 3417.4237 | 3870.3892 | 2948.4877 | 3055.0162 | 3844.152 | 3529.5682 | 2771.5837 | 3227.5327 | 3375.7425 | 0 | 0
Steam Costs ($)
Chilled Water Costs ($)
Natural Gas Costs ($)
53 | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall | [17 empty] | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall
NCSU - Wolf Ridge Building 2
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 48640.9912 | 49838.0127 | 49971.9849 | 47547.9736 | 44005.0049 | 47034.0576 | 44637.9395 | 45383.0566 | 45377.9297 | 39505.9814 | 35999.0234 | 27633.0566 |  | 525575.0122 | kwh |  | 1791.9543 | MMbtu
| Chilled Water (Dtherms) |  | 461.8455 | 376.8711 | 158.752 | 108.4395 | 55.0464 | 37.667 | 56.2261 | 130.2666 | 221.105 | 297.3047 | 443.3623 | 579.4775 |  | 2926.3635 | dthrms |  | 2926.3635 | MMbtu
| Steam (1,000 lbs) |  | 40.4099 | 39.6398 | 98.6099 | 125.6003 | 114.2597 | 267.6306 | 216.4797 | 108.9101 | 106 | 113.58 | 59.3603 | 101.4298 |  | 1391.91 | 1000 lbs |  | 1391.91 | MMbtu
| Water (CCF) |  | 271 | 215 | 137 | 132 | 107 | 103 | 120 | 105 | 106 | 65 | 32 | 33 |  | 1426 | CCF |  | 1066648 | gallons
| Electric Cost ($) |  | 4183.1252 | 4286.0691 | 4297.5907 | 4089.1257 | 3784.4304 | 4044.929 | 3838.8628 | 3902.9429 | 3902.502 | 3397.5144 | 3095.916 | 2404.0759 |  | 45227.0841 | $
| Chilled Water Cost ($) |  | 6451.9811 | 5264.8892 | 2217.7648 | 1514.8992 | 768.998 | 526.2079 | 785.4783 | 1819.8244 | 3088.8366 | 4153.3465 | 6193.7714 | 7504.2341 |  | 40290.2314 | $
| Steam Cost ($) |  | 541.088 | 530.777 | 1320.3868 | 1681.7874 | 1529.9375 | 3583.5736 | 2898.6638 | 1458.306 | 1419.34 | 1520.8366 | 794.8338 | 1219.1857 |  | 18498.7163 | $
| Water Cost ($) |  | 2493.2 | 1978 | 1260.4 | 1214.4 | 984.4 | 947.6 | 1104 | 966 | 975.2 | 598 | 294.4 | 307.89 |  | 13123.49 | $
54 | UNCG - Spartan Village Building 2 - Highland | [17 empty] | UNCG - Spartan Village Building 2
Spartan Village # 2
| Highland Residence Hall | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
701 Highland Avenue
| Electricity (kWhs) | 54581 | 60418 | 77125 | 63722 | 69467 | 62518 | 86863 | 85967 | 67171 | 71204 | 59045 | 75766
| Water Usage (gallons) | 5236 | 35904 | 142120 | 203456 | 216920 | 143616 | 64328 | 211684 | 215424 | 227392 | 164560 | 125664
| Natural Gas (Therms) | 84 | 80 | 376 | 395 | 525 | 490 | 331 | 682 | 656 | 590 | 450 | 374
| Electricity Cost ($) | 5102.08 | 5449.56 | 6450.17 | 5675.06 | 6023.35 | 5602.06 | 7083.82 | 7031.59 | 5890.34 | 6135.21 | 5396.94 | 6412.21
| Water Costs ($) | 786.59 | 1024.96 | 1879.8 | 2373.44 | 2481.8 | 1891.84 | 1253.72 | 2439.66 | 2469.76 | 2566.08 | 2060.4 | 1747.36
| Natural Gas Cost ($) | 86.52 | 83.52 | 305.44 | 322.74 | 421.09 | 383.35 | 264.62 | 511.42 | 492.82 | 443.88 | 352.63 | 297.55
55 | UNCC - PORTAL | [17 empty] | UNCC - PORTAL
| PORTAL |  | 2015-08-01: 08-07560-03A
| 117992 | Jul '15 | Aug '15 | Sep '15 | Oct '15 | Nov '15 | Dec '15 | Jan '16 | Feb '16 | Mar '16 | Apr '16 | May '16 | Jun '16
Consumption
| Electric (KWH) | 76766 | 80807 | 72885.4 | 70898.8 | 71999.6 | 73852.2 | 75118 | 68766 | 77821 | 78207.2 | 85712.8 | 87298.8
| Nat Gas (Therms) | 37 | 35 | 119 | 137 | 213 | 196 | 188 | 206 | 197 | 156 | 119 | 100
| Water (CF) | 150 | 2400 | 4050 | 2530 | 2470 | 1570 | 2750 | 2900 | 3090 | 3060 | 2700 | 1950
| Chill water mmBTU (BTUX10^6) | 424 | 343 | 174 | 122 | 163 | 239 | 137 | 148 | 174 | 273.7 | 337.2 | 411.8
| Hot water mmBTU | 135 | 115 | 77 | 147 | 242 | 208 | 314 | 276 | 177 | 156.6 | 152.4 | 113
Costs $
| Electric | 5124.9359 | 5397.2013 | 4871.2021 | 4332.4971 | 4050.9783 | 4158.5571 | 4253.2513 | 4015.1459 | 4580.6503 | 4487.8769 | 5019.407 | 5638.1402
| Nat Gas | 47.93 | 46.52 | 105.38 | 118 | 170.19 | 156.75 | 148.7 | 159.72 | 153.71 | 126.73 | 103.33 | 90.56
| Water | 11.18 | 181.3747 | 310.048 | 207.3122 | 203.8772 | 134.5623 | 254.8475 | 240.4129 | 253.8483 | 247.2346 | 213.1897 | 128.0552
| Chill water | 2185.7344 | 1780.3731 | 921.0754 | 608.1086 | 852.1228 | 1045.3705 | 815.6555 | 879.3976 | 848.4411 | 885.7708 | 1373.5244 | 1819.8868
| Hot water | 605.3796 | 670.1277 | 425.2297 | 603.7328 | 814.7807 | 943.1769 | 1373.5986 | 1041.2888 | 717.1333 | 732.643 | 773.0877 | 1010.6758
| BTU/GSF | 6988.8263 | 6247.9955 | 4335.7599 | 4446.121 | 5694.9847 | 6090.1053 | 6153.8292 | 5756.5733 | 5392.105 | 6040.6042 | 6728.8636 | 7056.9488 | 70932.7167
Includes Cooking Loads
56 | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall | [17 empty] | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall
NCSU - Wolf Ridge Building 3
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 42022.0337 | 41414.0015 | 40640.9912 | 39221.9849 | 38379.0283 | 41500 | 39580.9937 | 40283.9966 | 39995.9717 | 37370.9717 | 36082.0312 | 37901.9775 |  | 474393.9819 | kwh |  | 1617.452 | MMbtu
| Chilled Water (Dtherms) |  | 376.0398 | 279.2551 | 93.2671 | 59.8391 | 70.082 | 27.1128 | 33.918 | 86.2432 | 97.4399 | 153.2837 | 310.918 | 437.7861 |  | 2025.1848 | dthrms |  | 2025.1848 | MMbtu
| Steam (1,000 lbs) |  | 51.5101 | 43.5099 | 106.0499 | 143.3102 | 148.63 | 312.6702 | 246.9596 | 128.5202 | 94.5902 | 45.8998 | 25.0396 | 28.8003 |  | 1375.49 | 1000 lbs |  | 1375.49 | MMbtu
| Water (CCF) |  | 56 | 78 | 65 | 63 | 56 | 63 | 75 | 72 | 72 | 44 | 22 | 21 |  | 687 | CCF |  | 513876 | gallons
| Electric Cost ($) |  | 3613.8949 | 3561.6041 | 3495.1252 | 3373.0907 | 3300.5964 | 3569 | 3403.9655 | 3464.4237 | 3439.6536 | 3213.9036 | 3103.0547 | 3297.472 |  | 40835.7844 | $
| Chilled Water Cost ($) |  | 5253.2759 | 3901.1941 | 1302.9412 | 835.9524 | 979.046 | 378.7657 | 473.834 | 1204.817 | 1361.236 | 2141.3732 | 4343.524 | 5669.3304 |  | 27845.29 | $
| Steam Cost ($) |  | 689.7208 | 582.5974 | 1420.0084 | 1918.9237 | 1990.1559 | 4186.6541 | 3306.7893 | 1720.8854 | 1266.5629 | 614.598 | 335.2805 | 346.1791 |  | 18378.3554 | $
| Water Cost ($) |  | 515.2 | 717.6 | 598 | 579.6 | 515.2 | 579.6 | 690 | 662.4 | 662.4 | 404.8 | 202.4 | 195.93 |  | 6323.13 | $
57 | WSSU - Hill Hall Renovation | [17 empty] | WSSU - Hill Hall Renovation
Winston-Salem State University, Hill Hall - Student Success Center
| Utility |  | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
| Electricity (KWhs) building meter |  | 36485 | 43096 | 39521 | 42293 | 35250 | 29593 | 39198 | 37209 | 48237 | 48818 | 41529 | 40109
| Steam from Central Plant (lbs) - natural gas therms |  | 1511.532 | 1477.212 | 1720.356 | 2152.128 | 2459.853 | 2940.003 | 3732.069 | 3151.533 | 2822.556 | 2324.322 | 1156.221 | 1428.537
| Chilled Water from Central Plant (Dtherms) kwh |  | 49165.6932 | 57206.9108 | 43492.6232 | 25151.8332 | 17001.088 | 23729.3888 | 22241.6168 | 35202.1176 | 30072.9728 | 54939.8928 | 45885.9648 | 57163.1528
| Natural Gas (Therms) other than from central steam plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) |  | 11.4 | 25.6 | 47.4 | 46.1 | 43.1 | 11.4 | 25.1 | 34.8 | 21.3 | 30.7 | 11.7 | 10.4
| Electricity Cost ($) building meter x blended rate ($.0712/kwh) |  | 2597.732 | 3068.4352 | 2813.8952 | 3011.2616 | 2509.8 | 2107.0216 | 2790.8976 | 2649.2808 | 3434.4744 | 3475.8416 | 2956.8648 | 2855.7608
| Steam from Central Plant Cost ($) for Natural Gas |  | 606.0985 | 608.4774 | 661.3705 | 801.704 | 736.0591 | 1248.69 | 1590.5475 | 1290.1591 | 1023.6983 | 914.7864 | 482.6151 | 586.5915
| Chilled Water from Central Plant Cost ($) kwh x $.0712/kwh |  | 3500.5974 | 4073.132 | 3096.6748 | 1790.8105 | 1210.4775 | 1689.5325 | 1583.6031 | 2506.3908 | 2141.1957 | 3911.7204 | 3267.0807 | 4070.0165
| Natural Gas Cost ($) other than from central steam. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Costs ($) |  | 88.71 | 179.01 | 312.44 | 313.51 | 297.84 | 99.2 | 178.32 | 243.45 | 154.27 | 218.46 | 96.38 | 87.67
58 | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall | [17 empty] | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall
NCSU - Wolf Ridge Building 5
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 34236.9995 | 36642.9901 | 37118.0115 | 35600.0061 | 33330.9937 | 37289.978 | 32999.0234 | 28028.9917 | 33976.0132 | 31752.9907 | 27868.988 | 29325.0122 |  | 398169.9982 | kwh |  | 1357.5654 | MMbtu
| Chilled Water (Dtherms) |  | 310.4771 | 265.093 | 103.02 | 72.3928 | 78.9221 | 29.3279 | 36.011 | 76.1572 | 103.1228 | 142.4321 | 254.7549 | 366.614 |  | 1838.325 | dthrms |  | 1838.325 | MMbtu
| Steam (1,000 lbs) |  | 55.98 | 61.2099 | 112.1101 | 134.2598 | 141.1103 | 245.6398 | 180.0201 | 80.5498 | 82 | 63 | 40 | 40.6899 |  | 1236.5697 | 1000 lbs |  | 1236.5697 | MMbtu
| Water (CCF) |  | 49 | 83 | 70 | 70 | 53 | 60 | 75 | 66 | 68 | 36 | 11 | 12 |  | 653 | CCF |  | 488444 | gallons
| Electric Cost ($) |  | 2944.382 | 3151.2971 | 3192.149 | 3061.6005 | 2866.4655 | 3206.9381 | 2837.916 | 2410.4933 | 2921.9371 | 2730.7572 | 2396.733 | 2551.2761 |  | 34271.9449 | $
| Chilled Water Cost ($) |  | 4337.3644 | 3703.3495 | 1439.1897 | 1011.3277 | 1102.542 | 409.7105 | 503.0735 | 1063.9165 | 1440.6256 | 1989.7768 | 3558.9257 | 4747.6515 |  | 25307.4533 | $
| Steam Cost ($) |  | 749.5726 | 819.6 | 1501.154 | 1797.7393 | 1889.4665 | 3289.117 | 2410.4691 | 1078.5613 | 1097.98 | 843.57 | 535.6 | 489.0928 |  | 16501.9226 | $
| Water Cost ($) |  | 450.8 | 763.6 | 644 | 644 | 487.6 | 552 | 690 | 607.2 | 625.6 | 331.2 | 101.2 | 111.96 |  | 6009.16 | $
59 | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall | [17 empty] | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall
NCSU - Wolf Ridge Building 4
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 36541.9922 | 32219.9707 | 32330.0171 | 28742.981 | 30244.9951 | 32134.0519 | 30700.9983 | 35416.0042 | 36603.9963 | 32574.9969 | 32916.0004 | 37680.0079 |  | 398106.012 | kwh |  | 1357.3472 | MMbtu
| Chilled Water (Dtherms) |  | 325.4529 | 237.6841 | 66.032 | 37.0249 | 42.3601 | 13.325 | 16.8 | 68.5488 | 65.865 | 129.9961 | 277.842 | 417.5339 |  | 1698.4648 | dthrms |  | 1698.4648 | MMbtu
| Steam (1,000 lbs) |  | 55.778 | 52.872 | 122.9539 | 152.874 | 160.0262 | 297.2637 | 203.8082 | 85.2779 | 149.7198 | 280.0901 | 249.3102 | 212.0899 |  | 2022.0639 | 1000 lbs |  | 2022.0639 | MMbtu
| Water (CCF) |  | 35 | 12 | 12 | 11 | 9 | 4 | 18 | 20 | 18 | 11 | 22 | 34 |  | 206 | CCF |  | 154088 | gallons
| Electric Cost ($) |  | 3142.6113 | 2770.9175 | 2780.3815 | 2471.8964 | 2601.0696 | 2763.5285 | 2640.2859 | 3045.7764 | 3147.9437 | 2801.4497 | 2830.776 | 3278.1607 |  | 34274.797 | $
| Chilled Water Cost ($) |  | 4546.5767 | 3320.4466 | 922.4668 | 517.2379 | 591.7707 | 186.1496 | 234.6967 | 957.6271 | 920.1339 | 1816.0454 | 3881.4533 | 5407.0645 |  | 23301.6693 | $
| Steam Cost ($) |  | 746.867 | 707.9563 | 1646.3528 | 2046.9833 | 2142.751 | 3980.3612 | 2728.9919 | 1141.8707 | 2004.7482 | 3750.4066 | 3338.2637 | 2549.3201 |  | 26784.8728 | $
| Water Cost ($) |  | 322 | 110.4 | 110.4 | 101.2 | 82.8 | 36.8 | 165.6 | 184 | 165.6 | 101.2 | 202.4 | 317.22 |  | 1899.62 | $
60 | Guilford Technical Community College - Aviation Center III Building | [17 empty] | Guilford Technical Community College - Aviation Center III Building
|  |  | Electric | Elec | Nat Gas | Nat Gas | Water | Water
|  |  | KWH | Cost | Therms | Cost | Gallons | Cost
| 2015-07-01 |  | 2015-08-01: 44997; 2015-09-01: 3935.36; 2015-10-01: 117; 2015-11-01: 110.51; 2015-12-01: 2244; 2016-01-01: 252.06
| 2015-08-01 |  | 2015-08-01: 41362; 2015-09-01: 3578.18; 2015-10-01: 148; 2015-11-01: 134.5; 2015-12-01: 7480; 2016-01-01: 294.2
| 2015-09-01 |  | 2015-08-01: 31658; 2015-09-01: 2741.16; 2015-10-01: 346; 2015-11-01: 282.95; 2015-12-01: 6732; 2016-01-01: 288.18
| 2015-10-01 |  | 2015-08-01: 33749; 2015-09-01: 2819.97; 2015-10-01: 663; 2015-11-01: 534.5; 2015-12-01: 20944; 2016-01-01: 402.56
| 2015-11-01 |  | 2015-08-01: 24073; 2015-09-01: 2196.4; 2015-10-01: 978; 2015-11-01: 740.98; 2015-12-01: 4488; 2016-01-01: 270.12
| 2015-12-01 |  | 2015-08-01: 24187; 2015-09-01: 2245.97; 2015-10-01: 782; 2015-11-01: 596.41; 2015-12-01: 1496; 2016-01-01: 246.04
| 2016-01-01 |  | 2015-08-01: 26355; 2015-09-01: 2422.46; 2015-10-01: 1915; 2015-11-01: 1393.45; 2015-12-01: 2992; 2016-01-01: 258.08
| 2016-02-01 |  | 2015-08-01: 25999; 2015-09-01: 2353.69; 2015-10-01: 1732; 2015-11-01: 1262.55; 2015-12-01: 3740; 2016-01-01: 264.1
| 2016-03-01 |  | 2015-08-01: 28659; 2015-09-01: 2509.35; 2015-10-01: 455; 2015-11-01: 338.18; 2015-12-01: 3740; 2016-01-01: 264.1
| 2016-04-01 |  | 2015-08-01: 31857; 2015-09-01: 2734.19; 2015-10-01: 305; 2015-11-01: 246.59; 2015-12-01: 4488; 2016-01-01: 270.12
| 2016-05-01 |  | 2015-08-01: 33705; 2015-09-01: 3138.44; 2015-10-01: 232; 2015-11-01: 193.27; 2015-12-01: 2244; 2016-01-01: 252.06
| 2016-06-01 |  | 2015-08-01: 36789; 2015-09-01: 3332.3; 2015-10-01: 133; 2015-11-01: 121.22; 2015-12-01: 2992; 2016-01-01: 268.35
|  | Totals | 2015-08-01: 383390; 2015-09-01: 34007.47; 2015-10-01: 7806; 2015-11-01: 5955.11; 2015-12-01: 63580; 2016-01-01: 3329.97
Note: GTCC did not take benificial occupancy of this building until August 2014
61 | UNCC - Martin Residence Hall | [17 empty] | UNCC - Martin Residence Hall
| Martin Residence Hall |  | 2015-08-01: 11-09156-02A
| 220048 | Jul '15 | Aug '15 | Sep '15 | Oct '15 | Nov '15 | Dec '15 | Jan '16 | Feb '16 | Mar '16 | Apr '16 | May '16 | Jun '16
Consumption
| Electric (KWH) | 186825 | 183184 | 161861 | 129523 | 130154 | 131739 | 106152 | 121893 | 138818 | 148064 | 134975 | 163897
| Nat Gas (Therms) | 1390 | 968 | 1881 | 2020 | 2621 | 3487 | 3868 | 4816 | 3136 | 2768 | 2998 | 1892
| Water (CF) | 26755 | 65503 | 67495 | 65577 | 65709 | 40024 | 50489 | 59711 | 55065 | 68618 | 60481 | 43399
Costs $
| Electric | 12472.5288 | 12235.0901 | 10817.772 | 7914.9157 | 7322.9717 | 7418.1156 | 6010.4254 | 7117.1536 | 8171.017 | 8496.5707 | 7904.2391 | 10585.1886
| Nat Gas | 995.97 | 700.28 | 1340.02 | 1437.41 | 1845.53 | 2419.27 | 2628.74 | 3241.78 | 2118.6 | 1878.35 | 2071.01 | 1319.17
| Water | 1994.1346 | 4950.245 | 5167.0838 | 5373.4839 | 5423.7112 | 3430.3969 | 4678.9083 | 4950.1014 | 4523.6751 | 5544.0345 | 4775.5293 | 2849.9828
| BTU/GSF | 3528.5342 | 3280.3016 | 3364.5829 | 2926.3273 | 3209.2337 | 3627.3607 | 3403.7602 | 4078.6506 | 3577.615 | 3553.7445 | 3455.3129 | 3401.1514 | 41406.575
62 | UNCSA - New Library Building | [17 empty] | UNCSA - New Library Building
63 | NCA&T - Student Health Center | [17 empty] | NCA&T - Student Health Center
Agency - New Student Health Center
| Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14
| Electricity (KWhs) | 32348 | 32571 | 33777 | 26945 | 20269 | 19441 | 17141 | 17406 | 20710 | 19561 | 20052 | 23035 | 29474 | 38354
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) | 1048 | 156 | 324 | 490 | 608 | 962 | 777 | 873 | 1467 | 631 | 491 | 512 | 764 | 804
| Water (CCF) | 11 | 13 | 12 | 12 | 14 | 12 | 10 | 9 | 14 | 11 | 14 | 12 | 13
| Electricity Cost ($) | 2264.36 | 2279.97 | 2364.39 | 1886.15 | 1418.83 | 1360.87 | 1199.87 | 1218.42 | 1449.7 | 1369.27 | 1403.64 | 1612.45 | 2063.18 | 2684.78
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 746.61 | 140.5 | 266.46 | 390.91 | 479.39 | 699.74 | 555.61 | 614.81 | 1002.78 | 443.86 | 345.71 | 371.93 | 545.32 | 573.86
64 | UNCG - Campus Police Facility | [17 empty] | UNCG - Campus Police Facility
| Campus Police Facility | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
1200 West Gate City Blvd
| Electricity (kWhs) | 58911 | 50302 | 45092 | 37399 | 37572 | 32861 | 36614 | 34312 | 37139 | 40184 | 35306 | 46821
| Water Usage (gallons) | 4488 | 20196 | 5984 | 12716 | 11220 | 8976 | 5984 | 6732 | 8228 | 748 | 14960 | 6732
| Natural Gas (Therms) | 334 | 312 | 374 | 690 | 947 | 1113 | 1514 | 1745 | 1265 | 1100 | 714 | 598
| Electricity Cost ($) | 4466.906 | 3967.1217 | 3549.9744 | 3074.1882 | 3082.2608 | 2768.1073 | 3046.6539 | 2911.5943 | 3101.1835 | 3310.5722 | 2988.95 | 3742.7906
| Water Costs ($) | 269.7 | 365 | 313.63 | 328.99 | 327.75 | 309.69 | 285.61 | 291.63 | 303.67 | 243.47 | 353.8 | 310.31
| Natural Gas Cost ($) | 273.95 | 257.46 | 303.94 | 847.84 | 740.63 | 840.83 | 1125.27 | 1271.84 | 928.47 | 807.32 | 545.69 | 461.65
65 | UNCC - South Village Dining Facility | [17 empty] | UNCC - South Village Dining Facility
| South Village Dinning |  | 2015-08-01: 10-08633-03A
| 57844 | Jul '15 | Aug '15 | Sep '15 | Oct '15 | Nov '15 | Dec '15 | Jan '16 | Feb '16 | Mar '16 | Apr '16 | May '16 | Jun '16
Consumption
| Electric (KWH) | 125849 | 187598 | 177291 | 187480 | 178291 | 169137 | 164254 | 171012 | 169281.8 | 183634.8 | 141157.6 | 124718.7
| Nat Gas (Therms) | 616 | 1307 | 3678 | 4293 | 5631 | 5544 | 6329 | 7429 | 5019 | 4479 | 3493 | 287
| Water (CF) | 7522 | 52053 | 70851 | 65585 | 58110 | 40236 | 48273 | 63411 | 50103 | 65019 | 29891 | 9697
| Chill water mmBTU (BTUX10^6) | 505 | 698 | 535 | 279 | 216 | 236 | 37 | 95 | 280 | 363 | 414 | 505
| Hot water mmBTU | 78 | 42 | 46 | 75 | 92 | 52 | 178 | 154 | 97 | 76 | 71 | 48
Costs $
| Electric | 8401.741 | 12529.9067 | 11849.0163 | 11456.5629 | 10031.3471 | 9523.9665 | 9300.2149 | 9985.14 | 9964.1578 | 10537.7813 | 8266.2969 | 8054.8818
| Nat Gas | 453.63 | 937.81 | 2599.17 | 3030.11 | 3939.7 | 3833.44 | 4287.26 | 4988.73 | 3377.5 | 3029.09 | 2409.33 | 218.77
| Water | 560.6384 | 3933.7908 | 5424.0026 | 5374.1395 | 4796.4793 | 3448.5671 | 4473.5475 | 5256.835 | 4116.0391 | 5253.251 | 2360.1684 | 636.7954
| Chill water | 2778.6005 | 3778.0623 | 2609.9008 | 1210.3588 | 935.7969 | 1091.4467 | 309.2056 | 553.2258 | 1300.7829 | 1725.4697 | 1950.4153 | 2984.8147
| Hot water | 1375.4908 | 798.1978 | 1160.7583 | 1678.9517 | 1880.4148 | 1111.0622 | 2404.4323 | 2390.7405 | 2138.3959 | 1281.973 | 1344.3389 | 899.4067
| BTU/GSF | 18567.1252 | 26118.2556 | 26860.4677 | 24600.3347 | 25576.1858 | 24540.0637 | 24347.1172 | 27235.2006 | 25179.6124 | 26164.5449 | 22749.6323 | 17413.0455 | 289351.5856
Includes Cooking Loads
66 | UNCG - Dining Hall Renovation | [17 empty] | UNCG - Dining Hall Renovation
| Dining Hall/ Moran Common | July-15 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01
1209 North Drive
| Electricity (kWhs) | 237396 | 296404 | 292447 | 298357 | 271644 | 220151 | 256814 | 261897 | 277239 | 283360 | 213393 | 272438
| Lighting submeter (kWhs) | 18874 | 22762 | 21655 | 23364 | 20761 | 18990 | 21075 | 21033 | 22224 | 23239 | 16536 | 20448
| Mechanical submeter (kWhs) | 50338 | 66741 | 56423 | 56965 | 54886 | 45534 | 53343 | 53336 | 54115 | 43778 | 44685 | 59490
| Chilled water (ton-hrs) | Note 2 | Note 2 | 275675.4729 | 188795.4115 | 170295.5094 | 127155.0646 | 122574.7365 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2
| Steam Usage (lbs) | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1
| Water Usage (gallons) | 312903.36 | 519515.92 | 662997.28 | 636368.48 | 546099.84 | 196724 | 552203.52 | 589468.88 | 490186.84 | 596380.4 | 108998.56 | 175450.88
| Natural Gas (Therms) | 1818 | 1950 | 4943 | 4312 | 5211 | 3111 | 1468 | 4609 | 3236 | 4627 | 3701 | 949
| Electricity Cost ($) | 16623.5259 | 21067.1684 | 20124.5868 | 18997.4332 | 17296.5231 | 12952.7384 | 15235.5716 | 15466.9711 | 16570.612 | 16453.4744 | 12697.8832 | 17775.5457
| Water Costs ($) | 2475.8688 | 4110.7044 | 5335.8872 | 5121.5752 | 4395.0816 | 1583.26 | 4444.2048 | 4744.1212 | 3945.0866 | 4799.746 | 877.2344 | 1412.0512
| Natural Gas Cost ($) | 1386.58 | 1485.56 | 3729.55 | 3256.46 | 3951.72 | 2309.6 | 1090.16 | 3320.63 | 2338.44 | 3287.62 | 2730.09 | 719.08
Note 1: Inaccurate Steam Meter
Note 2: Missing Data
Note 3: Chilled water costs are based on a per square foot allocation, not on metered consumption.
67 | WSSU - Center for Design Innovation | [17 empty] | WSSU - Center for Design Innovation
Winston-Salem State University, Center for Design Innovation
| Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14
| Electricity (KWH) building utility meter |  | 47920 | 46518 | 44399 | 41897 | 44113 | 39258 | 48881 | 54626 | 34601 | 29667 | 26960 | 31878
Steam from Central Plant (lbs) - natural gas therms
Chilled Water from Central Plant (Dtherms) kwh
Natural Gas (Therms) other than from central steam plant
| Emergency Generator #2 Fuel Oil Use (Gallons-Estimated) |  | 33.75 | 33.75 | 33.75 | 33.75 | 33.75 | 33.75 | 33.75 | 33.75 | 33.75 | 33.75 | 33.75 | 33.75
| Water (CCF) |  | 0.36 | 0.6 | 1.1 | 0.8 | 0.9 | 1.05 | 0.76 | 0.5 | 0.8 | 0.68 | 2.12 | 1.9
| Electricity Cost ($) utility building meter invoice |  | 3837.92 | 3704.59 | 3562.8 | 3704.31 | 3394.29 | 4060.68 | 4435.71 | 3134.97 | 2814.49 | 2638.65 | 2962.44 | 2590.435
Steam from Central Plant Cost ($) for Natural Gas
Chilled Water from Central Plant Cost ($) kwh x $.071/wh
Natural Gas Cost ($) other than from central steam.
| Emergency Generator #2 Fuel Oil Cost (Estimated) |  | 54.6277 | 54.6277 | 54.6277 | 54.6277 | 54.6277 | 54.6277 | 54.6277 | 54.6277 | 54.6277 | 54.6277 | 54.6277 | 54.6277
| Water Costs ($) |  | 24.716 | 28.9 | 31.45 | 31.82 | 35.63 | 38.27 | 29.27 | 31.74 | 28.53 | 34.52 | 37.99 | 37.34
Building is all electric and at an off-campus location. No central plant is available and no natural gas is delivered to the building or site.
68 | FSU - Jones Student Center - Renovation and Addition | [17 empty] | FSU - Jones Student Center - Renovation and Addition
69 | UNCSA - Campus Police Facility | [17 empty] | UNCSA - Campus Police Facility
70 | UNCSA - Central Storage Facility | [17 empty] | UNCSA - Central Storage Facility
71 | NCSU - Talley Student Center Renovation and Addition | [17 empty] | NCSU - Talley Student Center Renovation and Addition
NCSU - Talley Student Union
| Utility |  | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 |  | Total | Units |  | Total | Units
| Electric (kWh) |  | 388256.6608 | 401822.6825 | 401297.6684 | 373326.6197 | 344497.625 | 368648.9014 | 368706.3012 | 377279.1033 | 398226.4342 | 344496.569 | 337694.2513 | 346360.3197 |  | 4450613.1364 | kwh |  | 15174.4189 | MMbtu
| Chilled Water (Dtherms) |  | 2989.47 | 2818.7938 | 984.3447 | 1134.2844 | 1098.0269 | 420.6158 | 312.2264 | 565.5972 | 704.3402 | 746.4359 | 2103.3341 | 3060.2535 |  | 16937.723 | dthrms |  | 16937.723 | MMbtu
| Steam (1,000 lbs) |  | 495.7705 | 589.2002 | 940.5303 | 1062.1602 | 1047.5391 | 1897.791 | 1572.4191 | 1016.0755 | 955.7054 | 605.1602 | 462.3594 | 385.1055 |  | 11029.8161 | 1000 lbs |  | 11029.8161 | MMbtu
| Water (CCF) |  | 595.2834 | 713.028 | 726.2019 | 698.2714 | 426.4318 | 615.8422 | 705.9759 | 656.9572 | 816.873 | 395.6912 | 357.4049 | 422.0535 |  | 7130.0145 | CCF |  | 5333250.8125 | gallons
| Natural Gas (thms) |  | 2568 | 3948 | 3553 | 3645 | 2396 | 3635 | 3761 | 3131 | 3758 | 1767 | 1580 | 2029 |  | 35771 | thms |  | 35771 | thms
| Electric Cost ($) |  | 33390.0728 | 34556.7507 | 34511.5995 | 32106.0893 | 29626.7957 | 31703.8055 | 31708.7419 | 32446.0029 | 34247.4733 | 29626.7049 | 29041.7056 | 30133.3478 |  | 383099.0901 | $
| Chilled Water Cost ($) |  | 41762.8959 | 39378.5496 | 13751.2953 | 15845.9536 | 15339.4354 | 5876.0029 | 4361.8033 | 7901.3927 | 9839.6333 | 10427.7092 | 29383.5777 | 39630.2828 |  | 233498.5317 | $
| Steam Cost ($) |  | 6638.3671 | 7889.3906 | 12593.7004 | 14222.3245 | 14026.548 | 25411.4217 | 21054.6914 | 13605.2507 | 12796.8951 | 8103.0945 | 6190.992 | 4628.9677 |  | 147161.6437 | $
| Water Cost ($) |  | 5476.6075 | 6559.8579 | 6681.0572 | 6424.0968 | 3923.1723 | 5665.7487 | 6494.9786 | 6044.0064 | 7515.2316 | 3640.3588 | 3288.1252 | 3937.7589 |  | 65650.9999 | $
| Natural Gas ($) |  | 1844.29 | 2807.19 | 2513.78 | 2394.85 | 1576.31 | 2136.78 | 2270.12 | 1909.88 | 2378.54 | 1145.41 | 1029.6 | 1307.68 |  | 23314.43 | $
72 | Nash CC - CE and BLET | [17 empty] | Nash CC - CE and BLET
Nash Community College - Continuing Education Building 2015-2016 (July 1, 2015 - June 30, 2016) | bar: 2015-08-01 to 2016-01-01
| Utility | Jun-15 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-14
| Electricity (KWhs) |  |  | 68480 | 102000 | 85760 | 62880 | 62400 | 66240 | 46000 | 60080 | 59840 | 82000 | 89840
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) |  | 244 | 479 | 724 | 1416 | 2857 | 4292 | 4199 | 6262 | 5811 | 2043 | 1464 | 1040
| Water (CCF) |  | 320 | 300 | 295 | 33 | 31 | 21 | 13 | 23 | 38 | 31 | 29 | 137
| Electricity Cost ($) |  | 75.84 | 7149.64 | 10385.95 | 8599.12 | 6849.76 | 6747.39 | 7022.24 | 5657.86 | 6744.76 | 6727.04 | 8476.17 | 8942.58
Steam Costs ($)
| Chilled Water Costs ($) |  | 695.2 | 1304.4 | 1282.9 | 156.3 | 147.7 | 104.7 | 70.3 | 133.3 | 177.8 | 147.7 | 139.1 | 603.5
| Natural Gas Costs ($) |  | 323.85 | 638.73 | 897.5 | 1458.84 | 2901.99 | 4313.7 | 4221.68 | 6326.38 | 5807.43 | 2093.56 | 1499.91 | 1082.29
Note: Electricity Cost Includes Steet Lights for Continuing Education Buildiing | bar: 2015-08-01 to 2015-10-01
73 | UNCSA - Film School Production Design Facility | [17 empty] | UNCSA - Film School Production Design Facility
74 | UNCC - Holshouser Residence Hall Renovation | [17 empty] | UNCC - Holshouser Residence Hall Renovation
75 | UNCC - Phase XIII Residence Hall | [17 empty] | UNCC - Phase XIII Residence Hall
76 | ASU - Belk Residence Hall Renovation | [17 empty] | ASU - Belk Residence Hall Renovation
Bldg. # | Building Name | time axis 2010-07-01 to 2016-06-01
ELECTRICITY
239 | Belk Residence Hall Total Electricity Use | 16320 | 10720 | 26400 | 28160 | 24320 | 20960 | 13920 | 20000 | 19040 | 21120 | 15680 | 11040 | 13920 | 10080 | 25920 | 20640 | 21920 | 20800 | 10880 | 21440 | 17440 | 21760 | 18240 | 11040 | 14240 | 11520 | 23840 | 21440 | 20960 | 19520 | 11680 | 21760 | 16000 | 19520 | 17600 | 9920 | 12960 | 10080 | 24960 | 20960 | 17920 | 20800 | 12000 | 21280 | 16160 | 19040 | 18720 | 5600 | 631 | 482 | 1192 | 2305 | 5419 | 6325 | 7358 | 8245 | 7236 | 6239 | 6000 | 11400 | 48240 | 51720 | 54840 | 46320 | 38280 | 31800 | 30720 | 36120 | 35040 | 38760 | 36240 | 28800
239 | Belk Residence Hall Total Electricity Cost | 1142.01 | 754.39 | 1839.74 | 1961.57 | 1695.77 | 1463.19 | 1085.85 | 1660.05 | 1580.96 | 1752.32 | 1304.14 | 921.88 | 1159.15 | 842.8 | 2147.77 | 1712.78 | 1818.23 | 1725.96 | 919.61 | 2008.07 | 1635.73 | 2037.84 | 1710.2 | 1040 | 1337.87 | 1084.68 | 2231.46 | 2008.07 | 1963.39 | 1829.34 | 916.63 | 2027.47 | 1492.97 | 1818.71 | 1641.04 | 930.34 | 1211.66 | 915.7 | 2249.2 | 1890.74 | 1618.31 | 1876.39 | 1122.82 | 1941.43 | 1448.59 | 1704.55 | 1676.11 | 510.07 | 66.64 | 53.85 | 119.45 | 222.28 | 510 | 593.71 | 711.77 | 748.31 | 677.97 | 578 | 545.97 | 1026.16 | 4302.14 | 4611.59 | 4889.04 | 4131.41 | 3416.46 | 2840.22 | 2744.19 | 3062.34 | 2834.92 | 3134.57 | 2931.58 | 2332.28
STEAM
239 | Belk Residence Hall Steam Use in lbs. | 54223 | 70907 | 75078 | 78414.8 | 171845.2 | 283628 | 308654 | 250260 | 287799 | 193534.4 | 78414.8 | 74243.8 | 58394 | 115953.8 | 117622.2 | 103440.8 | 161000.6 | 241918 | 279457 | 285296.4 | 258602 | 191031.8 | 103440.8 | 113451.2 | 97601.4 | 118456.4 | 134306.2 | 141814 | 201042.2 | 216892 | 275286 | 291970 | 316996 | 201042.2 | 150156 | 116788 | 114285.4 | 125130 | 136808.8 | 145985 | 223565.6 | 250260 | 392908.2 | 302814.6 | 310322.4 | 243586.4 | 116788 | 4171 | 4171 | 4171 | 4171 | 4171 | 4171 | 218560.4 | 500520 | 583940 | 291970 | 125130 | 16684 | 25026 | 133472 | 125130 | 108446 | 133472 | 165171.6 | 250260 | 107611.8 | 125964.2 | 80083.2 | 69238.6 | 36704.8 | 35036.4
239 | Belk Residence Hall Steam Cost | 2386.15 | 3120.35 | 3303.9 | 3450.74 | 7562.26 | 12481.4 | 13582.7 | 11013 | 12664.95 | 8516.72 | 3450.74 | 1559.28 | 1226.4 | 2435.28 | 2470.32 | 2172.48 | 3381.36 | 5080.8 | 5869.2 | 5991.84 | 5431.2 | 4012.08 | 2172.48 | 2382.72 | 2049.84 | 2487.84 | 2820.72 | 2978.4 | 4222.32 | 4555.2 | 5781.6 | 6132 | 6657.6 | 4222.32 | 3153.6 | 2452.8 | 2400.24 | 2628 | 2873.28 | 3066 | 4695.36 | 5256 | 8251.92 | 6359.76 | 6517.44 | 5115.84 | 2452.8 | 87.6 | 87.6 | 87.6 | 87.6 | 87.6 | 87.6 | 4590.24 | 10512 | 12264 | 6132 | 2628 | 350.4 | 525.6 | 2803.2 | 2628 | 2277.6 | 2803.2 | 3468.96 | 5256 | 2260.08 | 2645.52 | 1681.92 | 1454.16 | 770.88 | 735.84
WATER & SEWER
239 | Belk Residence Hall Water Use | 40000 | 46000 | 118000 | 160000 | 100000 | 90000 | 60000 | 190000 | 160000 | 50000 | 20000 | 30000 | 24000 | 92000 | 140000 | 130000 | 124000 | 72000 | 103000 | 135000 | 116000 | 129000 | 48000 | 34000 | 20000 | 94000 | 137000 | 147000 | 131000 | 52000 | 118000 | 137000 | 92000 | 128000 | 45000 | 25000 | 25000 | 92000 | 141000 | 151000 | 111000 | 58000 | 115000 | 135000 | 104000 | 124000 | 13000 | 21000 | 0 | 0 | 0 | 9000 | 20000 | 21000 | 29000 | 30000 | 554000 | 0 | 6000 | 22000 | 44000 | 110000 | 162000 | 144000 | 114000 | 37000 | 94000 | 104000 | 81000 | 110000 | 50000 | 53000
239 | Belk Residence Hall Water & Sewer Cost | 184 | 151.8 | 247.8 | 288 | 320 | 198 | 240 | 361 | 640 | 215 | 94 | 102 | 100.8 | 230 | 294 | 468 | 483.6 | 280.8 | 412 | 364.5 | 371.2 | 670.8 | 211.2 | 248.2 | 62 | 338.4 | 315.1 | 426.3 | 379.9 | 239.2 | 436.6 | 616.5 | 386.4 | 627.2 | 315 | 150 | 210 | 441.6 | 648.6 | 649.3 | 588.3 | 458.2 | 667 | 877.5 | 676 | 744 | 88.4 | 140.7 | 0 | 0 | 0 | 76.5 | 148 | 205.8 | 118.9 | 228 | 2548.4 | 0 | 38.4 | 151.8 | 211.2 | 473 | 502.2 | 1065.6 | 615.6 | 247.9 | 357.2 | 436.8 | 421.2 | 385 | 340 | 439.9
77 | UNCW - S & BS Building Renovation | 2011-12-01: UNCW - S & BS Building Renovation
78 | ECU - Gateway Residence Hall (Belk Replacement) | 2011-12-01: ECU - Gateway Residence Hall (Belk Replacement)
3 | ECU - Gateway Residence Hall (Belk Replacement)
| Utility | 2010-07-01: Jun-15; 2010-08-01: 2015-07-01; 2010-09-01: 2015-08-01; 2010-10-01: 2015-09-01; 2010-11-01: 2015-10-01; 2010-12-01: 2015-11-01; 2011-01-01: 2015-12-01; 2011-02-01: 2016-01-01; 2011-03-01: 2016-02-01; 2011-04-01: 2016-03-01; 2011-05-01: 2016-04-01; 2011-06-01: 2016-05-01; 2011-07-01: 2016-06-01; 2011-08-01: 2016-07-01; 2011-09-01: 2016-08-01; 2011-10-01: 2016-09-14
| Electricity (KWhs) | 2010-09-01: 270712.91; 2010-10-01: 280841.83; 2010-11-01: 227735.55; 2010-12-01: 202331.36; 2011-01-01: 182200.91; 2011-02-01: 160156.85; 2011-03-01: 175411.62; 2011-04-01: 187663.05; 2011-05-01: 196419.51; 2011-06-01: 183772.96; 2011-07-01: 197344.59; 2011-08-01: 271022.3
| Steam (lbs) | 2010-07-01: Condensate meter not communicating - Manual readings commenced in Aug 2016
Chilled Water (Dtherms)
Natural Gas (Therms)
| Water (kGal) | 2010-10-01: 1059.16; 2010-11-01: 851.97; 2010-12-01: 709.1; 2011-01-01: 532.57; 2011-02-01: 202.7; 2011-03-01: 667.21; 2011-04-01: 525.83; 2011-05-01: 724.05; 2011-06-01: 488.43; 2011-07-01: 213
| Electricity Cost ($) | 2010-07-01: 0; 2010-08-01: 0; 2010-09-01: 23755.0579; 2010-10-01: 24643.8706; 2010-11-01: 19983.7945; 2010-12-01: 17754.5768; 2011-01-01: 15988.1299; 2011-02-01: 14053.7636; 2011-03-01: 15392.3697; 2011-04-01: 16467.4326; 2011-05-01: 17235.812; 2011-06-01: 16126.0772; 2011-07-01: 17316.9878; 2011-08-01: 23782.2068; 2011-09-01: 0; 2011-10-01: 0
Steam Costs ($)
Chilled Water Costs ($)
Natural Gas Costs ($)
79 | UNCC - Oak Residence Hall Renovation | 2011-12-01: UNCC - Oak Residence Hall Renovation
Note on D659: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on E659: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on F659: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on G659: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on H659: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on O659: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on D664: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on E664: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on F664: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on G664: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on H664: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on O664: Building used internal summer boiler this month. Central steam plant is isolated from the building.
Note on H666: Turned off summer boiler off 12/7/15
Note on N666: Summer boiler operating
Note on F795: Duane reported of lot of flooding from toilets running and overflowing.
Note on C1016: Nihal Ali Al Raees: Data for (19) Days
Note on D1016: Nihal Ali Al Raees: Data for (15) days
Note on E1016: Nihal Ali Al Raees: Data for (25) days
Note on H1016: Nihal Ali Al Raees: Data for (26) days
Note on I1016: Nihal Ali Al Raees: Data for (27) days
Note on J1016: Nihal Ali Al Raees: Data for (20) days
Note on N1016: Nihal Ali Al Raees: Data for (10) days
Note on D1043: First bill to WSSU covers 3/17/15 to 7/31/15, divided evenly over the five month period.

## 2015 Summary
|  | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [12 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [13 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [10 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project | [12 empty] | State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project
2015-09-22 |  | PACKAGE DATA (Pages 1 - 6) | [11 empty] | 2015-09-22 | ANNUAL ENERGY USAGE (x1,000,000 BTU/YEAR) (Pages 7 -12) | [12 empty] | 2015-09-22 | ANNUAL ENERGY USAGE ($/YEAR) (pages 13-18) | [9 empty] | 2015-09-22 | ANNUAL INDOOR WATER USAGE (GALLONS/YEAR) (Pages 19 - 24) | [11 empty] | 2015-09-22 | Construction and Design Costs and Fees (Pages 25 - 30)
Project | LEED | Agency or Institution | County | Energy Contact | SCO ID# |  | Energy Model Report Phase | Construction Contract Award Date | Actual or Projected Acceptance Date | Principal Occupancy / Category / Use(s) | Number of Beds | Size (GSF from building code summary) | Floors (from building code summary) | Project | ASHRAE Standard | Baseline | Site EUI Baseline (kBtu/Sq Ft/yr) | Proposed | Site EUI Proposed (kBtu/Sq Ft/yr) | Proposed improvement in energy efficiency | Proposed Energy Savings | Date of Meter Data | Metered Energy Usage | Site EUI Metered (kBtu/Sq Ft/yr) | Metered improvement in energy efficiency | Meets SB 668 (from unclean data) | Metered Energy Savings (from unclean data) | Project | Baseline | Baseline ($/Yr/Sq Ft) | Proposed | Proposed ($/Yr/Sq Ft) | Proposed % improvement in energy cost | Proposed Savings in Energy Cost | Metered | Metered ($/Yr/Sq Ft) | Metered % improvement in energy cost | Metered Savings in Energy Cost | Project | Baseline (Gallons/Year) | Baseline (Gal/Res/Yr) | Baseline (Gal/Sq Ft/Yr) | Proposed (Gallons/Year) | Proposed (Gal/Res/Yr) | Proposed (Gal/Sq Ft/Yr) | Proposed % improvement in water usage | Proposed Savings (Gallons/Year) | Metered (Gallons/Year) | Metered (Gal/Res/Yr) | Metered (Gal/Sq Ft/Yr) | Metered improvement in water usage | Project | Cost Estimate or Original Amount Construction Contract | Construction Cost/SF | Designer's Baseline (non-SB668) Estimate | Original Total Design Fee (without amendments) | Additional Design Fees (LEED or SB 668 - included in OTDF) | Advance Planning Contract Item G | Commissioning Fee | Simple Payback in Years (Net Savings Required /HB 628) | Modeler | ASHRAE Standard
Cone Residence Hall Renovation | Gold | ASU | Watauga | Jerry Marshall | 08-07272-01A | 2009-01-20 | CD | 2009-09-14 | 2010-06-23 | Residence Hall | 278 | 58803 | 8 | Cone Residence Hall Renovation | 90.1-2004 | 3467 | 58.9596 | 1993 | 33.8928 | 42.52% | 1474 | 2015-08-26 | 4977.5037 | 84.6471 | -43.57% |  | -1510.5037 | Cone Residence Hall Renovation | 81830 | 1.3916 | 43969 | 0.74773 | 46.27% | 37861 | 119426.8458 | 2.031 | -45.95% | -37596.8458 | Cone Residence Hall Renovation | 2000376 | 7195.5971 | 34.0183 | 1397116 | 5025.5971 | 23.7593 | 30.16% | 603260 | 1690223 | 6079.9388 | 28.7438 | 15.5% | Cone Residence Hall Renovation | 7585100 | 128.9917 | 5965486 | 883660 | 0 |  | 62500 | 44.4287 | SKA | 90.1-2004
Prospector Hall Renovation Phase II | None | UNCC | Mecklenburg | Tony Schallert | 06-07223-01A | 2013-03-15 | LEED submit. | 2010-08-12 | 2011-05-30 | Food Service/Dining | NA | 22705 | 2 | Prospector Hall Renovation Phase II | 90.1-2004 | 2082 | 91.6979 | 1477 | 65.0518 | 29.06% | 605 | 2015-08-04 | 7539.908 | 332.0814 | -262.1% |  | -5457.908 | Prospector Hall Renovation Phase II | 30538 | 1.345 | 21943 | 0.96644 | 28.15% | 8595 | 74557.2589 | 3.2837 | -144.1% | -44019.2589 | Prospector Hall Renovation Phase II | 48654 | NA | 2.1429 | 27934 | NA | 1.2303 | 42.59% | 20720 | 4749014.6 | NA | 209.1616 | -9661% | Prospector Hall Renovation Phase II | 4029200 | 177.4587 | 3944812 | 295500 | 0 |  | 65100 | 17.3924 | M&C | 90.1-2004
Miltimore Residence Hall | Silver | UNCC | Mecklenburg | Tony Schallert | 05-06656-01A | 2009-06-10 | CD | 2009-07-22 | 2011-07-19 | Residence Hall | 431 | 173086 | 5 | Miltimore Residence Hall | 90.1-2004 | 38283 | 221.1791 | 32882 | 189.9749 | 14.11% | 5401 | 2015-08-04 | 11699.8187 | 67.5954 | 69.44% | ü | 26583.1813 | Miltimore Residence Hall | 478677 | 2.7655 | 411144 | 2.3754 | 14.11% | 67533 | 152079.2516 | 0.87863 | 68.23% | 326597.7484 | Miltimore Residence Hall | 6961135 | 16151.1253 | 40.2178 | 5188175 | 12037.529 | 29.9746 | 25.47% | 1772960 | 4749014.6 | 11018.5954 | 27.4373 | 31.78% | Miltimore Residence Hall | 32995620 | 190.6314 | 33000165 | 2747550 | 58700 |  | 177000 | 3.4228 | CN | 90.1-2004
Nursing Building | Silver | NCCU | Durham | Ondin Mihalcescu <o.mihalcescu@nccu.edu> | 07-07203-02A | 2009-12-22 | CD | 2010-01-25 | 2011-08-05 | Offices/Classrooms | NA | 69610 | 5 | Nursing Building | 90.1-2004 | 6048.6 | 86.8927 | 2596.2 | 37.2964 | 57.08% | 3452.4 | 2015-08-26 | 5266.0815 | 75.6512 | 12.94% |  | 782.5185 | Nursing Building | 148249 | 2.1297 | 61035 | 0.87681 | 58.83% | 87214 | 53111.43 | 0.76299 | 64.17% | 95137.57 | Nursing Building | 871150 | NA | 12.5147 | 601563 | NA | 8.6419 | 30.95% | 269587 | 573514.04 | NA | 8.239 | 34.17% | Nursing Building | 16198787 | 232.7078 | 16003466 | 1795875 | 82875 | 16175 | 265694 | 6.4217 | RMF | 90.1-2004
Chidley North Residence Hall | Gold | NCCU | Durham | Ondin Mihalcescu <o.mihalcescu@nccu.edu> | 05-07248-02A | 2012-03-23 | LEED submit. | 2009-08-03 | 2011-08-10 | Residence Hall | 528 | 133570 | 4 | Chidley North Residence Hall | 90.1-2004 | 16482 | 123.396 | 10635 | 79.6212 | 35.48% | 5847 | 2015-08-26 | 5468.1768 | 40.9387 | 66.82% |  | 11013.8232 | Chidley North Residence Hall | 292778 | 2.1919 | 198708 | 1.4877 | 32.13% | 94070 | 90016.62 | 0.67393 | 69.25% | 202761.38 | Chidley North Residence Hall | 6283057 | 11899.7292 | 47.0394 | 4373148 | 8282.4773 | 32.7405 | 30.4% | 1909909 | 6365098.52 | 12055.1108 | 47.6537 | -1.306% | Chidley North Residence Hall | 23276802 | 174.2667 | 21956196 | 2186050 | 173500 |  | 104934 | 16.9984 | SWA | 90.1-2004
The Loudermilk Center for Excellence | None | UNC-CH | Orange |  | 09-07851-01A | 2010-05-17 | CD | No Contract (Found. Proj) | 2011-08-18 | Offices/Locker rooms/Club | NA | 170189 | 6 | The Loudermilk Center for Excellence | 90.1-2004 | 10672 | 62.7068 | 7143 | 41.971 | 33.07% | 3529 | 2015-08-17 | 25820.0525 | 151.714 | -141.9% |  | -15148.0525 | The Loudermilk Center for Excellence | 116674 | 0.68556 | 78320 | 0.46019 | 32.87% | 38354 | 274420.26 | 1.6124 | -135.2% | -157746.26 | The Loudermilk Center for Excellence | 1518337 | NA | 8.9215 | 991995 | NA | 5.8288 | 34.67% | 526342 | 1871000 | NA | 10.9937 | -23.23% | The Loudermilk Center for Excellence | (Foundation Project) |  |  | (Foundation Project) |  | (Foundation Project) | (Foundation Project) |  | MSWG | 90.1-2004
Davis Event Center | In Progress | DoAG&CS | Buncombe | Debbie Robertson <debbie.robertson@ncagr.gov> | 08-07347-02A | 2010-05-06 | CD | 2010-10-26 | 2011-08-19 | Assembly | NA | 67904 | 1 | Davis Arena Add & Renov | 90.1-2004 | 2961 | 43.6057 | 1736 | 25.5655 | 41.37% | 1225 | 2015-08-24 | 3571.0091 | 52.5891 | -20.6% |  | -610.0091 | Davis Arena Add & Renov | 72840 | 1.0727 | 42637 | 0.6279 | 41.46% | 30203 | 67408.87 | 0.99271 | 7.456% | 5431.13 | Davis Arena Add & Renov | 109500 | NA | 1.6126 | 87313 | NA | 1.2858 | 20.26% | 22187 | 913308 | NA | 13.45 | -734.1% | Davis Arena Add & Renov | 5507600 | 81.1086 | 5351000 | 484000 | 15000 |  | 43640 | 7.1264 |  | 90.1-2004
Student Health Center Add and Renovation | Gold | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 07-07345-02A | 2010-03-12 | CD | 2010-06-10 | 2011-09-12 | Offices/Clinics | NA | 24663 | 2 | Student Health Center Addition and Renovation | 90.1-2004 | 2746 | 111.3409 | 1547 | 62.7255 | 43.66% | 1199 | 2015-08-26 | 13935.8357 | 565.0503 | -407.5% |  | -11189.8357 | Student Health Center Addition and Renovation | 69316 | 2.8105 | 38688 | 1.5687 | 44.19% | 30628 | 227815.7231 | 9.2371 | -228.7% | -158499.7231 | Student Health Center Addition and Renovation | 320198 | NA | 12.9829 | 230958 | NA | 9.3646 | 27.87% | 89240 | 227815.7231 | NA | 9.2371 | 28.85% | Student Health Center Addition and Renovation | 6017900 | 244.0052 | 5778782 | 634045 | 65575 |  | 106438 | 13.4234 | RMF | 90.1-2004
Gilchrist Education and Psychology Complex | In Progress | ECSU | Pasquotank | Elizabeth Linney | 07-07081-02A | 2010-01-11 | CD | 2010-01-05 | 2012-02-01 | Office/Classroom | NA | 48112 | 3 | Gilchrist Education and Psychology Complex | 90.1-2004 | 3078 | 63.9757 | 1625 | 33.7754 | 47.21% | 1453 | 2015-08-27 | 2146.7497 | 44.6198 | 30.26% | ü | 931.2503 | Gilchrist Education and Psychology Complex | 64655 | 1.3438 | 34128 | 0.70934 | 47.22% | 30527 | 76577.07 | 1.5916 | -18.44% | -11922.07 | Gilchrist Education and Psychology Complex | 1506938 | NA | 31.3215 | 1056525 | NA | 21.9597 | 29.89% | 450413 | 56394.5624 | NA | 1.1722 | 96.26% | Gilchrist Education and Psychology Complex | 14394127 | 299.1796 | 13822099 | 1654600 | 35000 |  | 57000 | 21.7522 | AEI | 90.1-2004
EPIC | None | UNCC | Mecklenburg | Tony Schallert | 07-07078-02A | 2009-08-21 | CD | 2009-09-30 | 2012-04-12 | Offices/Labs/Classrooms | NA | 200164 | 4 | EPIC | 90.1-2004 | 30494.5 | 152.3476 | 18910.6 | 94.4755 | 37.99% | 11583.9 | 2015-08-04 | 66560.0861 | 332.5278 | -118.3% |  | -36065.5861 | EPIC | 284103 | 1.4194 | 165774 | 0.82819 | 41.65% | 118329 | 518840.9275 | 2.5921 | -82.62% | -234737.9275 | EPIC | 3172838 | NA | 15.8512 | 1985718 | NA | 9.9205 | 37.42% | 1187120 | 663640.56 | NA | 3.3155 | 79.08% | EPIC | 61500000 | 307.2481 | 51725930 | 5792635 | 221084 |  | 404815 | 87.8903 | M&L | 90.1-2004
SENC Ag Center | None | DoAG&CS | Robeson | Debbie Robertson <debbie.robertson@ncagr.gov> | 08-07348-02A | 2010-06-28 | DD | 2011-03-22 | 2012-04-12 | Equine & Livestock | NA | 55605 | 1 | SENC Ag Center | 90.1-2004 | 1743 | 31.3461 | 749 | 13.47 | 57.03% | 994 | 2015-08-24 | 731.9785 | 13.1639 | 58% | ü | 1011.0215 | SENC Ag Center | 42886 | 0.77126 | 28420 | 0.51111 | 33.73% | 14466 | 12828.84 | 0.23071 | 70.09% | 30057.16 | SENC Ag Center | 243256 | NA | 4.3747 | 171756 | NA | 3.0889 | 29.39% | 71500 | 594770 | NA | 10.6963 | -144.5% | SENC Ag Center | 4072395 | 73.2379 | 3919435 | 363080 | 0 |  | 11870 | 11.3943 |  | 90.1-2004
Veteran's Nursing Home - Swannanoa | None | NCDOA-VA | Buncombe | diane.norris@doa.nc.gov | 06-06924-05A | 2009-12-22 | CD | 2010-05-24 | 2012-05-31 | Nursing Home | 100 | 108770 | 1 | Veteran's Nursing Home - Swananoa | 90.1-2004 | 8495 | 78.1006 | 5163 | 47.4671 | 39.22% | 3332 | 2015-08-05 | 9280.6087 | 85.3232 | -9.248% |  | -785.6087 | Veteran's Nursing Home - Swananoa | 213106 | 1.9592 | 120807 | 1.1107 | 43.31% | 92299 | 173458.66 | 1.5947 | 18.6% | 39647.34 | Veteran's Nursing Home - Swananoa | 4378540 | 43785.4 | 40.255 | 3400982 | 34009.82 | 31.2676 | 22.33% | 977558 | 3709584 | 37095.84 | 34.1048 | 15.28% | Veteran's Nursing Home - Swananoa | 16135100 | 148.3415 | 15834228 | 1250000 | 0 |  | 96941 | 4.31 | MCBH | 90.1-2004
Russell Classroom Building | None | Pitt CC | Pitt | Don Heisey 'dheisey@email.pittcc.edu' | 08-07329-02A | 2010-04-12 | CD | 2010-12-06 | 2012-06-27 | Office/Classroom | NA | 50434 | 2 | Russell Classroom Building | 90.1-2004 | 3018 | 59.8406 | 1900 | 37.673 | 37.04% | 1118 | 2015-08-21 | 2060.4273 | 40.8539 | 31.73% | ü | 957.5727 | Russell Classroom Building | 91928 | 1.8227 | 56777 | 1.1258 | 38.24% | 35151 | 86351.1 | 1.7122 | 6.067% | 5576.9 | Russell Classroom Building | 1217970 | NA | 24.1498 | 954495 | NA | 18.9256 | 21.63% | 263475 | 340018.36 | NA | 6.7418 | 72.08% | Russell Classroom Building | 7393799 | 146.6035 | 7243287 | 943138 | 52150 |  | 42310 | 6.9691 | PDC | 90.1-2004
Bailey Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Bailey Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2015-08-19 | 3737.6975 | 121.6105 | 7.848% |  | 318.3025 | Bailey Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 21544.62 | 0.70098 | 63.86% | 38063.38 | Bailey Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 463600 | 5390.6977 | 15.0838 | -41.39% | Bailey Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Coit Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Coit Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2015-08-19 | 2996.5501 | 97.4963 | 26.12% | ü | 1059.4499 | Coit Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 14804.89 | 0.48169 | 75.16% | 44803.11 | Coit Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 465900 | 5417.4419 | 15.1586 | -42.09% | Coit Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Cotten Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Cotten Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2015-08-19 | 3009.2255 | 97.9088 | 25.81% | ü | 1046.7745 | Cotten Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 19763.29 | 0.64302 | 66.84% | 39844.71 | Cotten Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 525800 | 6113.9535 | 17.1075 | -60.36% | Cotten Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Gray Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Gray Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2015-08-19 | 2464.3936 | 80.182 | 39.24% | ü | 1591.6064 | Gray Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 19024.34 | 0.61898 | 68.08% | 40583.66 | Gray Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 496800 | 5776.7442 | 16.164 | -51.52% | Gray Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Hinshaw Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Hinshaw Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2015-08-19 | 3205.4454 | 104.293 | 20.97% | ü | 850.5546 | Hinshaw Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 23000.83 | 0.74836 | 61.41% | 36607.17 | Hinshaw Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 536100 | 6233.7209 | 17.4427 | -63.5% | Hinshaw Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Jamison Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Jamison Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2015-08-19 | 7152.6503 | 232.72 | -76.35% |  | -3096.6503 | Jamison Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 19585.99 | 0.63725 | 67.14% | 40022.01 | Jamison Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 525200 | 6106.9767 | 17.088 | -60.18% | Jamison Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Shaw Residence Hall Renovation | Gold | UNC-G | Guilford | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 118 | 54847 | 4 | Shaw Residence Hall Renovation | 90.1-2004 | 4056 | 73.9512 | 3076 | 56.0833 | 24.16% | 980 | 2015-08-19 | 7720.2166 | 140.7591 | -90.34% |  | -3664.2166 | Shaw Residence Hall Renovation | 59608 | 1.0868 | 46163 | 0.84167 | 22.56% | 13445 | 38727.49 | 0.7061 | 35.03% | 20880.51 | Shaw Residence Hall Renovation | 327880 | 2778.6441 | 5.9781 | 209536 | 1775.7288 | 3.8204 | 36.09% | 118344 | 925800 | 7845.7627 | 16.8797 | -182.4% | Shaw Residence Hall Renovation | 6196641.1429 | 112.9805 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Harrill Residence Hall Renovation | Gold | WCU | Jackson | David King <dbking@email.wcu.edu> | 03-07291-02A | 2011-01-07 | CD | 2011-08-03 | 2012-08-02 | Residence Hall | 350 | 71505 | 10 | Harrill Residence Hall Renovation | 90.1-2004 | 5122 | 71.6314 | 3189 | 44.5983 | 37.74% | 1933 | 2015-07-29 | 2923.6884 | 40.8879 | 42.92% | ü | 2198.3116 | Harrill Residence Hall Renovation | 114129 | 1.5961 | 82978 | 1.1605 | 27.29% | 31151 | 96702.5318 | 1.3524 | 15.27% | 17426.4682 | Harrill Residence Hall Renovation | 2675470 | 7644.2 | 37.4165 | 1801347 | 5146.7057 | 25.1919 | 32.67% | 874123 | 1553840 | 4439.5429 | 21.7305 | 41.92% | Harrill Residence Hall Renovation | 13435000 | 187.889 | 11750000 | 998800 | 0 |  | 153235 | 59.0105 | Optima | 90.1-2004
Renaissance Residence Hall | Silver | FSU | Cumberland | Jon Parsons | 11-08594-01A | 2011-09-12 | CD | No Contract (Found. Proj) | 2012-08-07 | Residence Hall | 340 | 85000 | 3 | Renaissance Residence Hall | 90.1-2004 | 5499 | 64.6941 | 3624 | 42.6353 | 34.1% | 1875 | 2015-08-28 | No Data |  |  |  |  | Renaissance Residence Hall | 174915 | 2.0578 | 88110 | 1.0366 | 49.63% | 86805 | No Data |  |  |  | Renaissance Residence Hall | 2636463 | 7754.3029 | 31.0172 | 1734140 | 5100.4118 | 20.4016 | 34.22% | 902323 | No Data |  |  |  | Renaissance Residence Hall | (Foundation Project) |  |  | (Foundation Project) | (Foundation Project) |  | (Foundation Project) |  | Optima | 90.1-2004
Health Science Building | Silver | UNCP | Robeson | Terry W. Divine <terry.divine@uncp.edu> | 06-06859-02A | 2009-11-17 | CD | 2010-07-16 | 2012-08-07 | Office/Classroom | NA | 87000 | 3 | Health Science Building | 90.1-2004 | 7163 | 82.3333 | 4954 | 56.9425 | 30.84% | 2209 | 2015-08-03 | 7364.686 | 84.6516 | -2.816% |  | -201.686 | Health Science Building | 98379 | 1.1308 | 65154 | 0.7489 | 33.77% | 33225 | 130334.915 | 1.4981 | -32.48% | -31955.915 | Health Science Building | 2606625 | NA | 29.9612 | 1672375 | NA | 19.2227 | 35.84% | 934250 | 848245 | NA | 9.7499 | 67.46% | Health Science Building | 14834300 | 170.5092 | 14419316 | 2004260 | 47460 |  | 0 | 13.9186 | MSWG | 90.1-2004
Overlook Residence Hall | None | UNCA | Buncombe | 'dtodd@unca.edu' | 09-07924-02B | 2011-02-28 | CD | 2011-07-14 | 2012-08-08 | Residence Hall | 300 | 91370 | 6 | Overlook Residence Hall | 90.1-2004 | 5737 | 62.7887 | 3460 | 37.868 | 39.69% | 2277 | No Data | [5 empty] | Overlook Residence Hall | 89281 | 0.97714 | 63609 | 0.69617 | 28.75% | 25672 | No Data |  |  |  | Overlook Residence Hall | 2888310 | 9627.7 | 31.6111 | 1728304 | 5761.0133 | 18.9154 | 40.16% | 1160006 | No Data |  |  |  | Overlook Residence Hall | 16467600 | 180.2298 | 14927082 | 1685000 | 0 |  | 85000 | 63.3187 | MSWG | 90.1-2004
Viking Tower Residence Hall | None | ECSU | Pasquotank | Elizabeth Linney | 00-06539-03A | 2010-09-03 | CD | 2011-01-25 | 2012-08-17 | Residence Hall | 210 | 53896 | 3 | Viking Tower Residence Hall | 90.1-2004 | 9118 | 169.1777 | 6399 | 118.7287 | 29.82% | 2719 | 2015-08-27 | 2074.1586 | 38.4845 | 77.25% | ü | 7043.8414 | Viking Tower Residence Hall | 217417 | 4.034 | 145256 | 2.6951 | 33.19% | 72161 | 64911.06 | 1.2044 | 70.14% | 152505.94 | Viking Tower Residence Hall | 1193460 | 5683.1429 | 22.1438 | 938250 | 4467.8571 | 17.4085 | 21.38% | 255210 | 2650585.7972 | 12621.8371 | 49.1796 | -122.1% | Viking Tower Residence Hall | 12474496 | 231.455 | 12222788 | 1199950 | 40000 |  | 85000 | 5.2204 | RMF | 90.1-2004
Teaching Laboratory Building | Silver | UNCW | New Hanover | Steve Sharpe | 07-07129-02A | 2010-08-06 | CD | 2011-01-21 | 2012-08-24 | Office/Classroom/Labs | NA | 85000 | 3 | Teaching Laboratory Building | 90.1-2004 | 7739 | 91.0471 | 4808 | 56.5647 | 37.87% | 2931 | 2015-08-27 | 21319.33 | 250.8156 | -175.5% |  | -13580.33 | Teaching Laboratory Building | 142633 | 1.678 | 90792 | 1.0681 | 36.35% | 51841 | 206164.53 | 2.4255 | -44.54% | -63531.53 | Teaching Laboratory Building | 751030 | NA | 8.8356 | 507514 | NA | 5.9708 | 32.42% | 243516 | 858349 | NA | 10.0982 | -14.29% | Teaching Laboratory Building | 15645200 | 184.0612 | 15440699 | 2615450 | 156820 |  | 0 | 6.9698 | RMF | 90.1-2004
Rhoades Hall Renovation | None | UNCA | Buncombe | 'dtodd@unca.edu' | 06-06994-02B | 2009-05-11 | CD | 2010-04-26 | 2012-09-10 | Classroom/Lab/Offices | NA | 40434 | 3 and 4 | Rhoades Hall Renovation | 90.1-2004 | 3231 | 79.908 | 1185 | 29.307 | 63.32% | 2046 | No Data | [5 empty] | Rhoades Hall Renovation | 98370 | 2.4329 | 43014 | 1.0638 | 56.27% | 55356 | No Data |  |  |  | Rhoades Hall Renovation | 957500 | NA | 23.6806 | 655500 | NA | 16.2116 | 31.54% | 302000 | No Data |  |  |  | Rhoades Hall Renovation | 5996300 | 148.2985 | 5834600 | 859165 | 76500 |  | 0 |  | ESE | 90.1-2004
Ledyard E. Ross Hall | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 07-07054-02A | 2010-04-16 | CD | 2010-07-01 | 2012-09-14 | Offices/Classrooms/Labs | NA | 157410 | 5 | Ledyard E. Ross Hall | 90.1-2004 | 43253 | 274.7792 | 27864 | 177.0154 | 35.58% | 15389 | 2015-08-14 | Incomplete data |  |  |  |  | Ledyard E. Ross Hall | 420065 | 2.6686 | 302543 | 1.922 | 27.98% | 117522 | Incomplete data |  |  |  | Ledyard E. Ross Hall | 1373584 | NA | 8.7262 | 905161 | NA | 5.7503 | 34.1% | 468423 | No Data |  |  |  | Ledyard E. Ross Hall | 33176057 | 210.7621 | 32922547 | 5394860 | 100000 |  | 346397 |  | BR+A | 90.1-2004
Lena Sue Beam Renovation | None | Gaston College | Gaston | Cynthia McCrory | 07-07395-02A | 2011-03-03 | CD | 2011-07-29 | 2012-10-03 | Office/Classroom | NA | 31418 | 2 | Lena Sue Beam Renovation | 90.1-2004 | 1732 | 55.1276 | 1161 | 36.9533 | 32.97% | 571 | 2015-08-28 | Incomplete data |  |  |  |  | Lena Sue Beam Renovation | 36406 | 1.1588 | 25403 | 0.80855 | 30.22% | 11003 | Incomplete data |  |  |  | Lena Sue Beam Renovation | 689715 | NA | 21.9529 | 403299 | NA | 12.8366 | 41.53% | 286416 | 82682 | NA | 2.6317 | 88.01% | Lena Sue Beam Renovation | 4701800 | 149.6531 | 4657494 | 474000 | 0 |  | 56984 | 9.2057 | M&L | 90.1-2004
Hunt Library | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 07-07171-02A | 2010-08-06 | CD-2 | 2009-08-25 | 2012-10-18 | Library/Offices/Lecture Hall/Meeting | NA | 253028 | 4 | Hunt Library | 90.1-2004 | 15191 | 60.0368 | 10342 | 40.8729 | 31.92% | 4849 | 2015-08-26 | 38091.3048 | 150.5419 | -150.7% |  | -22900.3048 | Hunt Library | 268448 | 1.0609 | 184680 | 0.72988 | 31.2% | 83768 | 709069.8544 | 2.8023 | -164.1% | -440621.8544 | Hunt Library | 4536750 | NA | 17.9298 | 2948625 | NA | 11.6534 | 35.01% | 1588125 | 709069.8544 | NA | 2.8023 | 84.37% | Hunt Library | 81306000 | 321.332 | 80844228 | 9829956 | 200000 |  | 605005 |  | AEI | 90.1-2004
Veteran's Nursing Home - Kinston | None | NCDOA-VA | Lenoir | diane.norris@doa.nc.gov | 06-06924-05A | 2009-12-22 | CD | 2010-05-24 | 2012-10-31 | Nursing Home | 100 | 108770 | 1 | Veteran's Nursing Home - Kinston | 90.1-2004 | 8495 | 78.1006 | 5163 | 47.4671 | 39.22% | 3332 | 2015-08-12 | 9115.7526 | 83.8076 | -7.307% |  | -620.7526 | Veteran's Nursing Home - Kinston | 213106 | 1.9592 | 120807 | 1.1107 | 43.31% | 92299 | 195648.13 | 1.7987 | 8.192% | 17457.87 | Veteran's Nursing Home - Kinston | 4378540 | 43785.4 | 40.255 | 3400982 | 34009.82 | 31.2676 | 22.33% | 977558 | 2992050 | 29920.5 | 27.508 | 31.67% | Veteran's Nursing Home - Kinston | 12903000 | 118.6265 | 12602128 | 1077600 | 0 |  | 107804 | 4.4277 | MCBH | 90.1-2004
Judy W. Rose Football Center | Certified | UNCC | Mecklenburg | Tony Schallert | 08-07833-02A | 2010-12-10 | CD | 2011-03-29 | 2012-10-31 | Lockerrooms/Offices | NA | 43290 | 2 | Judy W. Rose Football Center | 90.1-2004 | 8320 | 192.1922 | 5184 | 119.7505 | 37.69% | 3136 | 2015-08-04 | 9876.4027 | 228.1451 | -18.71% |  | -1556.4027 | Judy W. Rose Football Center | 65175 | 1.5055 | 44151 | 1.0199 | 32.26% | 21024 | 143891.5219 | 3.3239 | -120.8% | -78716.5219 | Judy W. Rose Football Center | 1349491 | NA | 31.1733 | 1113354 | NA | 25.7185 | 17.5% | 236137 | 2243237.04 | NA | 51.8188 | -66.23% | Judy W. Rose Football Center | 12987000 | 300 | 12521456 | 3448472 | 45000 |  | 99500 |  | M&C | 90.1-2004
Klaussner Building Renovation | Gold | Randolph CC | Randolph | Cindi Goodwin | 07-07252-03A | 2010-12-08 | CD | 2011-10-14 | 2012-11-27 | Office/Classroom/Labs | NA | 43967 | 1 | Klaussner Building | 90.1-2004 | 2940 | 66.8683 | 1839 | 41.8268 | 37.45% | 1101 | 2015-08-05 | 3211.1589 | 73.0357 | -9.223% |  | -271.1589 | Klaussner Building | 67485 | 1.5349 | 43675 | 0.99336 | 35.28% | 23810 | 70680.68 | 1.6076 | -4.735% | -3195.68 | Klaussner Building | 544858 | NA | 12.3924 | 436998 | NA | 9.9392 | 19.8% | 107860 | 15176.92 | NA | 0.34519 | 97.21% | Klaussner Building | 6361300 | 144.6835 | 6060565 | 363200 | 0 |  | 49800 | 14.7222 | PDC | 90.1-2004
Plemmons Student Union Addition | In Progress | ASU | Watauga | Jerry Marshall | 08-07327-02A | 2010-08-19 | CD | 2010-06-08 | 2012-12-18 | Office/Classroom/Conference | NA | 50560 | 4 | Plemmons Student Union | 90.1-2004 | 2185 | 43.216 | 1346 | 26.6218 | 38.4% | 839 | 2015-08-26 | 12682.8288 | 250.8471 | -480.4% |  | -10497.8288 | Plemmons Student Union | 53367 | 1.0555 | 32912 | 0.65095 | 38.33% | 20455 | 298171.3005 | 5.8974 | -458.7% | -244804.3005 | Plemmons Student Union | 1220706 | NA | 24.1437 | 950466 | NA | 18.7988 | 22.14% | 270240 | 2355608.9999 | NA | 46.5904 | -92.97% | Plemmons Student Union | 15232506 | 301.2758 | 14629006 | 985521.6 | 90950 |  | 71248.14 | 37.4333 | SKA | 90.1-2004
Summit Living Learning Center | In Progress | ASU | Watauga | Jerry Marshall | 08-07327-02A | 2010-08-19 | CD | 2010-06-08 | 2012-12-18 | Residence Hall / Office Classrooms | 333 | 128585 | 11 and 3 | Summit Living Learning Center | 90.1-2004 | 6323 | 49.1737 | 3660 | 28.4637 | 42.12% | 2663 | 2015-08-26 | 8724.2834 | 67.8484 | -37.98% |  | -2401.2834 | Summit Living Learning Center | 153208 | 1.1915 | 89024 | 0.69234 | 41.89% | 64184 | 220128.3136 | 1.7119 | -43.68% | -66920.3136 | Summit Living Learning Center | 3388865 | 10176.7718 | 26.3551 | 1928009 | 5789.8168 | 14.994 | 43.11% | 1460856 | 2745167.9999 | 8243.7477 | 21.3491 | 18.99% | Summit Living Learning Center | 40691217 | 316.4538 | 39309739 | 2664558.4 | 94925 |  | 192633.86 | 26.0039 | SKA | 90.1-2004
MARBIONC | In Progress | UNCW | New Hanover | Steve Sharpe | 07-07853-02A | 2010-06-03 | DD | 2011-08-01 | 2013-01-29 | Labs/Offices | NA | 68000 | 2 | MARBIONIC | 90.1-2004 | 31233 | 459.3088 | 19781 | 290.8971 | 36.67% | 11452 | 2015-08-27 | 23198.7913 | 341.1587 | 25.72% | ü | 8034.2087 | MARBIONIC | 425995 | 6.2646 | 301801 | 4.4383 | 29.15% | 124194 | 340591.26 | 5.0087 | 20.05% | 85403.74 | MARBIONIC | 5139169 | NA | 75.576 | 4083469 | NA | 60.051 | 20.54% | 1055700 | No data |  |  |  | MARBIONIC | 24371201 | 358.4 | 19975000 | 2804957 | 110280 |  | 294243 | 38.655 | CRB/AEI | 90.1-2004
NC State Bar HQ | In Progress | DOA | Wake | Joe Cerone <jcerone@ncbar.gov> | 09-07858-01A | 2011-05-31 | CD | 2011-11-28 | 2013-04-25 | Office/Courtroom | NA | 54565 | 4 | NC State Bar HQ | 90.1-2004 | 1689 | 30.9539 | 1116 | 20.4527 | 33.93% | 573 | 2015-08-05 | 3243.7152 | 59.4468 | -92.05% |  | -1554.7152 | NC State Bar HQ | 45238 | 0.82907 | 29457 | 0.53985 | 34.88% | 15781 | 83917.5 | 1.5379 | -85.5% | -38679.5 | NC State Bar HQ | 175310 | NA | 3.2129 | 116629 | NA | 2.1374 | 33.47% | 58681 | 220660 | NA | 4.044 | -25.87% | NC State Bar HQ | 12962700 | 237.5644 | 12687413 | 1125000 | 6000 |  | 56200 | 21.3857 | CJMW | 90.1-2004
Science and Technology Building | In Progress | FSU | Cumberland | Jon Parsons | 06-06971-02A | 2011-01-11 | Final | 2011-06-27 | 2013-05-21 | Office/Classrooms/Labs | NA | 65861 | 4 | Science and Technology Building | 90.1-2004 | 13356 | 202.7907 | 9641 | 146.3841 | 27.82% | 3715 | 2015-08-28 | No Data |  |  |  |  | Science and Technology Building | 151889 | 2.3062 | 100888 | 1.5318 | 33.58% | 51001 | No Data |  |  |  | Science and Technology Building | 2163492 | NA | 32.8494 | 1785946 | NA | 27.1169 | 17.45% | 377546 | No Data |  |  |  | Science and Technology Building | 17028032 | 258.545 | 16327000 | 1576000 | 135000 |  | 290182 | 22.0822 | M&C | 90.1-2004
Student Recreation Facility Addition | In Progress | UNCW | New Hanover | Steve Sharpe | 07-07060-03A | 2010-06-02 | CD | 2011-04-25 | 2013-05-22 | Gym/pool/fitness/courts/lockerrom | NA | 93917 | 2 | Student Recreation Facility Addition | 90.1-2004 | 22917 | 244.0133 | 15931 | 169.6285 | 30.48% | 6986 | 2015-08-27 | 24630.6836 | 262.2601 | -7.478% |  | -1713.6836 | Student Recreation Facility Addition | 351452 | 3.7422 | 248190 | 2.6427 | 29.38% | 103262 | 220426.58 | 2.347 | 37.28% | 131025.42 | Student Recreation Facility Addition | 810220 | NA | 8.627 | 634243 | NA | 6.7532 | 21.72% | 175977 | 1160700 | NA | 12.3588 | -43.26% | Student Recreation Facility Addition | 21478228 | 228.6937 | 20845432 | 2510110 | 215000 |  | 126000 | 9.4303 | SWA | 90.1-2004
Reaves Student Activities Center | Gold | WSSU | Forsyth | Dick Kabis | 06-07181-01A | 2010-10-25 | CD | 2011-05-17 | 2013-06-24 | Gym/Food Service/ | NA | 91513 | 3 | Reaves Student Activities Center | 90.1-2004 | 7587 | 82.9063 | 5004 | 54.6808 | 34.05% | 2583 | 2015-08-28 | 12978.5295 | 141.8217 | -71.06% |  | -5391.5295 | Reaves Student Activities Center | 105529 | 1.1532 | 66125 | 0.72257 | 37.34% | 39404 | 193521.0979 | 2.1147 | -83.38% | -87992.0979 | Reaves Student Activities Center | 1434603 | NA | 15.6765 | 990985 | NA | 10.8289 | 30.92% | 443618 | 625746.88 | NA | 6.8378 | 56.38% | Reaves Student Activities Center | 25393206 | 277.482 | 25315267 | 2408119 | 177240 |  | 287625 | 13.7754 | Sud | 90.1-2004
Creative Arts Building | In Progress | Haywood CC | Haywood | Josh Best rjbest@haywood.edu | 07-07315-03A | 2009-11-02 | DD-2 | 2010-10-28 | 2013-06-30 | Art studios, classrooms, offices | NA | 40722 | 3 | Creative Arts Building | 90.1-2004 | 3603 | 88.478 | 1672 | 41.0589 | 53.59% | 1931 | 2015-08-28 | 1698.6358 | 41.713 | 52.85% |  | 1904.3642 | Creative Arts Building | 65069 | 1.5979 | 19856 | 0.4876 | 69.48% | 45213 | 22920.42 | 0.56285 | 64.78% | 42148.58 | Creative Arts Building | 977508 | NA | 24.0044 | 255213 | NA | 6.2672 | 73.89% | 722295 | 154338 | NA | 3.79 | 84.21% | Creative Arts Building | 8385286 | 205.9154 | 6402774 | 851000 | 50000 |  | 80000 | 46.7236 | Elm | 90.1-2004
Belk Residence Hall | None | UNCC | Mecklenburg | Tony Schallert | 10-08450-02A | 2011-12-22 | CD-2 | 2012-01-17 | 2013-07-09 | Residence Hall | 400 | 164377 | 5 | Belk Residence Hall | 90.1-2004 | 10765 | 65.4897 | 7239 | 44.039 | 32.75% | 3526 | 2015-08-04 | 10981.1785 | 66.8048 | -2.008% |  | -216.1785 | Belk Residence Hall | 149183 | 0.90757 | 97190 | 0.59126 | 34.85% | 51993 | 149629.6389 | 0.91028 | -0.2994% | -446.6389 | Belk Residence Hall | 2719308 | 6798.27 | 16.5431 | 1869230 | 4673.075 | 11.3716 | 31.26% | 850078 | 8471370 | 21178.425 | 51.5362 | -211.5% | Belk Residence Hall | 30027284 | 182.6733 | 30027284 | 2167790 | 126000 |  | 186000 |  |  | 90.1-2004
Cherry Building Renovation | None | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 10-08698-02A | 2011-11-17 | CD | 2012-07-12 | 2013-07-15 | Office/Classroom | NA | 22482 | 2.5 | Cherry Building Renovation | 90.1-2004 | 1449 | 64.4516 | 1017 | 45.2362 | 29.81% | 432 | 2015-08-26 | 1918.2502 | 85.3238 | -32.38% |  | -469.2502 | Cherry Building Renovation | 27666 | 1.2306 | 21821 | 0.9706 | 21.13% | 5845 | 33166.25 | 1.4752 | -19.88% | -5500.25 | Cherry Building Renovation | 166500 | NA | 7.4059 | 120425 | NA | 5.3565 | 27.67% | 46075 | 120550.1733 | NA | 5.3621 | 27.6% | Cherry Building Renovation | 2670270 | 118.7737 | 2645494 | 292501 | 0 |  | 0 |  | SWA | 90.1-2004
Hunt Residence Hall | None | UNCC | Mecklenburg | Tony Schallert | 10-08610-03A | 2012-02-24 | CD | 2012-01-17 | 2013-07-29 | Residence Hall | 436 | 144175 | 5 | Hunt Residence Hall | 90.1-2004 | 11671 | 80.9502 | 6976 | 48.3856 | 40.23% | 4695 | 2015-08-04 | 9709.0475 | 67.3421 | 16.81% |  | 1961.9525 | Hunt Residence Hall | 141674 | 0.98265 | 87499 | 0.60689 | 38.24% | 54175 | 144007.7012 | 0.99884 | -1.647% | -2333.7012 | Hunt Residence Hall | 1100206 | 2523.4083 | 7.631 | 860579 | 1973.805 | 5.969 | 21.78% | 239627 | 2377256.2 | 5452.4225 | 16.4887 | -116.1% | Hunt Residence Hall | 24655367 | 171.01 | 22816693 | 2078598 | 0 |  | 297680 |  | CN | 90.1-2004
Wolf Ridge at Centennial Bldg 6 - Lakeview Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-08-01 | Residence Hall | 151 | 67202 | 6 | Wolf Ridge at Centennial Bldg 6 | 90.1-2004 | 4126 | 61.397 | 2853 | 42.4541 | 30.85% | 1273 | 2015-08-26 | 5261.3204 | 78.2911 | -27.52% |  | -1135.3204 | Wolf Ridge at Centennial Bldg 6 | 76622 | 1.1402 | 51093 | 0.76029 | 33.32% | 25529 | 91337.8791 | 1.3592 | -19.21% | -14715.8791 | Wolf Ridge at Centennial Bldg 6 | 1630661 | 10799.0795 | 24.2651 | 1029702 | 6819.2185 | 15.3225 | 36.85% | 600959 | 571472 | 3784.5828 | 8.5038 | 64.95% | Wolf Ridge at Centennial Bldg 6 | 14207759 | 211.4187 | 11410139.74 | 995826.9923 | 0 |  | 47050.2499 |  | Dewberry | 90.1-2004
Wolf Ridge at Centennial Bldg 1 - Tower Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-08-01 | Residence Hall | 251 | 154726 | 6 | Wolf Ridge at Centennial Bldg 1 - Tower Hall | 90.1-2004 | 12056 | 77.9184 | 8300 | 53.6432 | 31.15% | 3756 | 2015-08-26 | 16548.5064 | 106.9536 | -37.26% |  | -4492.5064 | Wolf Ridge at Centennial Bldg 1 - Tower Hall | 220350 | 1.4241 | 143383 | 0.92669 | 34.93% | 76967 | 300411.6147 | 1.9416 | -36.33% | -80061.6147 | Wolf Ridge at Centennial Bldg 1 - Tower Hall | 5618485 | 22384.4024 | 36.3125 | 4483837 | 17863.8924 | 28.9792 | 20.19% | 1134648 | 1964248 | 7825.6892 | 12.695 | 65.04% | Wolf Ridge at Centennial Bldg 1 | 32712171 | 211.42 | 26270927.62 | 2292793.7742 | 0 |  | 108328.5759 |  | Dewberry | 90.1-2004
Spartan Village 1 - Lee Residence Hall | In Progress | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 243 | 116224 | 5 | Spartan Village 1 - Lee Residence Hall | 90.1-2004 | 5889 | 50.6694 | 4141 | 35.6295 | 29.68% | 1748 | 2015-08-19 | 3553.559 | 30.5751 | 39.66% | ü | 2335.441 | Spartan Village 1 - Lee Residence Hall | 127318 | 1.0955 | 80286 | 0.69079 | 36.94% | 47032 | 78620.69 | 0.67646 | 38.25% | 48697.31 | Spartan Village 1 - Lee Residence Hall | 2900134 | 11934.7078 | 24.953 | 2258696 | 9295.0453 | 19.434 | 22.12% | 641438 | 1941869 | 7991.2305 | 16.708 | 33.04% | Spartan Village 1 - Lee Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Spartan Village 3 - Haywood Residence Hall | In Progress | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 130 | 56295 | 5 | Spartan Village 3 - Haywood Residence Hall | 90.1-2004 | 5889 | 104.6096 | 4141 | 73.5589 | 29.68% | 1748 | 2015-08-19 | 2070.3852 | 36.7774 | 64.84% | ü | 3818.6148 | Spartan Village 3 - Haywood Residence Hall | 127318 | 2.2616 | 80286 | 1.4262 | 36.94% | 47032 | 46912.73 | 0.83334 | 63.15% | 80405.27 | Spartan Village 3 - Haywood Residence Hall | 1736095 | 13354.5769 | 30.8392 | 1384588 | 10650.6769 | 24.5952 | 20.25% | 351507 | 699260 | 5378.9231 | 12.4214 | 59.72% | Spartan Village 3 - Haywood Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Spartan Village 4 - Union Residence Hall | In Progress | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 209 | 89104 | 5 | Spartan Village 4 - Union Residence Hall | 90.1-2004 | 5889 | 66.0913 | 4141 | 46.4738 | 29.68% | 1748 | 2015-08-19 | 2565.0317 | 28.7869 | 56.44% | ü | 3323.9683 | Spartan Village 4 - Union Residence Hall | 127318 | 1.4289 | 80286 | 0.90104 | 36.94% | 47032 | 57265.61 | 0.64268 | 55.02% | 70052.39 | Spartan Village - Building 4 | 2627757 | 12573 | 29.4909 | 2069683 | 9902.7895 | 23.2277 | 21.24% | 558074 | 1202269 | 5752.4833 | 13.4929 | 54.25% | Spartan Village 4 - Union Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Martin-Schexnider Residence Hall | Certified | WSSU | Forsyth | Dick Kabis | 11-09099-02A | 2012-07-18 | CD | No Contract (Privately Funded) | 2013-08-13 | Residence Hall | 227 | 55626 | 5 | Martin-Schexnider Residence Hall | 90.1-2004 | 6193 | 111.3328 | 4672 | 83.9895 | 24.56% | 1521 | 2015-08-28 | 8101.0625 | 145.6345 | -30.81% |  | -1908.0625 | Martin-Schexnider Residence Hall | 87219 | 1.568 | 53012 | 0.95301 | 39.22% | 34207 | 93751.7555 | 1.6854 | -7.49% | -6532.7555 | Martin-Schexnider Residence Hall | 2317437 | 10208.9736 | 41.661 | 1848705 | 8144.0749 | 33.2345 | 20.23% | 468732 | 2293936.48 | 10105.447 | 41.2386 | 1.014% | Martin-Schexnider Residence Hall | 10000000 | 179.772 | 9516280 | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | M&C | 90.1-2004
Union Station | In Progress | Cape Fear CC | New Hanover | Ken Pearce | 07-07399-03A | 2010-05-05 | CD | 2010-11-10 | 2013-08-22 | Office/Classroom/Auditorium | NA | 233900 | 6 | Union Station | 90.1-2004 | 12463 | 53.2835 | 8391 | 35.8743 | 32.67% | 4072 | 2015-08-31 | 28132.1 | 120.274 | -125.7% |  | -15669.1 | Union Station | 407210 | 1.741 | 294497 | 1.2591 | 27.68% | 112713 | 410213.45 | 1.7538 | -0.7376% | -3003.45 | Union Station | 1939781 | NA | 8.2932 | 1222056 | NA | 5.2247 | 37% | 717725 | 2997984 | NA | 12.8174 | -54.55% | Union Station | 38141300 | 163.0667 | 37627193 | 6113085 | 339250 |  | 237711 | 9.6801 | Cheatham | 90.1-2004
Smith-Williams Center | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 08-07305-01F | 2012-03-01 | CD | 2012-05-01 | 2013-08-27 | Gym/Office | NA | 49170 | 2 | Smith-Williams Center | 90.1-2004 | 2396 | 48.7289 | 1518 | 30.8725 | 36.64% | 878 | 2015-08-14 | Incomplete data |  |  |  |  | Smith-Williams Center | 48568 | 0.98776 | 38507 | 0.78314 | 20.72% | 10061 | Incomplete data |  |  |  | Smith-Williams Center | 347984 | NA | 7.0772 | 227682 | NA | 4.6305 | 34.57% | 120302 | Incomplete data |  |  |  | Smith-Williams Center | 13828376 | 281.236 | 12357348 | 736500 |  |  | 128800 |  | Edi | 90.1-2004
Wolf Ridge at Centennial Bldg 2 - Plaza Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-12-05 | Residence Hall | 223 | 84876 | 6 | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 90.1-2004 | 5653 | 66.603 | 3934 | 46.35 | 30.41% | 1719 | 2015-08-26 | 6186.9998 | 72.8946 | -9.446% |  | -533.9998 | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 102040 | 1.2022 | 70049 | 0.82531 | 31.35% | 31991 | 109251.2656 | 1.2872 | -7.067% | -7211.2656 | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 2385879 | 10699.009 | 28.1102 | 1498371 | 6719.1525 | 17.6536 | 37.2% | 887508 | 1422696 | 6379.8027 | 16.7621 | 40.37% | Wolf Ridge at Centennial Bldg 2 - Plaza Hall | 17944484 | 211.42 | 14286216 | 1257727.6242 | 0 |  | 59424.3774 |  | Dewberrry | 90.1-2004
Spartan Village 2 - Highland Residence Hall | In Progress | UNCG | Guilford | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2014-01-09 | Residence Hall | 231 | 110627 | 5 | Spartan Village 2 - Highland Residence Hall | 90.1-2004 | 5889 | 53.2329 | 4141 | 37.4321 | 29.68% | 1748 | 2015-08-19 | 3208.6927 | 29.0046 | 45.51% | ü | 2680.3073 | Spartan Village 2 - Highland Residence Hall | 127318 | 1.1509 | 80286 | 0.72574 | 36.94% | 47032 | 74606.12 | 0.67439 | 41.4% | 52711.88 | Spartan Village 2 - Highland Residence Hall | 2916495 | 12625.5195 | 26.3633 | 2297942 | 9947.8009 | 20.772 | 21.21% | 618553 | 1541790 | 6674.4156 | 13.9368 | 47.14% | Spartan Village 2 - Highland Residence Hall | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
PORTAL | None | UNCC | Mecklenburg | Tony Schallert | 08-07560-03A | 2011-02-03 | CD | 2012-04-09 | 2014-01-28 | Office | NA | 102914 | 4 | PORTAL | 90.1-2004 | 7934 | 77.0935 | 5513 | 53.569 | 30.51% | 2421 | 2015-08-04 | 11226.2716 | 109.084 | -41.5% |  | -3292.2716 | PORTAL | 142246 | 1.3822 | 98494 | 0.95705 | 30.76% | 43752 | 93136.0634 | 0.90499 | 34.52% | 49109.9366 | PORTAL | 776459 | NA | 7.5447 | 565009 | NA | 5.4901 | 27.23% | 211450 | 98967.88 | NA | 0.96166 | 87.25% | PORTAL | 25748184 | 250.1913 | 24736184 | 2215000 | 0 |  | 240424 | 28.6255 | M&C | 90.1-2004
Wolf Ridge at Centennial Bldg 3 - Innovation Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-02-06 | Residence Hall | 219 | 88512 | 6 | Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 90.1-2004 | 5069 | 57.2691 | 3543 | 40.0285 | 30.1% | 1526 | 2015-08-26 | 5491.1639 | 62.0386 | -8.328% |  | -422.1639 | Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 91459 | 1.0333 | 63494 | 0.71735 | 30.58% | 27965 | 96718.1438 | 1.0927 | -5.75% | -5259.1438 | Wolf Ridge at Centennial Bldg 3 | 2343922 | 10702.8402 | 26.4814 | 1472334 | 6722.9863 | 16.6343 | 37.19% | 871588 | 690404 | 3152.5297 | 7.8001 | 70.54% | Wolf Ridge at Centennial Bldg 3 - Innovation Hall | 18713207 | 211.42 |  | 1311607.3739 | none noted |  | 61970.0562 |  | Dewberry | 90.1-2004
Hill Hall Renovation | Gold | WSSU | Forsyth | Dick Kabis | 11-08884-03A | 2012-09-27 | CD | 2012-12-13 | 2014-03-25 | Offices | NA | 37898 | 3 | Hill Hall Renovation - Student Success Center | 90.1-2007 | 2638 | 69.6079 | 1913 | 50.4776 | 27.48% | 725 | 2015-08-28 | 6334.0541 | 167.1343 | -140.1% |  | -3696.0541 | Hill Hall Renovation - Student Success Center | 41267 | 1.0889 | 25579 | 0.67494 | 38.02% | 15688 | 80823.1978 | 2.1327 | -95.85% | -39556.1978 | Hill Hall Renovation - Student Success Center | 2719308 | NA | 71.7533 | 1869230 | NA | 49.3227 | 31.26% | 850078 | 184307.2 | NA | 4.8632 | 93.22% | Hill Hall Renovation - Student Success Center | 10890470 | 287.3627 | 10890470 | 1125000 | 100000 |  | 90000 | 12.1112 | CN | 90.1-2007
Wolf Ridge at Centennial Bldg 5 - Grove Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-04-09 | Residence Hall | 144 | 62645 | 6 | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 90.1-2004 | 3959 | 63.1974 | 2756 | 43.9939 | 30.39% | 1203 | 2015-08-26 | 4198.2811 | 67.017 | -6.044% |  | -239.2811 | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 73439 | 1.1723 | 49084 | 0.78353 | 33.16% | 24355 | 73828.6814 | 1.1785 | -0.5306% | -389.6814 | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 1557237 | 10814.1458 | 24.8581 | 984137 | 6834.2847 | 15.7097 | 36.8% | 573100 | 757724 | 5261.9722 | 12.0955 | 51.34% | Wolf Ridge at Centennial Bldg 5 - Grove Hall | 13244406 | 211.42 |  | 928299.4841 | none noted |  | 43859.7498 |  | Dewberry | 90.1-2004
Wolf Ridge at Centennial Bldg 4 - Valley Hall | Silver | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-05-09 | Residence Hall | 219 | 83460 | 6 | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 90.1-2004 | 5197 | 62.2694 | 3476 | 41.6487 | 33.12% | 1721 | 2015-08-26 | 4461.8307 | 53.4607 | 14.15% |  | 735.1693 | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 96219 | 1.1529 | 61768 | 0.74009 | 35.8% | 34451 | 77046.8744 | 0.92316 | 19.93% | 19172.1256 | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 2343922 | 10702.8402 | 28.0844 | 1472334 | 6722.9863 | 17.6412 | 37.19% | 871588 | 160072 | 730.9224 | 1.9179 | 93.17% | Wolf Ridge at Centennial Bldg 4 - Valley Hall | 17645113 | 211.42 |  | 1236744.7513 | none noted |  | 58432.9909 |  | Dewberry | 90.1-2004
Aviation Center III Building | In Progress | GTCC | Guilford | mjohnson@gtcc.edu | 08-07309-02A | 2012-03-09 | CD | 2012-09-17 | 2014-07-21 | Office/Classroom | NA | 42087 | 4 | Aviation Center III Building | 90.1-2004 | 2425 | 57.6187 | 1699 | 40.3688 | 29.94% | 726 | 2015-08-20 | 2341.9332 | 55.645 | 3.425% |  | 83.0668 | Aviation Center III Building | 68705 | 1.6325 | 55378 | 1.3158 | 19.4% | 13327 | 53289.92 | 1.2662 | 22.44% | 15415.08 | Aviation Center III Building | 1135125 | NA | 26.9709 | 550575 | NA | 13.0818 | 51.5% | 584550 | 51612 | NA | 1.2263 | 95.45% | Aviation Center III Building | 6535600 | 155.2879 |  | 686500 | 20000 |  | 149249 |  | SWA | 90.1-2004
Martin Residence Hall | None | UNCC | Mecklenburg | Tony Schallert | 11-09156-02A | 2012-12-19 | CD | 2013-04-05 | 2014-08-13 | Residence Hall | 408 | 174657 | 6 | Martin Residence Hall | 90.1-2007 | 21396 | 122.503 | 13060 | 74.7751 | 38.96% | 8336 | 2015-08-04 | 10477.9843 | 59.9918 | 51.03% | ü | 10918.0157 | Martin Residence Hall | 306609 | 1.7555 | 210750 | 1.2067 | 31.26% | 95859 | 146344.3765 | 0.8379 | 52.27% | 160264.6235 | Martin Residence Hall | 4970906 | 12183.5931 | 28.461 | 3510140 | 8603.2843 | 20.0973 | 29.39% | 1460766 | 3504533.34 | 8589.5425 | 20.0652 | 29.5% | Martin Residence Hall | 35192772 | 201.4965 | 29686104 | 2733245 | 15000 |  | 175000 | 59.4276 |  | 90.1-2007
14.15 sums | 44 | [9 empty] | 7095 | 5109640 |  | 14.15 sums |  | 509341.1 |  | 340635.8 |  | 33.12% | 168705.3 | [6 empty] | 14.15 sums | 8352140 |  | 5556658 |  | 33.47% | 2795482 |  |  |  |  | 14.15 sums | [7 empty] | 34551885 |  | 52.3513 |  |  | 14.15 sums | 950470110 |  |  | 94282546 | 2929309 |  | 6595180 | 1054277145
New Library Building | None | UNCSA | Forsyth |  | 06-06981-05A | 2012-07-27 | FI | 2013-01-18 | 2014-09-09 | Library/Offices | NA | 73432 | 4 | New Library Building | 90.1-2004 | 6402 | 87.1827 | 4631 | 63.0651 | 27.66% | 1771 | [6 empty] | New Library Building | 90245 | 1.229 | 62106 | 0.84576 | 31.18% | 28139 |  |  |  |  | New Library Building | 706800 | NA | 9.6252 | 478350 | NA | 6.5142 | 32.32% | 228450 |  |  |  |  | New Library Building | 15433000 | 210.1672 | 17328709 | 1833332 | 0 |  | 108825 | -63.502 |  | 90.1-2004
Student Health Center | In Progress | NCA&T | Guilford | barlow@ncat.edu | 08-08109-02A | 2011-12-21 | DD | 2013-04-08 | 2014-10-29 | Offices/Clinics | NA | 27548 | 2 | Student Health Center | 90.1-2004 | 1911 | 69.3698 | 1336 | 48.4972 | 30.09% | 575 | [6 empty] | Student Health Center | 50033 | 1.8162 | 33648 | 1.2214 | 32.75% | 16385 |  |  |  |  | Student Health Center | 154588 | NA | 5.6116 | 101825 | NA | 3.6963 | 34.13% | 52763 |  |  |  |  | Student Health Center | 7444000 | 270.2193 | 7251633 | 785500 | 92000 |  | 51400 | 20.4923 | RMF | 90.1-2004
Campus Police Facility | Silver | UNCG | Guilford | Douglas Cato | 10-08905-03A | 2012-03-29 | CD | 2012-11-01 | 2014-11-12 | Offices | NA | 25877 | 2 | Campus Police Facility | 90.1-2004 | 2330 | 90.0413 | 1242 | 47.9963 | 46.7% | 1088 | [6 empty] | Campus Police Facility | 44281 | 1.7112 | 29471 | 1.1389 | 33.45% | 14810 |  |  |  |  | Campus Police Facility | 617945 | NA | 23.8801 | 478128 | NA | 18.4769 | 22.63% | 139817 |  |  |  |  | Campus Police Facility | 6143700 | 237.4193 |  | 854040 | 43000 |  | 81680 |  | SWA | 90.1-2004
South Village Dining Facility | None | UNCC | Mecklenburg | Tony Schallert | 10-08633-03A | 2013-04-17 | FI | 2012-10-04 | 2014-11-21 | Food Service/Dining | NA | 56146 | 2 | South Village Dining Facility | 90.1-2004 | 12578 | 224.0231 | 7334 | 130.6237 | 41.69% | 5244 | [6 empty] | South Village Dining Facility | 163454 | 2.9112 | 113314 | 2.0182 | 30.68% | 50140 |  |  |  |  | South Village Dining Facility | 546557 | NA | 9.7346 | 435029 | NA | 7.7482 | 20.41% | 111528 |  |  |  |  | South Village Dining Facility | 26618418.39 | 474.0929 | 25649718.39 | 1918410 | 78000 |  | 182024 | 24.5059 | M&C | 90.1-2004
Dining Hall Renovation | None | UNCG | Guilford | Douglas Cato | 08-07382-02A | 2011-04-28 | CD | 2011-06-06 | 2015-02-05 | Food Service/Dining | NA | 111160 | 2 | Dining Hall Renovation | 90.1-2004 | 18584 | 167.1824 | 12522 | 112.6484 | 32.62% | 6062 | [6 empty] | Dining Hall Renovation | 269366 | 2.4232 | 187898 | 1.6903 | 30.24% | 81468 |  |  |  |  | Dining Hall Renovation | 6216053 | NA | 55.9199 | 3532573 | NA | 31.7792 | 43.17% | 2683480 |  |  |  |  | Dining Hall Renovation | 28459035 | 256.0187 |  | 2837884 | 60000 |  | 283540 |  | M&L | 90.1-2004
Center for Design Innovation | In Progress | WSSU | Forsyth | Dick Kabis | 06-06646-03A | 2013-05-03 | FI | 2012-04-12 | 2015-03-03 | Offices, classrooms, labs | NA | 23982 | 3 | Center for Design Innovation | 90.1-2007 | 4288 | 178.8008 | 2361 | 98.4488 | 44.94% | 1927 | [6 empty] | Center for Design Innovation | 106582 | 4.4442 | 65369 | 2.7258 | 38.67% | 41213 |  |  |  |  | Center for Design Innovation | 67775 | NA | 2.8261 | 44733 | NA | 1.8653 | 34% | 23042 |  |  |  |  | Center for Design Innovation | 8727727 | 363.9282 | 6497174 | 700000 | 50000 |  | 80300 | 57.2842 | RMF | 90.1-2007
Jones Student Center - Renovation and Addition | In Progress | FSU | Cumberland | Jon Parsons | 11-09090-03A | 2013-06-28 | FI | 2013-06-10 | 2015-03-06 | Assembly/Dining/Offices | NA | 82961 | 2 | Jones Student Center - Renovation and Addition | 90.1-2007 | 14304 | 172.4184 | 11048 | 133.171 | 22.76% | 3256 | [6 empty] | Jones Student Center - Renovation and Addition | 215110 | 2.5929 | 143121 | 1.7252 | 33.47% | 71989 |  |  |  |  | Jones Student Center - Renovation and Addition | 4017684 | NA | 48.4286 | 3910346 | NA | 47.1348 | 2.672% | 107338 |  |  |  |  | Jones Student Center - Renovation and Addition | 17090447 | 206.0058 | 16915711 | 1536300 | 0 |  | 207560 | 5.3105 | Optima | 90.1-2007
Campus Police Facility | None | UNCSA | Forsyth | boydc@uncsa.edu | 08-07845-03A | 2012-04-05 | CD | 2013-05-30 | 2015-03-12 | Offices | NA | 9023 | 2 | Campus Police Facility | 90.1-2004 | 1171 | 129.7795 | 689 | 76.3604 | 41.16% | 482 | [6 empty] | Campus Police Facility | 18288 | 2.0268 | 12209 | 1.3531 | 33.24% | 6079 |  |  |  |  | Campus Police Facility | 289717 | NA | 32.1087 | 195438 | NA | 21.66 | 32.54% | 94279 |  |  |  |  | Campus Police Facility | 3059704 | 339.1005 |  | 292220 | none noted |  | 68561 |  | SWA | 90.1-2004
Central Storage Facility | None | UNCSA | Forsyth | boydc@uncsa.edu | 08-07844-03A | 2012-05-23 | CD | 2013-05-01 | 2015-03-25 | Warehouse/Storage | NA | 43637 | 2 | Central Storage Facility | 90.1-2007 | 1506 | 34.512 | 754 | 17.2789 | 49.93% | 752 | [6 empty] | Central Storage Facility | 27891 | 0.63916 | 14976 | 0.34319 | 46.31% | 12915 |  |  |  |  | Central Storage Facility | 128138 | NA | 2.9365 | 58898 | NA | 1.3497 | 54.04% | 69240 |  |  |  |  | Central Storage Facility | 5260039 | 120.5408 | 1412707 | 596884 | 0 |  | 65343 |  |  | 90.1-2007
Talley Student Center Renovation and Addition | In Progress | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 08-07847-03A | 2012-02-22 | CD | 2011-02-21 | 2015-05-07 | Offices/Theater/Conference/Food Service/Book Store | NA | 294736 | 5 | Talley Student Center Renovation and Addition | 90.1-2004 | 41725 | 141.5674 | 27808 | 94.3488 | 33.35% | 13917 | [6 empty] | Talley Student Center Renovation and Addition | 940212 | 3.19 | 699461 | 2.3732 | 25.61% | 240751 |  |  |  |  | Talley Student Center Renovation and Addition | 1088442 | NA | 3.6929 | 869385 | NA | 2.9497 | 20.13% | 219057 |  |  |  |  | Talley Student Center Renovation and Addition | 89115690 | 302.3577 |  | 9079497 | 178918 |  | 526000 |  | SWA | 90.1-2004
CE and BLET | None | Nash CC | Nash |  | 09-07972-03A | 2012-11-19 | CD | 2013-11-05 | 2015-06-05 | Offices/Classrooms/Gym/Training | NA | 79295 | 2 | CE and BLET | 90.1-2007 | 5941 | 74.9228 | 4122 | 51.9831 | 30.62% | 1819 | [6 empty] | CE and BLET | 95436 | 1.2036 | 64835 | 0.81764 | 32.06% | 30601 |  |  |  |  | CE and BLET | 2356578 | NA | 29.7191 | 1527392 | NA | 19.2621 | 35.19% | 829186 |  |  |  |  | CE and BLET | 11310270 | 142.6353 |  | 861998 | None Noted |  | 52620 |  | SWA | 90.1-2007
Film School Production Design Facility | None | UNCSA | Forsyth | boydc@uncsa.edu | 08-08115-03A | 2012-03-30 | CD | 2013-04-11 | 2015-06-16 | Various | NA | 29936 | 2 | Film School Production Design Facility | 90.1-2004 | 8887 | 296.8666 | 5860 | 195.7509 | 34.06% | 3027 | [6 empty] | Film School Production Design Facility | 148285 | 4.9534 | 99346 | 3.3186 | 33% | 48939 |  |  |  |  | Film School Production Design Facility | 55005 | NA | 1.8374 | 40257 | NA | 1.3448 | 26.81% | 14748 |  |  |  |  | Film School Production Design Facility | 7820696 | 261.2472 |  | 827850 | none noted |  | 47760 |  |  | 90.1-2004
Holshouser Residence Hall Renovation | None | UNCC | Mecklenburg | Tony Schallert | 12-09461-02A | 2014-03-17 | FD | 2014-02-06 | 2015-07-28 | Residence Hall | 400 | 99713 | 12 | Holshouser Residence Hall Renovation | 90.1-2007 | 12163 | 121.9801 | 9302 | 93.2877 | 23.52% | 2861 | [6 empty] | Holshouser Residence Hall Renovation | 169440 | 1.6993 | 126115 | 1.2648 | 25.57% | 43325 |  |  |  |  | Holshouser Residence Hall Renovation | 3663471 | 9158.6775 | 36.7402 | 2570153 | 6425.3825 | 25.7755 | 29.84% | 1093318 |  |  |  |  | Holshouser Residence Hall Renovation | 15172636 | 152.1631 | 14796933 | 1251550 | 11880 |  | 95000 | 11.1387 | CN | 90.1-2007 | 375703
Phase XIII Residence Hall | None | UNCC | Mecklenburg | Tony Schallert | 12-09496-03A | 2013-10-11 | DD-2 | 2014-01-02 | 2015-07-29 | Residence Hall | 412 | 143986 | 6 | Phase XIII Residence Hall | 90.1-2007 | 7705 | 53.5121 | 5840 | 40.5595 | 24.21% | 1865 | [6 empty] | Phase XIII Residence Hall | 102473 | 0.71169 | 56750 | 0.39414 | 44.62% | 45723 |  |  |  |  | Phase XIII Residence Hall | 4730466 | 11481.7136 | 32.8537 | 2731460 | 6629.7573 | 18.9703 | 42.26% | 1999006 |  |  |  |  | Phase XIII Residence Hall | 28765101 | 199.7771 | 26520850 | 2312090 | 13945 |  | 200000 | 53.7628 | Optima | 90.1-2007
Belk Residence Hall Renovation | In Progress | ASU | Watauga | Jerry Marshall | 10-09113-02A | 2014-02-21 | FD-2 | 2014-05-05 | 2015-07-30 | Residence Hall | 176 | 32839 | 5 | Belk Residence Hall Renovation | 90.1-2007 | 3330 | 101.4038 | 2305 | 70.1909 | 30.78% | 1025 | [6 empty] | Belk Residence Hall Renovation | 87029 | 2.6502 | 60703 | 1.8485 | 30.25% | 26326 |  |  |  |  | Belk Residence Hall Renovation | 1209992 | 6874.9545 | 36.8462 | 755467 | 4292.4261 | 23.0052 | 37.56% | 454525 |  |  |  |  | Belk Residence Hall Renovation | 7222300 | 219.9306 | 6512106 | 806400 | 50600 |  | 125000 | 33.6471 | CN | 90.1-2007
S & BS Building Renovation | None | UNCW | New Hanover | Steve Sharpe | 07-09975-02A | 2014-07-02 | CD | 2014-05-30 | 2015-08-03 | Offices, classrooms, labs | NA | 43554 | 2 | S & BS Building Renovation | 90.1-2010 | 5934.9 | 136.2653 | 5079 | 116.6139 | 14.42% | 855.9 | [6 empty] | S & BS Building Renovation | 110349 | 2.5336 | 91957 | 2.1113 | 16.67% | 18392 |  |  |  |  | S & BS Building Renovation | 1075870 | NA | 24.702 | 760602 | NA | 17.4634 | 29.3% | 315268 |  |  |  |  | S & BS Building Renovation | 9820475 | 225.4781 | 5837018 | 859450 |  | 17250 | 98204.75 | 222.8638 | MCBH | 90.1-2010
Belk Residence Hall | In Progress | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-09246-03A | 2013-10-03 | CD | 2013-05-22 | 2015-08-10 | Residence Hall | 720 | 208077 | 5 | Belk Residence Hall | 90.1-2007 | 22829 | 109.7142 | 15444 | 74.2225 | 32.35% | 7385 | [6 empty] | Belk Residence Hall | 519318 | 2.4958 | 339219 | 1.6303 | 34.68% | 180099 |  |  |  |  | Belk Residence Hall | 11970900 | 16626.25 | 57.5311 | 7250002 | 10069.4472 | 34.8429 | 39.44% | 4720898 |  |  |  |  | Belk Residence Hall | 48137413 | 231.3442 | 41707231 | 3917050 | 91100 |  | 322840 | 38.002 | SWA | 90.1-2007
Oak Residence Hall Renovation | None | UNCC | Mecklenburg | Tony Schallert | 12-09648-03A | 2014-01-06 | CD-2 | 2014-05-19 | 2015-08-24 | Residence Hall | 248 | 52844 | 4 | Oak Residence Hall Renovation | 90.1-2007 | 4104 | 77.6626 | 2776 | 52.532 | 32.36% | 1328 | [6 empty] | Oak Residence Hall Renovation | 78156 | 1.479 | 52863 | 1.0004 | 32.36% | 25293 |  |  |  |  | Oak Residence Hall Renovation | 3786332 | 15267.4677 | 71.6511 | 2951199 | 11899.996 | 55.8474 | 22.06% | 835133 |  |  |  |  | Oak Residence Hall Renovation | 7187260 | 136.009 | 5929373 | 591176 | 0 |  | 77500 | 52.7967 | Peterson | 90.1-2007
Belk Gymnasium Renovation | None | UNCC | Mecklenburg | Tony Schallert | 12-09471-03A | 2013-10-18 | DD | 2014-05-05 | 2015-10-15 | Gym, Pool, Offices | NA | 105000 | 3 | Belk Gymnasium Renovation (Student Recreation Facility) | 90.1-2010 | 5893 | 56.1238 | 5553 | 52.8857 | 5.77% | 340 | [6 empty] | Belk Gymnasium Renovation (Student Recreation Facility) | 96234 | 0.91651 | 84246 | 0.80234 | 12.46% | 11988 |  |  |  |  | Belk Gymnasium Renovation (Student Recreation Facility) | 2939272 | NA | 27.9931 | 1888963 | NA | 17.9901 | 35.73% | 1050309 |  |  |  |  | Belk Gymnasium Renovation (Student Recreation Facility) | 14388687 | 137.0351 | 13744319 | 1224800 | 0 |  | 136650 | 65.15 | M&L | 90.1-2010
Rizzo Conference Center Phase III (Privately Funded) |  | UNC-CH | Orange |  | 11-08953-01A | 2012-09-04 | CD | Privately Funded | 2015-10-01 | Hotel/Classrooms/Conference | 66 | 97014 | 5 | Rizzo Conference Center Phase III (Privately Funded) | 90.1-2004 | 6933 | 71.4639 | 4473 | 46.1067 | 35.48% | 2460 | [6 empty] | Rizzo Conference Center Phase III (Privately Funded) | 14092 | 0.14526 | 10313 | 0.1063 | 26.82% | 3779 |  |  |  |  | Rizzo Conference Center Phase III (Privately Funded) | 2116678 | 32070.8788 | 21.8183 | 1698607 | 25736.4697 | 17.5089 | 19.75% | 418071 |  |  |  |  | Rizzo Conference Center Phase III (Privately Funded) | 25040939 | 258.1168 |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | 90.1-2004
Holding Hall Renovation | In Progress | Wake TCC | Wake |  | 06-06753-02A | 2013-11-18 | CD | 2014-08-19 | 2015-11-03 | Offices/Classrooms | NA | 47729 | 1 | Holding Hall Renovation | 90.1-2007 | 2614 | 54.7675 | 1818 | 38.0901 | 30.45% | 796 | [6 empty] | Holding Hall Renovation | 52390 | 1.0977 | 33542 | 0.70276 | 35.98% | 18848 |  |  |  |  | Holding Hall Renovation | 1075022 | NA | 22.5235 | 817762 | NA | 17.1334 | 23.93% | 257260 |  |  |  |  | Holding Hall Renovation | 3636045 | 76.181 | 3327846 | 449750 | 41200 |  |  | 18.5377 | Dewberry | 90.1-2007
Winkler Residence Hall Renovation Demolished 06/01/14 |  | ASU |  | Jerry Marshall | 10-08894-03A | 2012-09-14 | CD | Demolished 06/01/14 | Demolished 06/01/14 | Residence Hall | 192 | 78450 | 12 | Winkler Residence Hall Renovation Demolished 06/01/14 | 90.1-2004 | 6070 | 77.3741 | 3601 | 45.9018 | 40.68% | 2469 | [6 empty] | Winkler Residence Hall Renovation Demolished 06/01/14 | 143502 | 1.8292 | 87933 | 1.1209 | 38.72% | 55569 |  |  |  |  | Winkler Residence Hall Renovation Demolished 06/01/14 | 2528379 | 13168.6406 | 32.2292 | 1493037 | 7776.2344 | 19.0317 | 40.95% | 1035342 |  |  |  |  | Winkler Residence Hall Renovation Demolished 06/01/14 | 11873469 | 151.3508 |  | 1313285 | 103000 |  | 92600 | 217.1907 |  | 90.1-2004
Bio-tech & Med Sim Center NOT SB 668 |  | Edgecombe CC |  |  | 05-06644-02A | 2014-04-09 | DD | Design Build / NOT SB 668 | Design Build / NOT SB 668 | Office/Classroom/Labs | NA | 44978 | 3 | Bio-tech & Med Sim Center NOT SB 668 | 90.1-2007 | 6871 | 152.7636 | 4929 | 109.5869 | 28.26% | 1942 | [6 empty] | Bio-tech & Med Sim Center NOT SB 668 | 134054 | 2.9804 | 98221 | 2.1838 | 26.73% | 35833 |  |  |  |  | Bio-tech & Med Sim Center NOT SB 668 |  | NA | 0 |  | NA | 0 |  | 0 |  |  |  |  | Bio-tech & Med Sim Center NOT SB 668 | 4825393 | 107.2834 | 4180000 | 932460 | 308832 |  | 28700 | 27.4307 |  | 90.1-2007
Student Recreation Center | In Progress | UNCG | Guilford | Douglas Cato | 09-07928-02A | 2014-03-17 | CD | 2014-03-06 | 2016-07-14 | Gym/Pool | NA | 213000 | 3 | Student Recreation Center | 90.1-2007 | 20211 | 94.8873 | 15288 | 71.7746 | 24.36% | 4923 | [6 empty] | Student Recreation Center | 275822 | 1.2949 | 188166 | 0.88341 | 31.78% | 87656 |  |  |  |  | Student Recreation Center | 2060500 | NA | 9.6737 | 1524900 | NA | 7.1592 | 25.99% | 535600 |  |  |  |  | Student Recreation Center (cost includes CUP?) | 69872746 | 328.0411 | 63588816 | 6427000 | 67200 |  | 344800 | 76.3887 | M&L | 90.1-2007
Phase XIV Residence Hall |  | UNCC | Mecklenburg | Tony Schallert | 12-10117-03A | 2014-10-22 | CD | 2015-03-30 | 2016-07-22 | Residence Hall | 436 | 157219 | 6 | Phase XIV Residence Hall | 90.1-2007 | 8086 | 51.4314 | 6532 | 41.5471 | 19.22% | 1554 | [6 empty] | Phase XIV Residence Hall | 132669 | 0.84385 | 106400 | 0.67676 | 19.8% | 26269 |  |  |  |  | Phase XIV Residence Hall | 3855098 | 8841.9679 | 24.5206 | 2204228 | 5055.5688 | 14.0201 | 42.82% | 1650870 |  |  |  |  | Phase XIV Residence Hall | 38708442 | 246.2072 | 36840000 | 3018220 |  | 27500 | 164340 | 78.4302 | Optima | 90.1-2007
Reynolds Coliseum Renovation | In Progress | NCSU | Wake | Shanna Harwell <smharwel@ncsu.edu> | 12-09912-01B | 2014-11-18 | CD | 2015-06-16 | 2016-10-11 | Basketball Arena, locker rooms, offices | NA | 165584 | 3 | Reynolds Coliseum Renovation | 90.1-2007 | 29857 | 180.3133 | 22062 | 133.2375 | 26.11% | 7795 | [6 empty] | Reynolds Coliseum Renovation | 534913 | 3.2305 | 426967 | 2.5786 | 20.18% | 107946 |  |  |  |  | Reynolds Coliseum Renovation | 330635 | NA | 1.9968 | 247594 | NA | 1.4953 | 25.12% | 83041 |  |  |  |  | Reynolds Coliseum Renovation | 23473863 | 141.7641 | 23473863 | 3170473 | 35000 | 60000 | 58725 | 1.4241 | BNK | 90.1-2007
Western Crime Lab | None | NCDoJ | Henderson |  | 12-09454-02A | 2014-10-31 | CD-2 | 2015-07-30 | 2017-02-08 | Labs/Offices | NA | 35357 | 2 | Western Crime Lab | 90.1-2007 | 7819 | 221.1443 | 5695 | 161.0714 | 27.16% | 2124 | [6 empty] | Western Crime Lab | 205920 | 5.824 | 145347 | 4.1108 | 29.42% | 60573 |  |  |  |  | Western Crime Lab | 142308 | NA | 4.0249 | 97350 | NA | 2.7533 | 31.59% | 44958 |  |  |  |  | Western Crime Lab | 14468100 | 409.2004 | 13630000 | 1440000 |  |  | 120000 | 15.8173 | M&C | 90.1-2007
New Student Center | In Progress | NCA&T | Guilford |  | 03-08608-02A | 2014-05-09 | CD | 2014-02-20 | 2017-10-05 | Offices/Theater/Conference/Food Service/Book Store | NA | 182275 | 4 | New Student Center | 90.1-2007 | 31691 | 173.8637 | 23425 | 128.5146 | 26.08% | 8266 | [6 empty] | New Student Center | 529117 | 2.9029 | 366504 | 2.0107 | 30.73% | 162613 |  |  |  |  | New Student Center | 5763776 | NA | 31.6213 | 4434106 | NA | 24.3265 | 23.07% | 1329670 |  |  |  |  | New Student Center | 71806942 | 393.9484 | 64958142 | 7250000 | 166000 |  | 594000 | 46.7908 | RMF | 90.1-2007
Advanced + Emerging Technologies Center NOT SB 668 |  | CFCC |  | Ken Pearce | 11-08585-02A | 2013-07-19 | DD | 2015-07-07 | 2017-02-27 | Classrooms, labs, offices | NA | 94236 | 2 | Advanced + Emerging Technologies Center NOT SB 668 | 90.1-2007 | 6944 | 73.6873 | 6610 | 70.143 | 4.81% | 334 | [6 empty] | Advanced + Emerging Technologies Center NOT SB 668 | 249013 | 2.6424 | 222050 | 2.3563 | 10.83% | 26963 |  |  |  |  | Advanced + Emerging Technologies Center NOT SB 668 | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. |  |  |  |  | Advanced + Emerging Technologies Center NOT SB 668 | 31280403 | 247.36 | 3432421 | 2079762 | 0 |  | 0 |  |  | 90.1-2007
Heavy Equipment + Transport Technology Center NOT SB 668 |  | CFCC |  | Ken Pearce | 11-08585-02A | 2013-07-19 | DD | 2015-07-07 | 2017-02-27 | Equipment repair, offices, classrooms | NA | 32221 | 2 | Heavy Equipment + Transport Technology Center NOT SB 668 | 90.1-2007 | [12 empty] | Heavy Equipment + Transport Technology Center NOT SB 668 | 28938 | 0.89811 | 22854 | 0.70929 | 21.02% | 6084 |  |  |  |  | Heavy Equipment + Transport Technology Center NOT SB 668 | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. |  |  |  |  | Heavy Equipment + Transport Technology Center NOT SB 668 | included in AET Center bid amount |  | 2041899 | Included w/A+ETC | 0 |  | NOT SB 668 |  |  | 90.1-2007
Science and Office Bldg | In Progress | WSSU | Forsyth | Dick Kabis | 07-07236-01A | 2013-04-01 | CD | Approved to bid 11/04/2013 | No Contract | Classroom/Lab/Offices | NA | 123275 | 6 | Science and Office Bldg | 90.1-2004 | 23068 | 187.1263 | 15903 | 129.0043 | 31.06% | 7165 | [6 empty] | Science and Office Bldg | 425425 | 3.451 | 296267 | 2.4033 | 30.36% | 129158 |  |  |  |  | Science and Office Bldg | 1377837 | NA | 11.1769 | 878485 | NA | 7.1262 | 36.24% | 499352 |  |  |  |  | Science and Office Bldg | 42881459 | 347.852 | 39331912 | 4603210 | 138000 |  | 455967 | 32.081 | AEI | 90.1-2004
Division 2 Equipment Shop |  | DOT |  | Eric Frazier | 12-09859-03A | 2015-06-12 | DD | No Contract | No Contract | Repair garage/storage/offices | NA | 38995 | 1 | Division 2 Equipment Shop | 90.1-2007 | 1434.6 | 36.7893 | 1435 | 36.7996 | -0.02788% | -0.4 | [6 empty] | Division 2 Equipment Shop | 86379 | 2.2151 | 86379 | 2.2151 | 0% | 0 |  |  |  |  | Division 2 Equipment Shop | [12 empty] | Division 2 Equipment Shop | 6459881 | 165.6592 | 6136886.95 | 539733 | 12290 | 8000 | 37090 | #DIV/0! | Dibble and Pledger | 90.1-2007
Elm Residence Hall Renovation |  | UNCC | Mecklenburg | Tony Schallert | 12-09940-03A | 2014-06-23 | DD | No Contract | No Contract | Residence Hall | 95 | 29845 | 3 | Elm Residence Hall Renovation | 90.1-2007 | 2122 | 71.1007 | 1669 | 55.9223 | 21.35% | 453 | [6 empty] | Elm Residence Hall Renovation | 34775 | 1.1652 | 26751 | 0.89633 | 23.07% | 8024 |  |  |  |  | Elm Residence Hall Renovation | 1069151 | 11254.2211 | 35.8235 | 696432 | 7330.8632 | 23.335 | 34.86% | 372719 |  |  |  |  | Elm Residence Hall Renovation | 5366082.96 | 179.7984 | 5158196.28 | 448389 |  | 3312 | 23400 | 29.2371 | Peterson | 90.1-2007
Maple Residence Hall Renovation |  | UNCC | Mecklenburg | Tony Schallert | 12-09940-03A | 2014-06-23 | DD | No Contract | No Contract | Residence Hall | 64 | 23270 | 3 | Maple Residence Hall Renovation | 90.1-2007 | 1704 | 73.2273 | 1196 | 51.3966 | 29.81% | 508 | [6 empty] | Maple Residence Hall Renovation | 28673 | 1.2322 | 19427 | 0.83485 | 32.25% | 9246 |  |  |  |  | Maple Residence Hall Renovation | 710168 | 11096.375 | 30.5186 | 462765 | 7230.7031 | 19.8868 | 34.84% | 247403 |  |  |  |  | Maple Residence Hall Renovation | 4173620.08 | 179.3563 | 4011930.44 | 348747 |  | 2576 | 18200 | 19.7345 | Peterson | 90.1-2007
Pine Residence Hall Renovation |  | UNCC | Mecklenburg | Tony Schallert | 12-09940-03A | 2014-06-23 | DD | No Contract | No Contract | Residence Hall | 95 | 29799 | 3 | Pine Residence Hall Renovation | 90.1-2007 | 2122 | 71.2104 | 1669 | 56.0086 | 21.35% | 453 | [6 empty] | Pine Residence Hall Renovation | 34775 | 1.167 | 26751 | 0.89771 | 23.07% | 8024 |  |  |  |  | Pine Residence Hall Renovation | 1069151 | 11254.2211 | 35.8788 | 696432 | 7330.8632 | 23.371 | 34.86% | 372719 |  |  |  |  | Pine Residence Hall Renovation | 5366082.96 | 180.0759 | 5158196.28 | 448389 |  | 3312 | 23400 | 29.2371 | Peterson | 90.1-2007
New Residence Hall - Freshman Living/Learning |  | WSSU | Forsyth | Dick Kabis | 13-10372-03A | 2014-10-20 | CD | No Contract | No Contract | Residence Hall | 290 | 71021 | 6 | New Residence Hall - Freshman Living/Learning | 90.1-2010 | 3347 | 47.1269 | 3202 | 45.0853 | 4.332% | 145 | [6 empty] | New Residence Hall - Freshman Living/Learning | 54763 | 0.77108 | 50499 | 0.71104 | 7.786% | 4264 |  |  |  |  | New Residence Hall - Freshman Living/Learning | 2798472 | 9649.9034 | 39.4034 | 2000107 | 6896.9207 | 28.1622 | 28.53% | 798365 |  |  |  |  | New Residence Hall - Freshman Living/Learning | 16712500 | 235.3177 | 16000000 | 1735188 | 75000 | 11000 | 176132 | 228.5722 | RMF | 90.1-2010
Brown Building Renovation & Addition | In Progress | WCU |  |  | 13-10964-02A | 2015-06-12 | DD | No Contract | No Contract | Food Service/Dining | NA | 64342 | 3 | Brown Building Renovation & Addition | 90.1-2010 | 9153 | 142.2554 | 8749 | 135.9765 | 4.414% | 404 | [6 empty] | Brown Building Renovation & Addition | 122323 | 1.9011 | 108903 | 1.6926 | 10.97% | 13420 |  |  |  |  | Brown Building Renovation & Addition | 62160 | NA | 0.96609 | 44226 | NA | 0.68736 | 28.85% | 17934 |  |  |  |  | Brown Building Renovation & Addition | 20832572 | 323.7787 | 20139556 | 2504600 | 62800 | 17574 | 139652 | 68.0359 | Optima | 90.1-2010
Workforce Solutions Complex | In Progress | Catawba Valley CC | Catawba |  | 07-07389-02A | 0/09/15 | DD | No Contract | No Contract | Classrooms/Ofices/Lab&Shop/conf training/etc | NA | 80200 | 1 | Workforce Solutions Complex | 90.1-2010 | 6020 | 75.0623 | 5167 | 64.4264 | 14.17% | 853 | [6 empty] | Workforce Solutions Complex | 88975 | 1.1094 | 79804 | 0.99506 | 10.31% | 9171 |  |  |  |  | Workforce Solutions Complex | 935004 | NA | 11.6584 | 509544 | NA | 6.3534 | 45.5% | 425460 |  |  |  |  | Workforce Solutions Complex | 20979000 | 261.5835 | 20407437 | 1928500 | 53000 |  | 45670 | 73.0818 | M&L | 90.1-2004
Allied Health & Workforce (Courtesy review only of DD phase) |  | ABTCC |  |  | 12-09487-01A | 2012-11-13 | DD | No Contract | No Contract | Office/Classroom/Lab/Assembly | NA | 185810 | 6 | Allied Health & Workforce | 90.1-2004 | 10582 | 56.9506 | 3675 | 19.7783 | 65.27% | 6907 | [6 empty] | Allied Health & Workforce | 267259 | 1.4383 | 93214 | 0.50166 | 65.12% | 174045 |  |  |  |  | Allied Health & Workforce | 115375 | NA | 0.62093 | 50944 | NA | 0.27417 | 55.84% | 64431 |  |  |  |  | Allied Health & Workforce | 45400738 | 244.3396 | 42736000 | no contract |  |  |  | 15.3106 |  | 90.1-2004
Building 600 NOT SB 668 |  | RCCC |  |  | 11-08937-02A | 2013-01-25 | DD | No Contract | No Contract | Classroom, offices | NA | 69250 | 2 | Building 600 NOT SB 668 | 90.1-2004 | 4413 | 63.7256 | 2774 | 40.0578 | 37.14% | 1639 | [6 empty] | Building 600 NOT SB 668 | 82649 | 1.1935 | 58907 | 0.85064 | 28.73% | 23742 |  |  |  |  | Building 600 NOT SB 668 | 60744 | NA | 0.87717 | 45643 | NA | 0.6591 | 24.86% | 15101 |  |  |  |  | Building 600 NOT SB 668 | 10191099 | 147.1639 | 8586550 | Included w/ Bldgs 300 and 500. | 0 |  | 0 | 67.5827 |  | 90.1-2004
Health Sciences Campus - Student Services Facility |  | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-10217-02A | 2015-01-19 | CD | No Contract | No Contract | Offices/Gym/ Food Service/ Book Store | NA | 75843 | 4 | Health Sciences Campus - Student Services Facility | 90.1-2010 | 10944 | 144.2981 | 9185 | 121.1054 | 16.07% | 1759 | [6 empty] | Health Sciences Campus - Student Services Facility | 107685 | 1.4198 | 91262 | 1.2033 | 15.25% | 16423 |  |  |  |  | Health Sciences Campus - Student Services Facility | 1899740 | NA | 25.0483 | 1215180 | NA | 16.0223 | 36.03% | 684560 |  |  |  |  | Health Sciences Campus - Student Services Facility | 25507078.25 | 336.3142 | 21220000 | 2903738 | 154488 |  | 300000 | 288.715 | RDK | 90.1-2004
Main Campus - Student Union | In Progress | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-09263-02A | 2015-07-20 | CD | No Contract | No Contract | Offices/Theater/Conference/ Food Service/ Book Store | NA | 213911 | 4 | Main Campus - Student Union | 90.1-2007 | 38581 | 180.3601 | 23447 | 109.611 | 39.23% | 15134 | [6 empty] | Main Campus - Student Union | 629463 | 2.9426 | 393838 | 1.8411 | 37.43% | 235625 |  |  |  |  | Main Campus - Student Union | 1394940 | NA | 6.5211 | 863295 | NA | 4.0358 | 38.11% | 531645 |  |  |  |  | Main Campus - Student Union | 75104396 | 351.1011 | 73104396 | 9640712 | 161300 |  | 707030 | 12.1733 | AEI | 90.1-2007
Mary Ellen Jones Renovation |  | UNC | Orange |  | 11-09861-02A and 11-09861-02C | 2015-02-09 | DD-2 | No Contract | No Contract | Labs/Offices | NA | 221618 | 11 | Mary Ellen Jones Renovation | 90.1-2010 | 27375.8 | 123.527 | 22956.3 | 103.585 | 16.14% | 4419.5 | [6 empty] | Mary Ellen Jones Renovation | 1006324 | 4.5408 | 813664 | 3.6715 | 19.14% | 192660 |  |  |  |  | Mary Ellen Jones Renovation | 663675 | NA | 2.9947 | 445591 | NA | 2.0106 | 32.86% | 218084 |  |  |  |  | Mary Ellen Jones Renovation | 77779202 | 350.9607 | 75208000 | 8628179 |  | 10370 | 730000 | 17.1887 | Newcomb & Boyd | 90.1-2007
Clement Residence Hall Renovation | None | ECU | Pitt | Les Hewlett hewlettl14@ecu.edu | 11-10689-02A | 2015-08-15 | DD | No Contract | No Contract | Residence Hall | 360 | 79783 | 10 | Clement Residence Hall Renovation | 90.1-2010 | 6062 | 75.9811 | 5097 | 63.8858 | 15.92% | 965 | [6 empty] | Clement Residence Hall Renovation | 126562 | 1.5863 | 114895 | 1.4401 | 9.218% | 11667 |  |  |  |  | Clement Residence Hall Renovation | 1606527 | 4462.575 | 20.1362 | 982138 | 2728.1611 | 12.3101 | 38.87% | 624389 |  |  |  |  | Clement Residence Hall Renovation | 15757980.67 | 197.5105 |  | 1750000 |  | 23400 | 78789.9034 |  | EDi | 90.1-2010
Advanced Applied Technology Center | Silver | Alamance CC |  |  | 07-07353-03A | 2015-08-31 | SD | No Contract | No Contract | Shops/Offices | NA | 55028 | 1 | Advanced Applied Technology Center | 90.1-2010 | 3345.491 | 60.7962 | 3310.615 | 60.1624 | 1.042% | 34.876 | [6 empty] | Advanced Applied Technology Center | 80013 | 1.454 | 79195 | 1.4392 | 1.022% | 818 |  |  |  |  | Advanced Applied Technology Center | 588719 | NA | 10.6985 | [9 empty] | Advanced Applied Technology Center | 12593715 | 228.8601 |  | 861500 | 43500 | 0 | 100000 |  | Little | 90.1-2010
Collaborative Science Building |  | UNC | Orange |  | 11-09030-02A | 2013-11-01 | DD | No Contract | No Contract | Labs/Offices | NA | 274810 | 9 | Collaborative Science Building | 90.1-2007 | 15342 | 55.8277 | 11509 | 41.8798 | 24.98% | 3833 | [6 empty] | Collaborative Science Building | 293091 | 1.0665 | 229379 | 0.83468 | 21.74% | 63712 |  |  |  |  | Collaborative Science Building | 1871354 | NA | 6.8096 | 1339798 | NA | 4.8754 | 28.4% | 531556 |  |  |  |  | Collaborative Science Building | 72817169 | 264.9728 | 78341076 | 7995000 | 223000 | 65350 | 500000 | -74.3276 | Atelier Ten | 90.1-2007
Student Housing Phase III |  | UNC | Orange |  | 12-09765-02A | 2015-01-14 | DD | No Contract | Project on Hold | Residence Hall and Offices | 275 | 112886 | 7 | Student Housing Phase III | 90.1-2010 | 9032 | 80.0099 | 7916 | 70.1238 | 12.36% | 1116 | [6 empty] | Student Housing Phase III | 219320 | 1.9428 | 186485 | 1.652 | 14.97% | 32835 |  |  |  |  | Student Housing Phase III | 917871 | 3337.7127 | 8.131 | 584333 | 2124.8473 | 5.1763 | 36.34% | 333538 |  |  |  |  | Student Housing Phase III | 26052469 | 230.7857 | 25799369 | 1961668 | 53300 | 31970 | 250000 | 17.919 | CN | 90.1-2010
Sanford Residence Hall Renovation |  | UNCC | Mecklenburg | Tony Schallert | 12-09978-03A | 2014-07-09 | DD | No Contract | Project on Hold | Residence Hall | 440 | 99436 | 12 | Sanford Residence Hall Renovation | 90.1-2010 | 5384 | 54.1454 | 4674 | 47.0051 | 13.19% | 710 | [6 empty] | Sanford Residence Hall Renovation | 58913 | 0.59247 | 50839 | 0.51127 | 13.7% | 8074 |  |  |  |  | Sanford Residence Hall Renovation | 4280271 | 9727.8886 | 43.0455 | 2887348 | 6562.1545 | 29.0373 | 32.54% | 1392923 |  |  |  |  | Sanford Residence Hall Renovation | 15688400 | 157.7738 | 15615290 | 1287470 |  | 4100 | 100000 | 21.9482 | M&L | 90.1-2010 | 73110
Highway Patrol Training Facility |  | DOA | Wake |  | 10-08389-02A | 2012-06-28 | CD | Project on Hold | Project on Hold | Office/Classroom/Training | NA | 34386 | 2 | Highway Patrol Training Facility | 90.1-2004 | 2484 | 72.2387 | 1436 | 41.7612 | 42.19% | 1048 | [6 empty] | Highway Patrol Training Facility | 59882 | 1.7415 | 41042 | 1.1936 | 31.46% | 18840 |  |  |  |  | Highway Patrol Training Facility | 667359 | NA | 19.4079 | 310095 | NA | 9.0181 | 53.53% | 357264 |  |  |  |  | Highway Patrol Training Facility | 6245727 |  | 5604454 | is for multiple buildings | is for multiple buildings |  | 84000 |  |  | 90.1-2004
Basic Skills Building |  | Robeson CC | Robeson |  | 07-07572-01A | 2010-12-22 | AP/SD | Project on Hold | Project on Hold | Office/Classroom | NA | 34271 | 2 | Basic Skills Building | 90.1-2004 | 2178 | 63.5523 | 1492 | 43.5354 | 31.5% | 686 | [6 empty] | Basic Skills Building | 51338 | 1.498 | 36026 | 1.0512 | 29.83% | 15312 |  |  |  |  | Basic Skills Building |  | NA | 0 |  | NA | 0 |  | 0 |  |  |  |  | Basic Skills Building | [9 empty] | 90.1-2004
School of Aviation |  | ECSU | Pasquotank | Elizabeth Linney | 07-07166-02A | 2011-01-24 | CD | Project on Hold | Project on Hold | Office/Classroom/Hangar | NA | 44000 | 1 | School of Aviation | 90.1-2004 | 1913 | 43.4773 | 1115 | 25.3409 | 41.71% | 798 | [6 empty] | School of Aviation | 118819 | 2.7004 | 67443 | 1.5328 | 43.24% | 51376 |  |  |  |  | School of Aviation | 179563 | NA | 4.081 | 121788 | NA | 2.7679 | 32.18% | 57775 |  |  |  |  | School of Aviation | [9 empty] | 90.1-2004
Multipurpose Bldg |  | South Piedmont CC |  |  | 07-07352-03A | 2010-07-23 | CD | Approved to bid 05/15/2011 | Project on Hold | Office/Classroom/Labs | NA | 75000 | 3 | Multipurpose Bldg | 90.1-2004 | 5827 | 77.6933 | 3550 | 47.3333 | 39.08% | 2277 | [6 empty] | Multipurpose Bldg | 135642 | 1.8086 | 87360 | 1.1648 | 35.6% | 48282 |  |  |  |  | Multipurpose Bldg | 587500 | NA | 7.8333 | 398125 | NA | 5.3083 | 32.23% | 189375 |  |  |  |  | Multipurpose Bldg | [9 empty] | 90.1-2004
Locomotive and Railcar Maint. Facility |  | DOT | Mecklenburg |  | 10-08634-03A | 2011-10-20 | SD | Project on Hold | Project on Hold | Offices & Railcar | NA | 68400 | 1 | Locomotive and Railcar Maint. Facility | 90.1-2004 | 23291 | 340.5117 | 8015 | 117.1784 | 65.59% | 15276 | [6 empty] | Locomotive and Railcar Maint. Facility | 210152 | 3.0724 | 107570 | 1.5727 | 48.81% | 102582 |  |  |  |  | Locomotive and Railcar Maint. Facility | [12 empty] | Locomotive and Railcar Maint. Facility | [9 empty] | 90.1-2004
Discovery Center Project - Reynolds East |  | NCSSM | Durham |  | 07-07313-04A | 2010-05-10 | CD | Final Not Approved 05/23/2011 | Project on Hold | Residence Hall / Classroom | 31 | 26000 | 4 | Discovery Center Project - Reynolds East | 90.1-2004 | 1846 | 71 | 1121 | 43.1154 | 39.27% | 725 | [6 empty] | Discovery Center Project - Reynolds East | 30466 | 1.1718 | 19282 | 0.74162 | 36.71% | 11184 |  |  |  |  | Discovery Center Project - Reynolds East | 475929 | 15352.5484 | 18.305 | 337075 | 10873.3871 | 12.9644 | 29.18% | 138854 |  |  |  |  | Discovery Center Project - Reynolds East | [9 empty] | 90.1-2004
0
Note on BD4: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on AO5: Leonard Thagard: limited kitchen use and limited bathroom use. Number is extremely low.
Note on AR5: Leonard Thagard: limited kitchen and bathroom use. Number is low.
Note on BD5: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on R6: Leonard Thagard: highest residence hall baseline EUI to date.
Note on T6: Leonard Thagard: highest proposed EUI for residence halls.
Note on BD6: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on AA7: Leonard Thagard: five months of steam consumption is not included.
Note on AJ7: Leonard Thagard: Does not include steam cost.
Note on BD7: Leonard Thagard: Calculated from original amount construction contract less increase noted in LCCA for envelope, plumb, chillers and lights.
Note on AA8: Leonard Thagard: five months of steam consumption is not included.
Note on BD8: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on BF8: Leonard Thagard: SB 668 at $99800 and LEED at $73700
Note on AW10: Leonard Thagard: Water meter shared with another building.
Note on BD10: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on M11: Leonard Thagard: size is for addition only
Note on Q11: Leonard Thagard: energy use is for addition only
Note on BD11: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on BB13: Leonard Thagard: Includes RUP?
Note on BD13: Leonard Thagard: Does not include RUP?
Note on BF13: Leonard Thagard: LEED fees of 180,000 plus design amend #1 for SB 668 for 41,084
Note on L17: Leonard Thagard: One model performed and applied to seven bldgs
Note on M17: Leonard Thagard: One model performed and applied to seven bldgs.
Note on Q17: Leonard Thagard: One model performed and applied to seven bldgs
Note on AL17: Leonard Thagard: Chilled water cost not included.
Note on BB17: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BE17: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BF17: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BH17: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L18: Leonard Thagard: One model performed and applied to seven bldgs
Note on M18: Leonard Thagard: One model performed and applied to seven bldgs.
Note on Q18: Leonard Thagard: One model performed and applied to seven bldgs
Note on BB18: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BE18: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BF18: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BH18: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L19: Leonard Thagard: One model performed and applied to seven bldgs
Note on M19: Leonard Thagard: One model performed and applied to seven bldgs.
Note on Q19: Leonard Thagard: One model performed and applied to seven bldgs
Note on BB19: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BE19: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BF19: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BH19: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L20: Leonard Thagard: One model performed and applied to seven bldgs
Note on M20: Leonard Thagard: One model performed and applied to seven bldgs.
Note on Q20: Leonard Thagard: One model performed and applied to seven bldgs
Note on BB20: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BE20: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BF20: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BH20: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L21: Leonard Thagard: One model performed and applied to seven bldgs
Note on M21: Leonard Thagard: One model performed and applied to seven bldgs.
Note on Q21: Leonard Thagard: One model performed and applied to seven bldgs
Note on BB21: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BE21: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BF21: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BH21: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L22: Leonard Thagard: One model performed and applied to seven bldgs
Note on M22: Leonard Thagard: One model performed and applied to seven bldgs.
Note on Q22: Leonard Thagard: One model performed and applied to seven bldgs
Note on BB22: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BE22: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BF22: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BH22: Leonard Thagard: Cx fee divided by 7 buildings.
Note on L23: Leonard Thagard: One model performed and applied to seven bldgs
Note on M23: Leonard Thagard: One model performed and applied to seven bldgs.
Note on Q23: Leonard Thagard: One model performed and applied to seven bldgs
Note on BB23: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BE23: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BF23: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BH23: Leonard Thagard: Cx fee divided by 7 buildings.
Note on BF26: Leonard Thagard: LEED services added as design amendment. Add to OTDF.
Note on BE28: Leonard Thagard: Combined design fee for original building design and revised building design.
Note on BF29: Leonard Thagard: SB 668 at 17520 and LEED at 139300
Note on BB33: Leonard Thagard: CMR bid packages, NCSU utility assessment, parking deck assessment, etc. make bid amount difficult to accurately calculate.
Note on BB35: Leonard Thagard: Amount is for entire football complex.
Note on BC35: Leonard Thagard: Error in calculation due to entire football complex in one bid package. Building was not broken out.
Note on BE35: Leonard Thagard: Fee includes design for complete football stadium complex.
Note on BB37: Leonard Thagard: Best guess from multiple bid packages. Will revisit later.
Note on BE37: Leonard Thagard: 27% of full design fee
Note on BB38: Leonard Thagard: 73 percent of bid package total for Plemmons and Summitt
Note on BE38: Leonard Thagard: 73 percent of full design fee.
Note on R39: Leonard Thagard: Baseline is high.
Note on T39: Leonard Thagard: Proposed is high.
Note on BD39: Leonard Thagard: Note in LCCA report: "*Initial Cost estimated to be 85% of Construction Budget."
Note on J40: Leonard Thagard: BO
Note on X43: Leonard Thagard: Metered on square footage basis.
Note on AJ43: Leonard Thagard: Metered on square footage basis for thermal utilities or steam and chilled water.
Note on X44: Leonard Thagard: 9 months of data from BAS.
Note on AJ44: Leonard Thagard: Calculated from 9 months of BAS meter data.
Note on BD44: Leonard Thagard: deduct for wall, roof, glaze, bid alt 3, plumb, daylighting, bid alt 1
Note on BB45: Leonard Thagard: Early site package plus building package.
Note on BD45: Leonard Thagard: Clark Nexsen analysis indicated baseline building cost more to build than the proposed building. Analysis not used here.
Note on BB47: Leonard Thagard: Early site plus site and building bid packages.
Note on B48: Leonard Thagard: Can not verify LEED status.
Note on B49: Leonard Thagard: Can not verify LEED status.
Note on J53: Leonard Thagard: Best guess.
Note on X53: Leonard Thagard: Thermal utiities are metered on a square foot basis not on usage.
Note on BB53: Leonard Thagard: Designer's LCCA estimate.
Note on BD53: Leonard Thagard: Designer's LCCA estimate.
Note on J54: Leonard Thagard: BO per Jerry Rogers' handwritten notes in file.
Note on BD54: Leonard Thagard: LCCA cost estimate for proposed building was $46,642,869 while baseline was $46,128,762 for a difference of 514,107 which was deducted from the bid amount to arrive at the baseline building estimate.
Note on BF54: Leonard Thagard: LEED certification 110000 and article 15-1 fee 229250
Note on BD58: Leonard Thagard: baseline calculated from bid amount less delta of $1,012,000 between proposed and baseline estimates by designer.
Note on B59: Leonard Thagard: Can not verify LEED status.
Note on BB60: Leonard Thagard: Early site plus building package.
Note on B61: Leonard Thagard: Can not verify LEED status.
Note on B62: Leonard Thagard: Can not verify LEED status.
Note on BD63: Leonard Thagard: baseline and proposed building cost estimates exceeded the bid amount. Costs to implement energy legislation are negative.
Note on BF64: Leonard Thagard: Green Globes.
Note on BB69: Leonard Thagard: CMR bid packages and CO's through CO#10.
Note on BD69: Leonard Thagard: CD estimates for baseline and proposed buildings exceed CMR bids through CO #10. Baseline estimate is CMR contract amount through CO #10 less designer's delta between baseline and proposed buildings.
Note on AU72: Leonard Thagard: includes kitchen load and cooling tower make up at 3,600,000 gall/yr.
Note on BB75: Leonard Thagard: Captures most but not all bid packages.
Note on BE75: Leonard Thagard: includes swing space, promotion support, bridge over RR tracks, etc.
Note on U79: Leonard Thagard: 27% improvement without plug and process loads.
Note on BF79: Leonard Thagard: Green Globes
Note on M81: Leonard Thagard: GSF does not include tempered un-occupied attic space of ~22,000 SF.
Note on BB81: Leonard Thagard: Designer's proposed building estimate is $5,957,771. Early demo is not included. Contract may include CUP and distribution piping. Ear
Note on BD81: Leonard Thagard: does not include early demo, CEP, CEP distribution, etc.
Note on BH81: Leonard Thagard: LTs guess
Note on M82: Leonard Thagard: Listed now as two buildings East at 102,127 GSF and West at 105,950 GSF.
Note on AP83: Leonard Thagard: Includes cooling tower make up and large laundry load.
Note on M84: Leonard Thagard: 131,341 includes pool deck and pool lobby in GSF. M&L estimate at 105,000 GSF.
Note on Q84: Leonard Thagard: Includes plug and process loads. Pool equipment and HVAC are considered process loads.
Note on U84: Leonard Thagard: 6% less energy than A90.1-2010.
Note on BI84: Leonard Thagard: Not correct since base is A90.1-2010 instead of A90.1-2004. Also window and roof replacement not analyzed based on LCCA.
Note on I85: Leonard Thagard: Private funding. No state contract.
Note on J85: Leonard Thagard: Interscope indicates 74% complete as of 2/27/15. Web search indicates Fall 2015. Will use 10/01/15 for now.
Note on BB88: Leonard Thagard: SB 668 bldg estimate from PDC. BCC DB GMP is $9,751,745
Note on BD88: Leonard Thagard: Proposed bldg estimate from PDC. BCC DB GMP is $9,751,745
Note on BF88: Leonard Thagard: PDC estimate from HB 628 study.
Note on BH88: Leonard Thagard: PDC estimate for Cx.
Note on M89: Leonard Thagard: GSF includes alternates for additional space and per email from Rebecca dated 12.19.13.
Note on Q89: Leonard Thagard: Includes process loads.
Note on S89: Leonard Thagard: Inlcudes process loads.
Note on U90: Leonard Thagard: 25% improvement w/o plug load
Note on AC90: Leonard Thagard: energy dollars include plug and process loads
Note on BD90: Leonard Thagard: baseline estimate from energy model report. Proposed estimate si $36,334,998 compared to CM estimate of
Note on N91: Leonard Thagard: base=57,963 1st=70,579 mez=37,042 Need to verify GSF.
Note on BH92: Leonard Thagard: Current contract is for $22,000. $120,000 is commissioning reserve.
Note on Q93: Leonard Thagard: Includes process load
Note on S93: Leonard Thagard: Includes process load.
Note on U93: Leonard Thagard: Savings are 46% with process load removed.
Note on AD93: Leonard Thagard: Includes process load.
Note on AF93: Leonard Thagard: Includes process load.
Note on AO93: Leonard Thagard: Includes cooling tower consumption.
Note on AR93: Leonard Thagard: Includes cooling tower consumption that is reduced due to smaller cooling load.
Note on BD93: Leonard Thagard: Baseline whole building estimate from LCCA.
Note on BE93: Leonard Thagard: Includes fee for swing space and others.
Note on M94: Leonard Thagard: Base bid GSF. Alt Bid adds 4019 GSF.
Note on Q94: Leonard Thagard: No updates for the DD submission.
Note on S94: Leonard Thagard: No updates for the DD submission.
Note on Q95: Leonard Thagard: No data provided with SD or DD submission.
Note on S95: Leonard Thagard: No data provided with SD or DD submission.
Note on BE96: Leonard Thagard: complicated fee structure due to multiple increases in scope and square footage of project.
Note on BF96: Leonard Thagard: complex due to multiple increases in scope and square footage
Note on BD97: Leonard Thagard: assume 95% of proposed building construction estimate
Note on M102: Leonard Thagard: Building Area including overhang.
Note on BD102: Leonard Thagard: Proposed building reconciled CRM cost estimate less delta for base buillding from LCCA.
Note on A104: Leonard Thagard: Courtsey review only of energy model and LCCA per Greg Driver & Joe Bace discussion (SCO Director & AB Tech Fac/Oper Director)
Note on T104: Leonard Thagard: second lowest proposed EUI, second only to a warehouse/storage facility.
Note on U104: Leonard Thagard: Highest percentage savings to date.
Note on BB107: Leonard Thagard: Includes all site costs of $11,588,331.
Note on BD107: Leonard Thagard: Delta between proposed and baseline is $2,000,000 per AEI LCCA.
Note on Q108: Leonard Thagard: Plug and process has not been included.
Note on S108: Leonard Thagard: Plug and process has not been included.
Note on AE108: Leonard Thagard: Highest $/GSF to date.
Note on AG108: Leonard Thagard: Highest $/GSF to date.
Note on BH108: Leonard Thagard: $730,000 Cx reserve. Current Cx contract is $36,940.
Note on BF109: Leonard Thagard: Not LEED per meeting minutes 04.09.14.
Note on BH109: Leonard Thagard: estimate of 0.5% of construction cost until Cx contract is complete.
Note on BF110: Leonard Thagard: LEED certification design & documentation for $35,000. LEED Registration for $8,500.
Note on BH110: Leonard Thagard: Cx reserve
Note on BH111: Leonard Thagard: Cx reserve. Design only Cx is for $44,680.
Note on BD112: Leonard Thagard: from page 89 of the energy model lcca report.
Note on BE112: Leonard Thagard: contract not signed as of 09.02.14
Note on BF112: Leonard Thagard: from design contract: $43,200 for model and $10,100 for LEED
Note on BH112: Leonard Thagard: Cx reserve of $250,000
Note on Q113: Leonard Thagard: Includes plug and process

## 14.15 Meter Data
2014/2015 Meter Data Summary
1 | ASU - Cone Residence Hall Renovation | [16 empty] | ASU - Cone Residence Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 906743.12 | kwhs | 3094.7143 | MMbtu
| Steam (lbs) | [16 empty] | 1882789.4 | lbs | 1882.7894 | MMbtu | 4977.5037 | MMbtu
| Water (gallons) | [16 empty] | 1690223 | gallons | 1690223 | gallons
| Electricity Cost ($) | [16 empty] | 79884.2058 |  | 79884.2058
| Steam Costs ($) | [16 empty] | 39542.64 |  | 39542.64
119426.8458
2 | UNCC - Prospector Hall Renovation Phase II | [16 empty] | UNCC - Prospector Hall Renovation Phase II
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 58248 | 73841 | 64140 | 48489 | 74632 | 62878 | 23850 | 52081 | 57328 | 60797 | 63751 | 47783 |  |  |  | 687818 | kwhs | 2347.5228 | MMbtu
| Nat Gas (Therms) |  | 1544 | 1757 | 2603 | 2191 | 3206 | 2740 | 3855 | 4075 | 3194 | 2249 | 1506 | 1021 |  |  |  | 29941 | therms | 2993.3851 | MMbtu
| Chilled Water (MMBtu) | [6 empty] | 0 | 0 | 42 | 120 | 489 | 688 | 860 |  |  |  | 2199 | MMbtu | 2199 | MMBbtu | 7539.908 | MMbtu
| Water Usage (CF) |  | 11520 | 14330 | 19980 | 19980 | 14640 | 6652 | 13970 | 10420 | 12020 | 13120 | 7020 | 6172 |  |  |  | 149824 | CF | 1120683.52 | gallons
| Electricity Cost ($) |  | 4058.8745 | 5285.4111 | 4441.4562 | 2974.7086 | 4292.4906 | 3620.5883 | 1330.1396 | 2935.9063 | 3353.0621 | 3392.9642 | 3583.1817 | 2999.0629 |  |  |  | 42267.8459 |  | 42267.8459
| Nat Gas Costs ($) |  | 1340.56 | 1522.46 | 2244.94 | 1893.09 | 2743.17 | 2319.95 | 3115.79 | 3040.89 | 2037.24 | 0 | 683.8 | 703.85 |  |  |  | 21645.74 |  | 21645.74
| Chilled Water ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252.9689 | 721.5973 | 2609.416 | 2878.4579 | 4181.2329 |  |  |  | 10643.673 |  | 10643.673
74557.2589
3 | UNCC - Miltimore Residence Hall | [16 empty] | UNCC - Miltimore Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 180200 | 207501 | 167465 | 164770 | 135799 | 119754 | 138887 | 118400 | 123371 | 153382 | 149826 | 158234 |  |  |  | 1817589 | kwhs | 6203.4313 | MMbtu
| Nat Gas (Therms) |  | 3393 | 3385 | 3936 | 2828 | 5568 | 6248 | 8297 | 6995 | 5056 | 3796 | 3010 | 2465 |  |  |  | 54977 | therms | 5496.3874 | MMbtu | 11699.8187 | MMbtu
| Water Usage (CF) |  | 59844 | 55320 | 72656 | 53662 | 45363 | 25194 | 49194 | 68476 | 52813 | 63623 | 42380 | 46370 |  |  |  | 634895 | CF | 4749014.6 | gallons
| Electricity Cost ($) |  | 12556.812 | 14852.5627 | 11596.3278 | 10108.3284 | 7810.5361 | 6895.5744 | 7745.874 | 6674.436 | 7215.8565 | 8559.9557 | 8421.1037 | 9931.4343 |  |  |  | 112368.8016 |  | 112368.8016
| Nat Gas Costs ($) |  | 2919.59 | 2912.76 | 3383.3 | 2522.48 | 4747.98 | 5331.75 | 6680.67 | 5204.12 | 3212.06 | 0 | 1127.55 | 1668.19 |  |  |  | 39710.45 |  | 39710.45
152079.2516
4 | NCCU - Nursing Building | [16 empty] | NCCU - Nursing Building
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 101656 | 83961 | 61140 | 51127 | 58131 | 51184 | 66259 | 77568 | 74983 | 71978 | 85948 | 66815 |  | 850750 | kwhs | 2903.6098 | MMbtu
| Steam (lbs) | Partial Data | [7 empty] | 434277 | 646511 | 375662 | 311334 | 186544 | 176351 | 180505 |  | 2311184 | lbs | 2311.184 | MMbtu
| Natural Gas (Therms) |  |  |  | 42 | 46 | 43 | 47 | 27 | 45 | 49 | 48 | 44 | 44 | 42 | 36 |  | 513 | therms | 51.2878 | MMbtu | 5266.0815 | MMbtu
| Water (CF) |  |  |  | 15613 | 8642 | 2880 | 795 | 1141 | 1906 | 4043 | 8228 | 8130 | 13138 | 12157 |  |  | 76673 | CF | 573514.04 | gallons
| Electricity Cost ($) |  |  |  | 6269.63 | 5178.29 | 3770.81 | 3153.26 | 3585.23 | 3156.77 | 4086.52 | 4784.01 | 4624.58 | 4439.24 | 5300 | 4120 |  | 52468.34 |  | 52468.34
| Steam Costs ($) | No Data | [15 empty] | 0 |  | 0
| Natural Gas ( $) |  |  |  | 57.66 | 61.33 | 57.88 | 57.04 | 40.73 | 55.28 | 56.06 | 55.3 | 52.39 | 52.39 | 50.84 | 46.19 |  | 643.09 |  | 643.09
53111.43
5 | NCCU - Chidley Residence Hall | [16 empty] | NCCU - Chidley Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 240288 | 181085 | 109864 | 71448 | 98048 | 80600 | 95216 | 127066 | 71760 | 85624 | 106024 | 82840 |  | 1349863 | kwhs | 4607.0824 | MMbtu
| Steam (lbs) | No Data | [15 empty] | 0 | lbs | 0 | MMbtu
| Natural Gas (Therms) |  |  |  | 576 | 0 | 0 | 776 | 242 | 1458 | 1904 | 1379 | 1405 | 275 | 299 | 299 |  | 8613 | therms | 861.0944 | MMbtu | 5468.1768 | Mmbtu
| Water (CF) |  |  |  | 128629 | 64361 | 57810 | 34713 | 130637 | 44559 | 62488 | 58412 | 21227 | 120430 | 127683 |  |  | 850949 | CF | 6365098.52 | gallons
| Electricity Cost ($) |  |  |  | 14819.76 | 11168.42 | 6775.15 | 4406.56 | 6047.11 | 4971.01 | 5872.45 | 7836.8 | 4425.8 | 5280.86 | 6539.03 | 5109.16 |  | 83252.11 |  | 83252.11
| Steam Costs ($) | No Data | [15 empty] | 0 |  | 0
| Natural Gas ( $) |  |  |  | 547.85 | 18.73 | 18.73 | 639.22 | 216.03 | 1153.16 | 1399.56 | 1012.81 | 1035.19 | 229.12 | 247.28 | 246.83 |  | 6764.51 |  | 6764.51
90016.62
6 | UNC-CH - Loudermilk | [16 empty] | UNC-CH - Loudermilk
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 145460 | 148965 | 204667 | 174103 | 172559 | 153194 | 141867 | 174836 | 164868 | 156341 | 135067 | 174677 |  |  | 1946604 | kwhs | 6643.7595 | MMbtu
| Steam Usage (mlbs) |  |  | 734 | 629 | 594 | 485 | 540 | 730 | 769 | 943 | 454 | 437 | 484 | 525 |  |  | 7324 | mlbs | 8744.856 | MMbtu
| Chilled water (ton-hrs) |  |  | 166476 | 172661 | 142526 | 56574 | 11017 | 1310 | 1023 | 16 | 7543 | 34751 | 92308 | 151339 |  |  | 837544 | ton-hrs | 10050.528 | MMbtu
| Natural Gas (therms) |  |  | 130 | 247 | 474 | 428 | 332 | 405 | 161 | 384 | 325 | 398 | 339 | 187 |  |  | 3810 | therms | 380.909 | MMbtu | 25820.0525 | Mmbtu
| Water Usage (kgallons) |  |  | 132 | 183 | 184 | 133 | 97 | 29 | 82 | 67 | 102 | 122 | 309 | 431 |  |  | 1871 | kgallons | 1871000 | gallons
| Electricity Cost ($) |  |  | 9833.1 | 10025.34 | 11911.62 | 10132.79 | 8610.69 | 8839.29 | 9334.85 | 8741.8 | 9562.34 | 9130.31 | 8104.02 | 9554.83 |  |  | 113780.98 |  | 113780.98
| Steam Cost ($) |  |  | 8245.83 | 7066.25 | 6673.06 | 5448.54 | 6066.41 | 8200.89 | 8639.02 | 10593.76 | 5100.28 | 4909.3 | 5437.3 | 5897.9 |  |  | 82278.54 |  | 82278.54
| Chilled Water ($) |  |  | 15482.27 | 16057.47 | 13254.92 | 5261.38 | 1024.58 | 121.83 | 95.14 | 1.49 | 701.5 | 3231.84 | 8584.64 | 14543.68 |  |  | 78360.74 |  | 78360.74
| Natural Gas ($) |  |  | 112.64 | 214.02 | 410.71 | 326.06 | 252.92 | 308.89 | 114.67 | 273.09 | 232.38 | 284.57 | 221.94 | 122.04 |  |  | 2873.93 |  | 2873.93
274420.26
7 | DoAg&CS - Davis Event Center | [16 empty] | DoAg&CS - Davis Arena
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 20500 | 56120 | 47040 | 67800 | 53240 | 29280 | 33400 | 33000 | 49720 | 32800 | 32200 | 38120 |  |  |  | 493220 | kwhs | 1683.3599 | MMbtu
| Nat Gas (Therms) |  | 166 | 114 | 96 | 302 | 1418 | 2056 | 2162 | 4388 | 6471 | 1096 | 455 | 157 |  |  |  | 18881 | therms | 1887.6492 | MMbtu | 3571.0091 | Mmbtu
| Water Usage (gallons) |  | 19448 | 77792 | 70312 | 72556 | 55352 | 23188 | 276760 | 58344 | 74800 | 103972 | 61336 | 19448 |  |  |  | 913308 | gallons | 913308 | gallons
| Electricity Cost ($) |  | 3902.46 | 5467.49 | 4715.73 | 6518.57 | 5215.84 | 3423.54 | 3835 | 3806.76 | 5078.95 | 3791.55 | 3745.89 | 4210.33 |  |  |  | 53712.11 |  | 53712.11
| Nat Gas Costs ($) |  | 172.77 | 124.42 | 107.73 | 298.43 | 1144.35 | 1520.27 | 1596.99 | 3182.58 | 4314.88 | 761.75 | 342.83 | 129.76 |  |  |  | 13696.76 |  | 13696.76
67408.87
8 | NCSU - Student Health Center Addition and Renovation | [16 empty] | NCSU - Student Health Center Addition and Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electric (kWh) |  |  | 74291.6667 | 65168.6 | 69007.9963 | 66408.9966 | 61874.0082 | 66953.0029 | 64019.9961 | 70717 | 67461 | 68776 | 65683 | 66473 |  |  | 806834.2668 | kwhs | 2753.7254 | MMbtu
| Chilled Water (Dtherms) |  |  | 937.0703 | 689.78 | 315.52 | 181.24 | 92.17 | 124.6 | 125.84 | 259.69 | 409.01 | 656.94 | 953.24 | 1018.01 |  |  | 5763.1103 | dthrms | 5763.1103 | MMbtu
| Steam (1,000 lbs) |  |  | 192 | 261 | 343 | 574 | 591 | 733 | 741 | 566 | 414 | 360 | 329 | 315 |  |  | 5419 | 1000 lbs | 5419 | MMbtu | 13935.8357 | Mmbtu
| Water (CCF) |  |  | 47.6347 | 51.6854 | 57.1786 | 50.4731 | 37.1814 | 45.695 | 47.513 | 54.3797 | 54.2509 | 44 | 37.3868 | 43.3814 |  |  | 570.7599 | CCF | 426928.4045 | gallons
| Electricity Cost ($) |  |  | 6463.375 | 5669.6682 | 6003.6957 | 5777.5827 | 5383.0387 | 5824.9113 | 5569.7397 | 6152.379 | 5869.107 | 5983.512 | 5714.421 | 5783.151 |  |  | 70194.5812 |  | 70194.5812
| Chilled Water Cost ($) |  |  | 13493.8128 | 9932.832 | 4543.488 | 2609.856 | 1327.248 | 1794.24 | 1812.096 | 3739.536 | 5889.744 | 9459.936 | 13726.656 | 13956.9171 |  |  | 82286.3619 |  | 82286.3619
| Steam Cost ($) |  |  | 2663.04 | 3620.07 | 4757.41 | 7961.38 | 8197.17 | 10166.71 | 10277.67 | 7850.42 | 5742.18 | 4993.2 | 4563.23 | 4542.3 |  |  | 75334.78 |  | 75334.78
|  |  |  | Aug-14 data is from 13.14 Meter Data | [15 empty] | 227815.7231
9 | ECSU - Gilchrist Ed & Psych Bldg | [16 empty] | ECSU - Gilchrist Ed & Psych Bldg
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity Usage (KWhs) |  | 52224 | 55872 | 56832 | 50880 | 50112 | 50112 | 55872 | 64320 | 60480 | 43584 | 45312 | 43392 |  |  |  | 628992 | kwhs | 2146.7497 | MMbtu
| Water Usage (CCF) |  | 529.61 | 938.42 | 896.81 | 817.2 | 782 | 252.56 | 365.83 | 232.19 | 411.89 | 625.06 | 1124.08 | 563.73 |  |  |  | 7539.38 | CCF | 56394.5624 | gallons
| Electricity Cost ($) |  | 6467.55 | 6834.85 | 7158.93 | 5973.78 | 5956.18 | 6277.44 | 6560.56 | 7264.31 | 6987.37 | 5296.43 | 5969.07 | 5830.6 |  |  |  | 76577.07 |  | 76577.07
10 | DoAg&CS - SENC Ag Center | [16 empty] | DoAg&CS - SENC Ag Center
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 2360 | 2600 | 3180 | 4320 | 4320 | 2520 | 2640 | 3040 | 1800 | 3360 | 4680 | 4360 |  |  |  | 39180 | kwhs | 133.7213 | MMbtu
| Nat Gas (Therms) |  | 23 | 22 | 28 | 29 | 1458 | 1195 | 1162 | 1264 | 654 | 33 | 29 | 87 |  |  |  | 5984 | therms | 598.2571 | MMbtu | 731.9785 | Mmbtu
| Water Usage (gallons) |  | 30470 | 53490 | 40810 | 62630 | N/A | 53920 | 60016 | 68914 | 15210 | 5800 | 77670 | 125840 |  |  |  | 594770 | gallons | 594770 | gallons
| Electricity Cost ($) |  | 483.83 | 606.25 | 552.75 | 1045.67 | 856.41 | 510.76 | 570.39 | 599.9 | 405.87 | 852.49 | 890.21 | 823.7 |  |  |  | 8198.23 |  | 8198.23
| Nat Gas Costs ($) |  | 44.55 | 43.65 | 45.91 | 38.45 | 1242.38 | 1045.21 | 926.42 | 133.03 | 947.21 | 41.76 | 39.37 | 82.67 |  |  |  | 4630.61 |  | 4630.61
12828.84
11 | UNCC - EPIC | [16 empty] | UNCC - EPIC
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 415523 | 415560 | 377745 | 440404 | 435530 | 448250 | 455310 | 414430 | 456675 | 448690 | 453830 | 419430 |  |  |  | 5181377 | kwhs | 17684.0397 | MMbtu
| Nat Gas (Therms) |  | 182 | 131 | 142 | 531 | 2083 | 2611 | 979 | 805 | 689 | 1625 | 679 | 166 |  |  |  | 10623 | therms | 1062.0464 | MMbtu
| Chilled water (BTU*10^6) |  | 2555 | 18112 | 9894 | 1481 | 640 | 685 | 456 | 486 | 1141 | 1269 | 2273 | 2539 |  |  |  | 41531 | MMbtu | 41531 | MMbtu
| Hot Water (BTU*10^6) |  | 205 | 345 | 333 | 498 | 624 | 891 | 735 | 858 | 665 | 416 | 439 | 274 |  |  |  | 6283 | MMbtu | 6283 | MMbtu | 66560.0861 | MMbtu
| Water Usage (CF) |  | 4963 | 4932 | 7234 | 8982 | 9050 | 7383 | 6346 | 6550 | 10382 | 10707 | 5507 | 6686 |  |  |  | 88722 | CF | 663640.56 | gallons
| Electricity Cost ($) |  | 28954.7402 | 29745.066 | 26157.435 | 27017.954 | 25049.6894 | 25810.7556 | 25393.1175 | 23362.2171 | 26710.5013 | 25040.5298 | 25507.9191 | 26325.1986 |  |  |  | 315075.1236 |  | 315075.1236
| Nat Gas Costs ($) |  | 177.43 | 133.87 | 143.27 | 475.47 | 1790 | 2240.91 | 807.69 | 618.37 | 456.72 | 353.28 | 428.59 | 132.86 |  |  |  | 7758.46 |  | 7758.46
| Chilled Water |  | 12034.0236 | 42822.3508 | 32682.7684 | 6593.3437 | 9279.7439 | 5684.7613 | 1813.3641 | 3422.7781 | 3692.5994 | 4106.8437 | 11697.4049 | 15243.352 |  |  |  | 149073.3339 |  | 149073.3339
| Hot Water |  | 1531.35 | 2577.15 | 2487.51 | 3720.06 | 4661.28 | 6655.77 | 5490.45 | 6409.26 | 4967.55 | 3107.52 | 3279.33 | 2046.78 |  |  |  | 46934.01 |  | 46934.01
518840.9275
12 | DOA - VA - VA Home Swananoa | [16 empty] | DOA - VA - VA Home Swananoa
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 173700 | 171400 | 202200 | 153000 | 136900 | 161700 | 160600 | 155100 | 146400 | 119900 | 166900 | 178000 |  |  |  | 1925800 | kwhs | 6572.7554 | MMbtu
| Nat Gas (Therms) |  | 1898 | 1719 | 1966 | 2064 | 2100 | 2587 | 2456 | 2408 | 2827 | 2648 | 2193 | 2219 |  |  |  | 27085 | therms | 2707.8533 | MMbtu | 9280.6087 | Mmbtu
| Water Usage (gallons) |  | 248353 | 276779 | 301464 | 261070 | 308945 | 267054 | 365049 | 323906 | 362057 | 300716 | 387490 | 306701 |  |  |  | 3709584 | gallons | 3709584 | gallons
| Electricity Cost ($) |  | 13329.99 | 13121.53 | 15209.35 | 11819.42 | 10615.14 | 12709.56 | 12463.86 | 11939.57 | 12358.56 | 10139.3 | 13776.57 | 14631.04 |  |  |  | 152113.89 |  | 152113.89
| Nat Gas Costs ($) |  | 1688.33 | 1533.74 | 1746.79 | 1820.97 | 1674.26 | 2036.34 | 1937.51 | 1784.45 | 2024.33 | 1905.52 | 1587.16 | 1605.37 |  |  |  | 21344.77 |  | 21344.77
173458.66
13 | Pitt CC - Russell Classroom Building | [16 empty] | Pitt CC - Russell Classroom Building
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 60672 | 58872 | 52676 | 41202 | 38303 | 41087 | 39456 | 46614 | 46234 | 50102 | 62826 | 63061 |  |  | 601105 | kwhs | 2051.5714 | MMbtu
| Gas Usage (Therms) |  |  | 1.28 | 2.15 | 5.26 | 12.87 | 11.43 | 17.67 | 21.27 | 7.99 | 5.36 | 1.97 | 0.65 | 0.68 |  |  | 88.58 | Therms | 8.8559 | MMbtu | 2060.4273 | Mmbtu
| Water CCF |  |  | 56.1 | 61.9 | 48.4 | 38.7 | 15.5 | 58 | 46.4 | 48.4 | 40.6 | 13.5 | 15.5 | 11.57 |  |  | 454.57 | CCF | 340018.36 | gallons
| Electricity Cost ($) |  |  | 7985 | 8153 | 6422 | 5048 | 4407 | 5081 | 4047 | 5306 | 6614 | 6576 | 8175 | 8246 |  |  | 76060 |  | 76060
| Gas Cost ($) |  |  | 185.13 | 292.33 | 670.57 | 1463 | 1313 | 1963 | 2337 | 955 | 653 | 248 | 104 | 107.07 |  |  | 10291.1 |  | 10291.1
86351.1
14 | UNCG - Bailey Residence Hall Renovation | [16 empty] | UNCG - Bailey Residence Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 25182 | 25236 | 27426 | 22419 | 22341 | 22298 | 21389 | 19621 | 26668 | 17996 | 18459 | 18557 |  |  | 267592 | kwhs | 913.2915 | MMbtu
| Steam Usage (lbs) |  |  | 9290 | 11270 | 17980 | 109290 | 109540 | 116840 | 148210 | 29320 | 14890 | 3930 | 7960 | 5030 |  |  | 583550 | lbs | 583.55 | MMbtu
| Chilled water (ton-hrs) |  |  | 28341 | 23764 | 17575 | 10474 | 9538 | 6006 | 4472 | 8930 | 14827 | 18012 | 24276 | 20523 |  |  | 186738 | ton-hrs | 2240.856 | MMbtu | 3737.6975 | Mmbtu
| Water (gallons) |  |  | 47500 | 62200 | 51000 | 44300 | 19000 | 42600 | 52200 | 45200 | 52300 | 15200 | 21300 | 10800 |  |  | 463600 | gallons | 463600 | gallons
| Electricity Cost ($) |  |  | 1708.09 | 1806.6 | 2051.07 | 1351.18 | 1372.39 | 1346.37 | 1259.52 | 1219.31 | 1543.43 | 1041.53 | 1211.79 | 1074 |  |  | 16985.28 |  | 16985.28
| Steam Cost ($) |  |  | 72.58 | 88.05 | 140.48 | 853.89 | 855.85 | 912.88 | 1157.98 | 229.08 | 116.34 | 30.71 | 62.2 | 39.3 |  |  | 4559.34 |  | 4559.34
| Chilled Water ($) | No Data | [15 empty] | 0 |  | 0
21544.62
15 | UNCG - Coit Residence Hall Renovation | [16 empty] | UNCG - Coit Residence Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 22964 | 22523 | 21812 | 17902 | 17834 | 18258 | 19041 | 18479 | 22274 | 14896 | 14053 | 15739 |  |  | 225775 | kwhs | 770.5701 | MMbtu
| Steam Usage (lbs) |  |  | 7620 | 7720 | 8150 | 8080 | 4490 | 2190 | 1990 | 3970 | 8830 | 3510 | 1760 | 2150 |  |  | 60460 | lbs | 60.46 | MMbtu
| Chilled water (ton-hrs) |  |  | 23987 | 18955 | 15893 | 12571 | 11494 | 11455 | 10102 | 12252 | 13560 | 14870 | 16792 | 18529 |  |  | 180460 | ton-hrs | 2165.52 | MMbtu | 2996.5501 | Mmbtu
| Water (gallons) |  |  | 32800 | 53900 | 47600 | 42600 | 13800 | 42500 | 59300 | 85000 | 62700 | 18900 | 2400 | 4400 |  |  | 465900 | gallons | 465900 | gallons
| Electricity Cost ($) |  |  | 1557.65 | 1612.38 | 1631.22 | 1078.95 | 1095.53 | 1102.43 | 1121.25 | 1148.42 | 1289.13 | 862.12 | 922.54 | 910.9 |  |  | 14332.52 |  | 14332.52
| Steam Cost ($) |  |  | 59.53 | 60.32 | 63.68 | 63.13 | 35.08 | 17.11 | 15.55 | 31.02 | 68.98 | 27.42 | 13.75 | 16.8 |  |  | 472.37 |  | 472.37
| Chilled Water ($) | No Data | [15 empty] | 0 |  | 0
14804.89
16 | UNCG - Cotten Residence Hall Renovation | [16 empty] | UNCG - Cotten Residence Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 24495 | 25411 | 26518 | 22416 | 21871 | 21506 | 22596 | 22466 | 27110 | 18572 | 18579 | 19064 |  |  | 270604 | kwhs | 923.5715 | MMbtu
| Steam Usage (lbs) |  |  | 17550 | 12732 | 9979 | 38280 | 39810 | 43710 | 41860 | 36410 | 31070 | 24400 | 25670 | 12939 |  |  | 334410 | lbs | 334.41 | MMbtu
| Chilled water (ton-hrs) |  |  | 20417 | 18544 | 13312 | 7876 | 6822 | 5563 | 3988 | 8682 | 11908 | 12609 | 16985 | 19231 |  |  | 145937 | ton-hrs | 1751.244 | MMbtu | 3009.2255 | Mmbtu
| Water (gallons) |  |  | 38200 | 59400 | 53900 | 55900 | 14100 | 51700 | 53200 | 71000 | 58900 | 18000 | 37200 | 14300 |  |  | 525800 | gallons | 525800 | gallons
| Electricity Cost ($) |  |  | 1661.49 | 1819.12 | 1983.16 | 1351 | 1343.52 | 1298.55 | 1330.59 | 1396.2 | 1569.01 | 1074.87 | 1219.67 | 1103.35 |  |  | 17150.53 |  | 17150.53
| Steam Cost ($) |  |  | 137.11 | 99.48 | 77.97 | 299.08 | 311.04 | 341.51 | 327.06 | 284.47 | 242.75 | 190.64 | 200.56 | 101.09 |  |  | 2612.76 |  | 2612.76
| Chilled Water ($) | No Data | [15 empty] | 0 |  | 0
19763.29
17 | UNCG - Gray Residence Hall Renovation | [16 empty] | UNCG - Gray Residence Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 24553 | 23453 | 25958 | 21316 | 21784 | 19256 | 19638 | 21133 | 24940 | 18405 | 18933 | 19003 |  |  | 258372 | kwhs | 881.8236 | MMbtu
| Steam Usage (lbs) |  |  | 8350 | 10920 | 8520 | 10990 | 49270 | 36690 | 88540 | 57360 | 46910 | 12810 | 4460 | 2990 |  |  | 337810 | lbs | 337.81 | MMbtu
| Chilled water (ton-hrs) |  |  | 18369 | 15458 | 8036 | 2089 | 680 | 963 | 1142 | 3540 | 6454 | 10571 | 17518 | 18910 |  |  | 103730 | ton-hrs | 1244.76 | MMbtu | 2464.3936 | Mmbtu
| Water (gallons) |  |  | 39200 | 61200 | 55100 | 52400 | 18000 | 45300 | 62400 | 56700 | 58900 | 16100 | 21400 | 10100 |  |  | 496800 | gallons | 496800 | gallons
| Electricity Cost ($) |  |  | 1665.43 | 1678.95 | 1941.28 | 1284.71 | 1338.18 | 1162.69 | 1185.75 | 1276.02 | 1443.42 | 1065.2 | 1242.9 | 1099.82 |  |  | 16384.35 |  | 16384.35
| Steam Cost ($) |  |  | 65.24 | 85.32 | 66.57 | 85.86 | 384.95 | 286.66 | 691.77 | 448.82 | 366.51 | 100.08 | 34.85 | 23.36 |  |  | 2639.99 |  | 2639.99
| Chilled Water ($) | No Data | [15 empty] | 0 |  | 0
19024.34
18 | UNCG - Hinshaw Residence Hall Renovation | [16 empty] | UNCG - Hinshaw Residence Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 31432 | 30723 | 33436 | 27231 | 28302 | 27151 | 25452 | 25746 | 31702 | 22632 | 22465 | 21988 |  |  | 328260 | kwhs | 1120.3514 | MMbtu
| Steam Usage (lbs) |  |  | 16160 | 19240 | 21050 | 25010 | 19710 | 42370 | 61490 | 30000 | 22580 | 8290 | 6020 | 4390 |  |  | 276310 | lbs | 276.31 | MMbtu
| Chilled water (ton-hrs) |  |  | 24184 | 20787 | 13290 | 7131 | 5843 | 4637 | 3069 | 8030 | 12007 | 14003 | 19467 | 18284 |  |  | 150732 | ton-hrs | 1808.784 | MMbtu | 3205.4454 | Mmbtu
| Water (gallons) |  |  | 46000 | 61400 | 61600 | 57900 | 35600 | 61800 | 62700 | 55300 | 58800 | 15500 | 14800 | 4700 |  |  | 536100 | gallons | 536100 | gallons
| Electricity Cost ($) |  |  | 2132.3 | 2199.4 | 2500.53 | 1641.2 | 1738.57 | 1639.39 | 1498.77 | 1600.04 | 1834.78 | 1309.85 | 1474.77 | 1272.57 |  |  | 20842.17 |  | 20842.17
| Steam Cost ($) |  |  | 126.25 | 150.32 | 164.45 | 195.39 | 153.98 | 331.01 | 480.39 | 234.37 | 176.41 | 64.76 | 47.03 | 34.3 |  |  | 2158.66 |  | 2158.66
| Chilled Water ($) | No Data | [15 empty] | 0 |  | 0
23000.83
19 | UNCG - Jamison Residence Hall Renovation | [16 empty] | UNCG - Jamison Residence Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 25698 | 25723 | 28328 | 23316 | 22429 | 22776 | 23748 | 23139 | 27712 | 19002 | 16703 | 18376 |  |  | 276950 | kwhs | 945.2304 | MMbtu
| Steam Usage (lbs) |  |  | 7090 | 10100 | 12230 | 27480 | 22220 | 70310 | 73750 | 24070 | 6400 | 1960 | 1840 | 1690 |  |  | 259140 | lbs | 259.14 | MMbtu
| Chilled water (ton-hrs) |  |  | 90670 | 87000 | 58900 | 36370 | 34920 | 29920 | 20640 | 26810 | 33920 | 38460 | 19340 | 18740 |  |  | 495690 | ton-hrs | 5948.28 | MMbtu | 7152.6503 | Mmbtu
| Water (gallons) |  |  | 43600 | 56000 | 54000 | 54600 | 22000 | 50200 | 75900 | 71900 | 69200 | 19300 | 2900 | 5600 |  |  | 525200 | gallons | 525200 | gallons
| Electricity Cost ($) |  |  | 1743.09 | 1841.46 | 2118.52 | 1405.24 | 1377.8 | 1375.23 | 1398.43 | 1438.02 | 1603.85 | 1099.76 | 1096.51 | 1063.53 |  |  | 17561.44 |  | 17561.44
| Steam Cost ($) |  |  | 55.39 | 78.91 | 95.55 | 214.69 | 173.59 | 549.3 | 576.17 | 188.05 | 50 | 15.32 | 14.38 | 13.2 |  |  | 2024.55 |  | 2024.55
| Chilled Water ($) | No Data | [15 empty] | 0 |  | 0
19585.99
20 | UNCG - Shaw Residence Hall Renovation | [16 empty] | UNCG - Shaw Residence Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 44245 | 47094 | 53020 | 44629 | 46112 | 44102 | 44996 | 44367 | 51886 | 38929 | 38420 | 37831 |  |  | 535631 | kwhs | 1828.1086 | MMbtu
| Steam Usage (lbs) |  |  | 12360 | 88760 | 98090 | 73480 | 75810 | 96760 | 97940 | 50950 | 8810 | 10820 | 2980 | 1480 |  |  | 618240 | lbs | 618.24 | MMbtu
| Chilled water (ton-hrs) |  |  | 55574 | 50017 | 37051 | 30148 | 29138 | 27972 | 21820 | 26412 | 29447 | 37054 | 46880 | 47976 |  |  | 439489 | ton-hrs | 5273.868 | MMbtu | 7720.2166 | Mmbtu
| Water (gallons) |  |  | 66600 | 101200 | 97600 | 95900 | 48700 | 87300 | 121900 | 101400 | 109300 | 38200 | 42400 | 15300 |  |  | 925800 | gallons | 925800 | gallons
| Electricity Cost ($) |  |  | 3001.13 | 3371.37 | 3965.13 | 2689.77 | 2832.63 | 2662.91 | 2649.64 | 2757.28 | 3002.94 | 2253.05 | 2522.18 | 2189.5 |  |  | 33897.53 |  | 33897.53
| Steam Cost ($) |  |  | 96.56 | 693.5 | 766.3 | 574.1 | 592.2 | 755.9 | 765.1 | 398.1 | 68.83 | 84.53 | 23.28 | 11.56 |  |  | 4829.96 |  | 4829.96
| Chilled Water ($) | No Data | [15 empty] | 0 |  | 0
38727.49
21 | WCU - Harrill Residence Hall Renovation | [16 empty] | WCU - Harrill Residence Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 60739 | 78737 | 86657 | 75803 | 77415 | 51474 | 78316 | 82982 | 73544 | 74750 | 59697 | 56519 |  |  |  | 856633 | kwhs | 2923.6884 | MMbtu
| Water (gallons) |  | 14690 | 114850 | 226300 | 198250 | 167200 | 79360 | 144200 | 197810 | 167900 | 180230 | 55320 | 7730 |  |  |  | 1553840 | gallons | 1553840 | gallons
| Electricity Cost ($) |  | 1065.451 | 8464.3301 | 16413.9916 | 11617.45 | 10065.44 | 4991.744 | 8493.38 | 11018.017 | 10006.84 | 10705.662 | 3280.476 | 579.75 |  |  |  | 96702.5318 |  | 96702.5318
22 | UNCP Health Science Builidng | [16 empty] | UNCP Health Science Builidng
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 124350 | 124506 | 157696 | 138410 | 115773 | 107197 | 96118 | 110983 | 90056 | 131594 | 122952 | 119384 |  |  |  | 1439019 | kwhs | 4911.3718 | MMbtu
| Nat Gas (Therms) |  | 878 | 1123 | 1488 | 1741 | 1756 | 2813 | 2829 | 3202 | 3083 | 2150 | 1769 | 1707 |  |  |  | 24539 | therms | 2453.3141 | MMbtu | 7364.686 | MMBtu
| Water (gallons) |  | 147700 | 141500 | 131000 | 67100 | 31250 | 18300 | 9750 | 10120 | 26800 | 50000 | 94225 | 120500 |  |  |  | 848245 | gallons | 848245 | gallons
| Electricity Cost ($) |  | 10042.506 | 10055.1046 | 12735.529 | 11177.9916 | 9349.8275 | 8657.2297 | 7762.4897 | 8962.9871 | 7272.9226 | 10627.5314 | 9929.6035 | 9641.4518 |  |  |  | 116215.1744 |  | 116215.1744
| Nat Gas Costs ($) |  | 505.2012 | 646.1742 | 856.1952 | 1001.7714 | 1010.4024 | 1618.6002 | 1627.8066 | 1842.4308 | 1773.9582 | 1237.11 | 1017.8826 | 982.2078 |  |  |  | 14119.7406 |  | 14119.7406
130334.915
23 | FSU - Renaissance Residence Hall | [16 empty] | FSU - Renaissance Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | No Data. | [15 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | No Data. | [15 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | No Data. | [15 empty] | 0 |  | 0
24 | UNCA - Overlook Residence Hall |  |  | NO DATA | [13 empty] | UNCA - Overlook Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
25 | ECSU - Viking Tower Residence Hall | [16 empty] | ECSU - Viking Tower Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity Usage (KWhs) |  | 46151 | 49957 | 57090 | 57474 | 52506 | 46523 | 49953 | 50798 | 50829 | 54029 | 50270 | 42143 |  |  |  | 607723 | kwhs | 2074.1586 | MMbtu
| Water (CCF) |  | 12794.38 | 33655.54 | 33655.54 | 41491.73 | 41491.73 | 32685.43 | 32685.43 | 35705.26 | 35705.26 | 29886.57 | 11631.36 | 12968.16 |  |  |  | 354356.39 | CCF | 2650585.7972 | gallons
| Electricity Cost ($) |  | 4859.69 | 5365.42 | 6102.94 | 6120.96 | 5691.63 | 5024.47 | 5280.02 | 5562.35 | 5403.08 | 5678.49 | 5308.49 | 4513.52 |  |  |  | 64911.06 |  | 64911.06
26 | UNCW - Teaching Lab | [16 empty] | UNCW Teaching Lab
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 100845 | 78204 | 93223 | 110163 | 109266 | 122835 | 135652 | 119214 | 106070 | 104028 | 81870 | 81322 |  |  |  | 1242692 | kwhs | 4241.3078 | MMbtu
| Heating Hot Water Usage (Mbtu) |  | 185760.6375 | 182846.5875 | 177215.625 | 195564.5625 | 353043.625 | 353908.8375 | 422476.1375 | 495615.6625 | 317742.1625 | 195338.2 | 202179.6875 | 187366.975 |  |  |  | 3269058.7 | Mbtu | 3269.0587 | MMbtu
| Chilled water (ton-hrs) |  | 184925.65 | 187610.7146 | 161643.9156 | 92603.6313 | 42747.975 | 24144.9792 | 20962.699 | 9090.1406 | 41390.976 | 73507.149 | 122285.9531 | 189833.1719 |  |  |  | 1150746.9552 | ton-hrs | 13808.9635 | MMbtu | 21319.33 | MMbtu
| Water Usage (gallons) |  | 59987 | 60321 | 93677 | 93797 | 82883 | 67813 | 82585 | 78934 | 77250 | 78573 | 44429 | 38100 |  |  |  | 858349 | gallons | 858349 | gallons
| Electricity Cost ($) |  | 8390.3 | 6381.45 | 7541.74 | 7975.8 | 8347.92 | 9433.73 | 10241.73 | 8821.84 | 7965.86 | 7968.54 | 6091.13 | 6774.12 |  |  |  | 95934.16 |  | 95934.16
| Heating Hot Water ($) |  | 1991.48 | 1230.58 | 1424.64 | 1651.44 | 2368.8 | 3424.12 | 2639.52 | 1759.68 | 2454.05 | 1963.63 | 1263.33 | 1306.98 |  |  |  | 23478.25 |  | 23478.25
| Chilled Water ($) |  | 16199.1 | 12131.34 | 11104.35 | 7007.04 | 3332.03 | 3691.6 | 1790.24 | 1136.79 | 4071.71 | 7374.51 | 8692.64 | 10220.77 |  |  |  | 86752.12 |  | 86752.12
206164.53
27 | UNCA - Rhoades Hall Renovation |  |  | NO DATA | [13 empty] | UNCA - Rhoades Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
28 | ECU - Ross Hall | [16 empty] | ECU - Ross Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 190224.69 | 191998.96 | 188596.37 | 199761.09 | 187643.35 | 182052.4 | 193078.83 | 174839.47 | 188608.53 | 184840.94 | 192226.79 | 190063.41 |  |  |  | 2263934.83 | kwhs | 7726.8096 | MMbtu
| Chilled water (ton-hrs) |  | 114762 | 107728 | 102847 | 80668 | 23516 | 22610 | 19803 | 15782 | 28793 | 54040 | 81870 | 115647 |  |  |  | 768066 | ton-hrs | 9216.792 | MMbtu
| Natural Gas (Therms) | Low Data. | 77.026 | 0 | 140.656 | 226.952 | 48.166 | 364.778 | 1599.237 | 661.081 | 274.463 | 189.666 | 1.835 | 60.306 |  |  |  | 3644.166 | therms | 364.3296 | MMbtu | 17307.9312 | MMbtu
| Water Usage (gallons) | No Data. | [15 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) |  | 17919.1658 | 18086.302 | 17765.7781 | 18817.4947 | 17676.0036 | 17149.3361 | 18188.0258 | 16469.8781 | 17766.9235 | 17412.0165 | 18107.7636 | 17903.9732 |  |  |  | 213262.661 |  | 213262.661
| Chilled Water ($) | No Data. | [15 empty] | 0 |  | 0
| Nat Gas Costs ($) | Low Data. | 64.2532 | 0 | 117.3318 | 189.3178 | 40.1789 | 304.2889 | 1334.0444 | 551.4576 | 228.9503 | 158.2147 | 1.5307 | 50.3058 |  |  |  | 3039.8741 |  | 3039.8741
213262.661
29 | Gaston College - Lena Sue Beam Renovation | [16 empty] | Gaston College - Lena Sue Beam Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 22640 | 30070 | 32560 | 22040 | 25200 | 25000 | 24040 | 25480 | 24280 | 23760 | 22840 | 21920 |  |  | 299830 | kwhs | 1023.3198 | MMbtu
| Heating Hot Water (?) | No Data. | [15 empty] | 0 | lbs | 0 | MMbtu
| Chilled water (ton-hrs) | No Data. | [15 empty] | 0 | ton-hrs | 0 | MMbtu
| Water (gallons) |  |  | 2390 | 2465 | 4500 | 9480 | 8375 | 9463 | 7783 | 11358 | 13838 | 7592 | 3017 | 2421 |  |  | 82682 | gallons | 82682 | gallons
| Electricity Cost ($) |  |  | 1803.9552 | 2809.7408 | 2521.772 | 1753.282 | 1884.708 | 1886.75 | 1765.4976 | 1967.5656 | 1781.4236 | 1796.9688 | 2093.7428 | 1878.8728 |  |  | 23944.2792 |  | 23944.2792
| Heating Hot Water Cost ($) | No Data. | [15 empty] | 0 |  | 0
| Chilled Water ($) | No Data. | [15 empty] | 0 |  | 0
23944.2792
30 | NCSU - Hunt Library | [16 empty] | NCSU - Hunt Library
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (kWh) |  |  | 352410.8887 | 373878.1738 | 383077.8809 | 368188.9648 | 376896.9727 | 373953.125 | 339479.0039 | 379661.1328 | 373618.6523 | 372617.1875 | 363661.1328 | 370893.0664 |  |  | 4428336.1816 | kwh | 15113.9114 | MMbtu
| Chilled Water (Dtherms) |  |  | 6501.92 | 1005 | 768.36 | 928.36 | 802.45 | 905.56 | 790.99 | 345.92 | 529.256 | 850.312 | 1236.704 | 1341.952 |  |  | 16006.784 | dthrms | 16006.784 | MMbtu
| Steam (1,000 lbs) |  |  | 345.3047 | 358 | 405.2969 | 723.3047 | 785.5 | 1123.5 | 1139 | 760 | 405.5 | 334.5938 | 299.7969 | 290.8125 |  |  | 6970.6094 | 1000 lbs | 6970.6094 | MMbtu | 38091.3048 | MMbtu
| Water (CCF) |  |  | 301 | 394 | 300 | 156 | 113 | 104 | 156 | 135 | 183 | 202 | 310 | 206 |  |  | 2560 | CCF | 1914880 | gallons
| Electricity Cost ($) |  |  | 30659.7473 | 31405.7666 | 32178.542 | 30927.873 | 32790.0366 | 32533.9219 | 29534.6733 | 33030.5186 | 32504.8228 | 32417.6953 | 31638.5186 | 32267.6968 |  |  | 381889.8127 |  | 381889.8127
| Chilled Water Cost ($) |  |  | 93627.648 | 14472 | 11064.384 | 13368.384 | 11555.28 | 13040.064 | 11390.256 | 4981.248 | 7621.2864 | 12244.4928 | 17808.5376 | 19324.1088 |  |  | 230497.6896 |  | 230497.6896
| Steam Cost ($) |  |  | 4789.376 | 4965.46 | 5621.4677 | 10032.236 | 10894.885 | 15582.945 | 15797.93 | 10541.2 | 5624.285 | 4640.8153 | 4158.1827 | 4033.5694 |  |  | 96682.352 |  | 96682.352
|  |  |  | Aug-14 data is from 13.14 Meter Data. Chilled water meter is high for Aug-14 | [15 empty] | 709069.8544
31 | UNCC - Rose Football Center | [16 empty] | UNCC - Rose Football Center
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 173510 | 179450 | 178020 | 171290 | 152680 | 146750 | 119470 | 137560 | 127360 | 189280 | 180300 | 220612 |  |  |  | 1976282 | kwhs | 6745.0505 | MMbtu
| Nat Gas (Therms) |  | 1124 | 1391 | 1882 | 1911 | 2927 | 3666 | 5134 | 4366 | 3219 | 2360 | 1947 | 1394 |  |  |  | 31321 | therms | 3131.3522 | MMbtu | 9876.4027 | Mmbtu
| Water Usage (CF) |  | 25696 | 28456 | 23223 | 16207 | 35992 | 14311 | 25039 | 6083 | 8008 | 20030 | 41158 | 55695 |  |  |  | 299898 | CF | 2243237.04 | gallons
| Electricity Cost ($) |  | 12090.6351 | 12844.7206 | 12327.2223 | 10508.3181 | 8781.4538 | 8450.0355 | 6662.9675 | 7754.5221 | 7449.1694 | 10563.3544 | 10133.922 | 13846.5411 |  |  |  | 121412.8619 |  | 121412.8619
| Nat Gas Costs ($) |  | 981.88 | 1209.9 | 1629.21 | 1653.97 | 2506 | 3137.48 | 4142.24 | 3256.47 | 2053.01 | 0 | 955.55 | 952.95 |  |  |  | 22478.66 |  | 22478.66
143891.5219
32 | DOA - VA - VA Home Kinston | [16 empty] | DOA - VA - VA Home Kinston
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 192600 | 188400 | 206400 | 154200 | 170800 | 165800 | 167000 | 171800 | 170600 | 159800 | 187400 | 194000 |  |  |  | 2128800 | kwhs | 7265.5944 | MMbtu
| Nat Gas (Therms) |  | 1161 | 1190 | 1404 | 1379 | 1566 | 1997 | 1716 | 1693 | 1835 | 1666 | 1780 | 1119 |  |  |  | 18506 | therms | 1850.1582 | MMbtu | 9115.7526 | MMBtu
| Water Usage (gallons) |  | 201000 | 188100 | 237890 | 210120 | 231200 | 221300 | 255000 | 266000 | 263700 | 260400 | 313240 | 344100 |  |  |  | 2992050 | gallons | 2992050 | gallons
| Electricity Cost ($) |  | 15850.18 | 15546.24 | 16838.5 | 12947.88 | 13953.54 | 14184.53 | 14604.67 | 14923.05 | 14541.59 | 13785.35 | 16256.28 | 17028.24 |  |  |  | 180460.05 |  | 180460.05
| Nat Gas Costs ($) |  | 1096 | 1110.93 | 1306.47 | 1289.61 | 1446.05 | 1750.52 | 1413.28 | 1192.94 | 1187.67 | 1090.97 | 1284.46 | 1019.18 |  |  |  | 15188.08 |  | 15188.08
195648.13
33 | Randolph CC - Klaussner Building Renovation | [16 empty] | Randolph CC - Klaussner Building Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 72500 | 64200 | 78300 | 57500 | 46600 | 42400 | 41300 | 45900 | 53900 | 56200 | 60400 | 81900 |  |  |  | 701100 | kwhs | 2392.8543 | MMbtu
| Nat Gas (Therms) |  | 260 | 282 | 368 | 487 | 618 | 722 | 1268 | 1416 | 1106 | 553 | 558 | 547 |  |  |  | 8185 | therms | 818.3046 | MMbtu | 3211.1589 | MMbtu
| Water Usage (CF) |  | 215 | 255 | 191 | 252 | 134 | 72 | 153 | 110 | 187 | 187 | 137 | 136 |  |  |  | 2029 | CF | 15176.92 | gallons
| Electricity Cost ($) |  | 6215.02 | 5721.38 | 6621.81 | 5269.94 | 4460.13 | 4236.56 | 4185.45 | 4541.13 | 5070.73 | 5215.29 | 5376.45 | 7033.46 |  |  |  | 63947.35 |  | 63947.35
| Nat Gas Costs ($) |  | 261.12 | 281.23 | 359.81 | 477.05 | 578.35 | 676.08 | 1074.86 | 1111.89 | 714.28 | 377.86 | 387.15 | 433.65 |  |  |  | 6733.33 |  | 6733.33
70680.68
34 | ASU - Plemmons Student Union Addition | [16 empty] | ASU - Plemmons Student Union Addition
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 1893162.9599 | kwhs | 6461.3652 | MMbtu
| Steam (lbs) | [16 empty] | 6221463.6 | lbs | 6221.4636 | MMbtu | 12682.8288 | MMbtu
| Water (gallons) | [16 empty] | 2355608.9999 | gallons | 2355608.9999 | gallons
| Elecricity Cost ($) | [16 empty] | 167507.1405 |  | 167507.1405
| Steam Costs ($) | [16 empty] | 130664.16 |  | 130664.16
298171.3005
35 | ASU - Summit Residence Hall and Appalachian Hall | [16 empty] | ASU - Summit Residence Hall and Appalachian Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 1120233.9199 | kwhs | 3823.3584 | MMbtu
| Steam (lbs) | [16 empty] | 4900925 | lbs | 4900.925 | MMbtu | 8724.2834 | MMbtu
| Water (gallons) | [16 empty] | 2745167.9999 | gallons | 2745167.9999 | gallons
| Electricity Cost ($) | [16 empty] | 100287.1136 |  | 100287.1136
| Steam Costs ($) | [16 empty] | 119841.2 |  | 119841.2
220128.3136
36 | UNCW - MARBIONC | [16 empty] | UNCW - MARBIONC
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 366800 | 369800 | 388600 | 286000 | 250000 | 216800 | 209000 | 204400 | 245800 | 272800 | 331200 | 384600 |  |  |  | 3525800 | kwhs | 12033.5554 | MMbtu
| Nat Gas (MCF) |  | 628.1 | 614.7 | 683.6 | 765 | 874.8 | 1261.3 | 1183.4 | 1312.6 | 1061.3 | 918 | 809 | 759.9 |  |  |  | 10871.7 | MCF | 11165.2359 | MMbtu | 23198.7913 | MMbtu
| Water Usage (CF) |  | * | * | * | * | * | * | * | * | * | * | * | * |  |  |  | 0 | CF | 0 | gallons
| Electricity Cost ($) |  | 27540.53 | 28192.91 | 28393.57 | 20454.03 | 17877.04 | 16461.45 | 15806.64 | 14454.17 | 17442.59 | 19280.93 | 22945.36 | 29672.26 |  |  |  | 258521.48 |  | 258521.48
| Nat Gas Costs ($) |  | 5582.74 | 5467.48 | 6073.21 | 7190.09 | 8071.29 | 11596.27 | 10014.6 | 10147.68 | 2069.12 | 5485.29 | 4943.11 | 5428.9 |  |  |  | 82069.78 |  | 82069.78 |  |  | MCF=1000CF
|  |  | * No Data. | [16 empty] | 340591.26 |  |  | 1 cubic foot = 1,025 Btu
37 | DOA - NC State Bar HQ | [16 empty] | DOA - NC State Bar HQ
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 75400 | 72000 | 75000 | 83000 | 83000 | 87600 | 78000 | 87200 | 88200 | 72600 | 71200 | 77200 |  |  | 950400 | kwhs | 3243.7152 | MMbtu
| Water Usage (CCF) |  |  | 23 | 22 | 21 | 19 | 17 | 15 | 20 | 59 | 17 | 21 | 24 | 37 |  |  | 295 | CCF | 220660 | gallons
| Elecricity Cost ($) |  |  | 6463.28 | 6206.95 | 6454.92 | 7033.84 | 7257.95 | 7902.84 | 7022.37 | 7897.36 | 7767.58 | 6580.62 | 6484.38 | 6845.41 |  |  | 83917.5 |  | 83917.5
83917.5
38 | FSU - Science and Technology Building | [16 empty] | FSU - Science and Technology Building
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | No Data. | [15 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | No Data. | [15 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | No Data. | [15 empty] | 0 |  | 0
39 | UNCW - Student Rec Facility Addition | [16 empty] | UNCW - Student Rec Facility Addition
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 167000 | 127000 | 154000 | 161000 | 123000 | 128000 | 131000 | 129000 | 133000 | 153000 | 125000 | 140000 |  |  |  | 1671000 | kwhs | 5703.123 | MMbtu
| Nat Gas (MCF) |  | 20 | 17 | 21 | 27 | 21 | 15 | 27 | 22 | 21 | 20 | 18 | 14 |  |  |  | 243 | MCF | 249.561 | MMbtu
| Heating Hot Water Usage (Mbtu) |  | 337499.136 | 367200.256 | 363899.904 | 314600.448 | 586699.776 | 638300.16 | 942000.128 | 738999.296 | 412600.32 | 359700.48 | 199000.064 | 119899.136 |  |  |  | 5380399.104 | Mbtu | 5380.3991 | MMbtu
| Chilled water (ton-hrs) |  | 173808.2987 | 174383.2747 | 148383.4027 | 86333.2693 | 35283.456 | 25399.9787 | 27408.2133 | 19616.768 | 66858.3253 | 91574.9547 | 108125.0133 | 150958.4213 |  |  |  | 1108133.376 | ton-hrs | 13297.6005 | MMbtu | 24630.6836 | MMbtu
| Water Usage (gallons) |  | 25000 | 113900 | 113500 | 142500 | 85100 | 51900 | 122400 | 138400 | 116400 | 116500 | 66500 | 68600 |  |  |  | 1160700 | gallons | 1160700 | gallons
| Electricity Cost ($) |  | 13894.4 | 10363.2 | 12458.6 | 11656.4 | 9397.2 | 9830.4 | 9890.5 | 9546 | 9988.3 | 11719.8 | 9300 | 11662 |  |  |  | 129706.8 |  | 129706.8
| Nat Gas Costs ($) |  | 114.4 | 86.36 | 110.25 | 141.75 | 110.25 | 87.9 | 126.9 | 93.06 | 89.67 | 74.2 | 66.6 | 56.28 |  |  |  | 1157.62 |  | 1157.62 |  |  | MCF=1000CF
| Heating Hot Water ($) |  | 1618.07 | 999.85 | 1157.52 | 1341.8 | 1924.65 | 2782.09 | 2144.61 | 1429.74 | 1993.92 | 1595.45 | 1026.45 | 1061.92 |  |  |  | 19076.07 |  | 19076.07
| Chilled Water ($) |  | 13161.77 | 9856.71 | 9022.28 | 5693.22 | 2707.28 | 2999.43 | 1454.57 | 923.64 | 3308.26 | 5991.79 | 7062.77 | 8304.37 |  |  |  | 70486.09 |  | 70486.09
[20 empty] | 220426.58 |  |  | 1 cubic foot = 1,025 Btu
40 | WSSU - Reaves Student Activities Center | [16 empty] | WSSU - Reaves Student Activities Center
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 90148 | 98775 | 95992 | 90698 | 65871 | 97417 | 90794 | 99425 | 95630 | 179402 | 67828 | 68049 |  |  | 1140029 | kwhs | 3890.919 | MMbtu
| Steam (Nat Gas in therms) |  |  | 4609.7442 | 4992.7299 | 5968.6934 | 8884.1676 | 9337.0674 | 10576.021 | 9202.8224 | 7797.375 | 5759.5345 | 3937.186 | 3772.6089 | 3816.8572 |  |  | 78654.8074 | therms | 7863.6028 | MMbtu
| Chilled water (kwh) |  |  | 111374.4222 | 96537.339 | 71467.2103 | 160197.8071 | 19567.3114 | 17388.7743 | 13207.0424 | 44098.373 | 64527.8505 | 162181.943 | 93334.8353 | 111579.6569 |  |  | 965462.5653 |  | 3295.1237 | MMbtu
| Nat Gas (Therms) |  |  | 678 | 765 | 765 | 851 | 613 | 999 | 942 | 763 | 1071 | 1126 | 1400 | 2270 |  |  | 12243 | therms | 1224.0077 | MMbtu | 12978.5295 | Mmbtu
| Water (CCF) |  |  | 99.75 | 106 | 78.79 | 82.91 | 33.7 | 99.76 | 81.82 | 81.82 | 86.51 | 30.02 | 32.47 | 23.01 |  |  | 836.56 | CCF | 625746.88 | gallons
| Electricity Cost ($) |  |  | 6400.508 | 7013.025 | 6815.432 | 6439.558 | 4676.841 | 6916.607 | 6446.374 | 7059.175 | 6789.73 | 12737.542 | 4815.788 | 4831.479 |  |  | 80942.059 |  | 80942.059
| Steam Costs ($ Natural Gas) |  |  | 2305.1888 | 2563.2683 | 3062.0171 | 4136.1361 | 4879.6141 | 4348.829 | 3881.8173 | 2986.1674 | 2144.4039 | 1467.4534 | 1529.7069 | 1530.4944 |  |  | 34835.0968 |  | 34835.0968
| Chilled water ($) |  |  | 7907.584 | 6854.1511 | 5074.1719 | 11374.0443 | 1389.2791 | 1234.603 | 937.7 | 3130.9845 | 4581.4774 | 11514.918 | 6626.7733 | 7922.1556 |  |  | 68547.8421 |  | 68547.8421
| Nat Gas Costs ($) |  |  | 601.01 | 675.3 | 691.29 | 735.3 | 546.88 | 798.14 | 702.95 | 466.52 | 663.31 | 699.83 | 1002.98 | 1612.59 |  |  | 9196.1 |  | 9196.1
193521.0979
41 | Haywood Community College - Creative Arts Building | [16 empty] | Haywood Community College - Creative Arts Building
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 282277 | kwhs | 963.4114 | MMbtu
| Nat Gas (therms) |  |  |  | 209 | 297 | 1409 | 1424 | 1364 | 1765 | 369 | 179 | 75 | 146 | 54 | 63 |  | 7354 | therms | 735.2244 | MMbtu | 1698.6358 | MMbtu
| Water Usage (CF) | [16 empty] | 154338 | gallons | 154338 | gallons
| Elecricity Cost ($) | [16 empty] | 16996 |  | 16996
| Nat Gas Costs ($) | [16 empty] | 5924.42 |  | 5924.42
22920.42
42 | UNCC - Belk Residence Hall | [16 empty] | UNCC - Belk Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 143000 | 187917 | 159676 | 202458 | 155992 | 144957 | 136202 | 137208 | 157337 | 157170 | 167331 | 179152 |  |  |  | 1928400 | kwhs | 6581.6292 | MMbtu
| Nat Gas (Therms) |  | 531 | 1986 | 2633 | 2708 | 4733 | 5292 | 7672 | 6684 | 4793 | 3129 | 1935 | 1910 |  |  |  | 44006 | therms | 4399.5493 | MMbtu | 10981.1785 | Mmbtu
| Water (CF) |  | 110859.6257 | 255355.615 | 263399.7326 | 64045.4545 | 58498.6631 | 33775.4011 | 62363.6364 | 64815.508 | 64834.2246 | 76471.9251 | 38299.4652 | 39816.8449 |  |  |  | 1132536.0963 | CF | 8471370 | gallons
| Electricity Cost ($) |  | 9964.6177 | 13450.7738 | 11056.9686 | 12420.4161 | 8971.9449 | 8346.7924 | 7596.1288 | 7734.6792 | 9202.4966 | 8771.3568 | 9404.9878 | 11244.3363 |  |  |  | 118165.4989 |  | 118165.4989
| Nat Gas Costs ($) |  | 475.47 | 1718.02 | 2270.56 | 2334.6 | 4039.25 | 4519.31 | 6179.08 | 4973.72 | 3046.12 |  | 610.46 | 1297.55 |  |  |  | 31464.14 |  | 31464.14
149629.6389
43 | NCSU - Cherry Building Renovation | [16 empty] | NCSU - Cherry Building Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 13560 | 29200 | 23900 | 24200 | 25900 | 28100 | 26700 | 33200 | 22200 | 26500 | 29900 | 34000 |  |  | 317360 | kwhs | 1083.1497 | MMbtu
| Nat Gas (Therms) |  |  | * | 193 | 375 | 1182 | 1546 | 1495 | 2357 | 536 | 307 | 195 | 99 | 68 |  |  | 8353 | therms | 835.1006 | MMbtu | 1918.2502 | Mmbtu
| Water (CCF) |  |  | 1 | 14.6769 | 18.7516 | 21.2852 | 16.4701 | 10.2581 | 5.6081 | 5.7214 | 8.9348 | 12.7715 | 21.6856 | 24 |  |  | 161.1633 | CCF | 120550.1733 | gallons
| Electricity Cost ($) |  |  | 1071.77 | 2676.13 | 1930.46 | 1915.03 | 1983.12 | 2187.26 | 2132.69 | 2531.18 | 1892.42 | 2296.74 | 2862.01 | 3057.41 |  |  | 26536.22 |  | 26536.22
| Nat Gas Costs ($) |  |  | * | 197.25 | 350.15 | 952.44 | 1233.77 | 1167.48 | 1717.28 | 425.16 | 253.6 | 167.92 | 94.38 | 70.6 |  |  | 6630.03 |  | 6630.03
|  |  |  | * No Data. Aug-14 data is from 13.14 Data. | [15 empty] | 33166.25
44 | UNCC - Hunt Residence Hall | [16 empty] | UNCC - Hunt Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 64434 | 94275 | 101437 | 110986 | 90523 | 83795 | 95329 | 94561 | 97703 | 99476 | 77330 | 70230 |  |  |  | 1080079 | kwhs | 3686.3096 | MMbtu
| Nat Gas (Therms) |  | 96 | 191 | 663 | 598 | 764 | 583 | 762 | 961 | 772 | 878 | 449 | 72 |  |  |  | 6789 | therms | 678.7379 | MMbtu
| Chilled Water (MMBtu) |  | 452 | 598 | 526 | 340 | 126 | 83 | 87 | 87 | 135 | 280 | 348 | 474 |  |  |  | 3536 | MMbtu | 3536 | MMbtu
| Hot Water (MMBtu) |  | 134 | 107 | 116 | 149 | 183 | 268 | 223 | 215 | 180 | 86 | 76 | 71 |  |  |  | 1808 | MMbtu | 1808 | MMbtu | 9709.0475 | MMbtu
| Water (CF) |  | 2075 | 23674 | 45449 | 42205 | 36231 | 16964 | 37109 | 33000 | 33000 | 33225 | 11740 | 3143 |  |  |  | 317815 | CF | 2377256.2 | gallons
| Electricity Cost ($) |  | 4489.9313 | 6748.0414 | 7024.1346 | 6808.7816 | 5206.4681 | 4825.0134 | 5316.5986 | 5330.5856 | 5714.5587 | 5551.5651 | 4346.4015 | 4407.9315 |  |  |  | 65770.0114 |  | 65770.0114
| Nat Gas Costs ($) |  | 103.98 | 185.11 | 588.2 | 532.69 | 670.46 | 517.45 | 633.54 | 733.94 | 509.09 | 194.97 | 290.86 | 70.08 |  |  |  | 5030.37 |  | 5030.37
| Chilled Water ($) |  | 3283.2235 | 6324.0974 | 5166.6005 | 2728.385 | 2340.7605 | 1782.0125 | 1219.1588 | 390.3426 | 2281.8506 | 1476.3234 | 1732.957 | 3040.8767 |  |  |  | 31766.5888 |  | 31766.5888
| Hot Water ($) |  | 5556.8312 | 2986.3489 | 3705.0382 | 3014.2207 | 3481.9795 | 7267.4249 | 6064.6244 | 3400.5636 | 3628.7419 | -306.4548 | 1132.0232 | 1509.3893 |  |  |  | 41440.7309 |  | 41440.7309
144007.7012
45 | NCSU - Wolf Ridge at Centennial Bldg 6 - Lakeview Hall | [16 empty] | NCSU - Wolf Ridge 6
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 38392 | 40170 | 39189.9996 | 37159.0004 | 31248.0011 | 35535.9955 | 35292.9993 | 35611.9995 | 36420.0134 | 35029.9988 | 33445.9839 | 34214.0198 |  |  | 431710.0112 | kwhs | 1473.4263 | MMbtu
| Steam (1000lbs) |  |  | 25.23 | 49.85 | 81.02 | 148 | 181.1 | 236.26 | 259 | 184 | 117 | 68 | 41.9898 | 70 |  |  | 1461.4498 | 1000lbs | 1461.4498 | MMbtu
| Chilled Water (Dtherms) |  |  | 286 | 286 | 189 | 97 | 83 | 99 | 81 | 112 | 161 | 236 | 338 | 359 |  |  | 2327 | dtherms | 2326.4444 | MMbtu | 5261.3204 | Mmbtu
| Water (CCF) |  |  | 62 | 100 | 81 | 80 | 43 | 63 | 80 | 57 | 72 | 51 | 41 | 34 |  |  | 764 | CCF | 571472 | gallons
| Electricity Cost ($) |  |  | 3340.104 | 3494.79 | 3409.53 | 3232.833 | 2718.5761 | 3091.6316 | 3070.4909 | 3098.244 | 3168.5412 | 3047.6099 | 2909.8006 | 2976.6197 |  |  | 37558.771 |  | 37558.771
| Steam Costs ($) |  |  | 349.9401 | 691.4195 | 1123.7474 | 2052.76 | 2511.857 | 3276.9262 | 3592.33 | 2552.08 | 1622.79 | 943.16 | 582.398 | 970.9 |  |  | 20270.3082 |  | 20270.3082
| Chilled Water ($) |  |  | 4118.4 | 4118.4 | 2721.6 | 1396.8 | 1195.2 | 1425.6 | 1166.4 | 1612.8 | 2318.4 | 3398.4 | 4867.2 | 5169.6 |  |  | 33508.8 |  | 33508.8
91337.8791
46 | NCSU - Wolf Ridge at Centennial Bldg 1 - Tower Hall | [16 empty] | NCSU - Wolf Ridge 1
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 151838.6459 | 141682.9834 | 141580.9326 | 129261.1084 | 118741.9434 | 136548.9502 | 133772.0947 | 141210.8765 | 140703.0029 | 131492.1875 | 121101.1556 | 123175.0259 |  |  | 1611108.907 | kwhs | 5498.7147 | MMbtu
| Steam (1000lbs) |  |  | 146.6543 | 198.1319 | 303.5922 | 495.3952 | 542.0977 | 714.7441 | 825.057 | 627.2033 | 351.6739 | 279.3356 | 258.1463 | 235.0534 |  |  | 4977.0849 | 1000lbs | 4977.0849 | MMbtu
| Chilled water (Dtherms) |  |  | 650.1258 | 824.968 | 473.8459 | 155.5774 | 85.0735 | 122.8071 | 144.7073 | 286.1628 | 485.854 | 765.8796 | 1051.1902 | 1027.9653 |  |  | 6074.1571 | dtherms | 6072.7068 | MMbtu
| Natural Gas (thms) |  |  | * | 1113 | 1377 | 1217 | 1159 | 768 | 995 | 1220 | 1167 | 1255 | 854 | 764 |  |  | 11889 | therms | 1188.6161 | MMbtu | 16548.5064 | Mmbtu
| Water (CCF) |  |  | 190 | 345 | 335 | 335 | 170 | 132 | 134 | 265 | 345 | 180 | 110 | 85 |  |  | 2626 | CCF | 1964248 | gallons
| Electricity Cost ($) |  |  | 11869.3297 | 12326.4196 | 12317.5411 | 11245.7164 | 10330.5491 | 11879.7587 | 11638.1722 | 12285.3463 | 12241.1613 | 11439.8203 | 10535.8005 | 10716.2273 |  |  | 138825.8424 |  | 138825.8424
| Steam Costs ($) |  |  | 2427.25 | 2748.0892 | 4210.8234 | 6871.1312 | 7518.8956 | 9913.5 | 11443.5409 | 8699.3094 | 4877.7166 | 3874.3853 | 3580.4895 | 3260.1911 |  |  | 69425.3223 |  | 69425.3223
| Chilled Water ($) |  |  | 14054.4 | 11879.5395 | 6823.3816 | 2240.3145 | 1225.0582 | 1768.4227 | 2083.7848 | 4120.7449 | 6996.2977 | 11028.6668 | 15137.1387 | 14802.7008 |  |  | 92160.45 |  | 92160.45
| Natural Gas ($) |  |  | * | 1035.18 | 1269.93 | 1120.15 | 959.37 | 626.92 | 832.28 | 941.44 | 888.38 | 960.95 | 679.15 | 604.79 |  |  | 9918.54 |  | 9918.54
|  |  |  | * No Data. Aug-14 data is from 13.14 Data. | [15 empty] | 300411.6147
47 | UNCG - Spartan Village 1 - Lee | [16 empty] | UNCG - Spartan Village 1
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 51376 | 67310 | 58835 | 64810 | 75371 | 86365 | 94925 | 71614 | 63508 | 55389 | 80642 | 87080 |  |  | 857225 | kwhs | 2925.7089 | MMbtu
| Nat Gas (Therms) |  |  | 122 | 465 | 460 | 564 | 569 | 412 | 750 | 742 | 752 | 541 | 452 | 451 |  |  | 6280 | therms | 627.8501 | MMbtu | 3553.559 | Mmbtu
| Water (gallons) |  |  | 33660 | 183582 | 231343 | 259701 | 96269 | 129105 | 210448 | 204478 | 164179 | 179105 | 126865 | 123134 |  |  | 1941869 | gallons | 1941869 | gallons
| Electricity Cost ($) |  |  | 4890.97 | 5840.79 | 5375.91 | 5689.39 | 6337.58 | 7133.63 | 7684.1 | 6134.2 | 5636.92 | 5138.84 | 6688.05 | 7073.86 |  |  | 73624.24 |  | 73624.24
| Nat Gas Costs ($) |  |  | 135.02 | 448.45 | 443.88 | 542.06 | 537.58 | 387.14 | 635.13 | 575.35 | 225.89 | 372.43 | 331.84 | 361.68 |  |  | 4996.45 |  | 4996.45
78620.69
48 | UNCG - Spartan Village 3 - Haywood | [16 empty] | UNCG - Spartan Village 3
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 32916 | 41890 | 33239 | 39016 | 55321 | 64709 | 66639 | 46837 | 38846 | 26591 | 29312 | 34899 |  |  | 510215 | kwhs | 1741.3638 | MMbtu
| Nat Gas (Therms) |  |  | 195 | 257 | 254 | 309 | 327 | 229 | 434 | 428 | 423 | 282 | 71 | 82 |  |  | 3291 | therms | 329.0214 | MMbtu | 2070.3852 | Mmbtu
| Water (gallons) |  |  | 2992 | 79105 | 94776 | 99254 | 60448 | 23880 | 94776 | 83582 | 70895 | 80597 | 5970 | 2985 |  |  | 699260 | gallons | 699260 | gallons
| Electricity Cost ($) |  |  | 3046.58 | 3579.35 | 3084.03 | 3404.64 | 4401.52 | 5053.94 | 5576.07 | 3900.93 | 3410.71 | 2658.9 | 2825.83 | 3164.91 |  |  | 44107.41 |  | 44107.41
| Nat Gas Costs ($) |  |  | 201.73 | 258.38 | 255.63 | 307.63 | 327.09 | 225.63 | 379.2 | 349.65 | 137.79 | 205.6 | 71.97 | 85.02 |  |  | 2805.32 |  | 2805.32
46912.73
49 | UNCG - Spartan Village 4 - | [16 empty] | UNCG - Spartan Village 4
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 39247 | 53964 | 44200 | 51002 | 59338 | 66087 | 69213 | 54411 | 47866 | 35981 | 41225 | 47471 |  |  | 610005 | kwhs | 2081.9471 | MMbtu
| Nat Gas (Therms) |  |  | 119 | 446 | 430 | 492 | 489 | 287 | 622 | 638 | 602 | 423 | 141 | 143 |  |  | 4832 | therms | 483.0846 | MMbtu | 2565.0317 | Mmbtu
| Water (gallons) |  |  | 14212 | 132835 | 169403 | 176119 | 100000 | 63433 | 151492 | 131343 | 117164 | 132836 | 6716 | 6716 |  |  | 1202269 | gallons | 1202269 | gallons
| Electricity Cost ($) |  |  | 3731.22 | 4611.42 | 4057.39 | 4431.6 | 4943.22 | 5372.3 | 5576.07 | 4662.3 | 4260.77 | 3531.66 | 3853.37 | 4231.56 |  |  | 53262.88 |  | 53262.88
| Nat Gas Costs ($) |  |  | 132.27 | 431.08 | 416.47 | 475.87 | 465.31 | 276.82 | 532.81 | 559.6 | 165.82 | 296.22 | 119.71 | 130.75 |  |  | 4002.73 |  | 4002.73
57265.61
50 | WSSU - Martin-Schexnider Residence Hall | [16 empty] | WSSU - Martin-Schexnider Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 35938 | 46762 | 37721 | 36427 | 24293 | 35096 | 43165 | 34692 | 33878.5 | 76057 | 34350 | 36421 |  |  | 474800.5 | kwhs | 1620.4941 | MMbtu
| Steam (Nat Gas in Therms) |  |  | 2677.1659 | 2899.5896 | 3466.3925 | 5159.5902 | 5422.6173 | 6142.155 | 5344.6529 | 4528.4219 | 3344.9209 | 2286.5695 | 2190.9892 | 2216.687 |  |  | 45679.7519 | therms | 4566.8846 | MMbtu
| Chilled Water (kwh) |  |  | 64682.0727 | 56065.2532 | 41505.466 | 93036.8572 | 11363.958 | 10098.7457 | 7670.1532 | 25610.6753 | 37475.347 | 94189.1686 | 54205.3596 | 64801.2653 |  |  | 560704.3219 | kwhs | 1913.6839 | MMbtu | 8101.0625 | Mmbtu
| Water (CCF) |  |  | 413.55 | 280.07 | 318.23 | 242.52 | 88.36 | 207.83 | 214.64 | 214.64 | 312.91 | 296.62 | 271.37 | 206.02 |  |  | 3066.76 | CCF | 2293936.48 | gallons
| Electricity Cost ($) |  |  | 2551.598 | 3320.102 | 2678.191 | 2586.317 | 1724.803 | 2491.816 | 3064.715 | 2463.132 | 2405.3735 | 5400.047 | 2438.85 | 2585.891 |  |  | 33710.8355 |  | 33710.8355
| Steam ($) |  |  | 1338.7669 | 1488.6497 | 1778.3043 | 2402.1122 | 2833.8962 | 2525.6362 | 2254.4134 | 1734.2537 | 1245.3891 | 852.2417 | 888.3962 | 888.8536 |  |  | 20230.9131 |  | 20230.9131
| Chilled Water($) |  |  | 4592.4272 | 3980.633 | 2946.8881 | 6605.6169 | 806.841 | 717.0109 | 544.5809 | 1818.3579 | 2660.7496 | 6687.431 | 3848.5805 | 4600.8898 |  |  | 39810.0069 |  | 39810.0069
93751.7555
51 | Cape Fear Community College - Union Station | [16 empty] | Cape Fear Community College - Union Station
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 305600 | 314800 | 358400 | 294000 | 258000 | 249600 | 259200 | 238800 | 271200 | 294400 | 280800 | 375600 |  |  |  | 3500400 | kwhs | 11946.8652 | MMbtu
| Nat Gas (Therms) |  | 8429 | 10007 | 8611 | 9993 | 12959 | 13657 | 18058 | 17223 | 18541 | 17712 | 14560 | 12141 |  |  |  | 161891 | therms | 16185.2348 | MMbtu | 28132.1 | MMbtu
| Water (CCF) |  | 883 |  | 979 |  | 735 |  | 389 |  | 374 |  | 648 |  |  |  |  | 4008 | CF | 2997984 | gallons
| Electricity Cost ($) |  | 25329.44 | 25902.54 | 29201.72 | 24706.17 | 21704.77 | 21436.37 | 22465.23 | 20920.68 | 18876.21 | 20686.22 | 20190.83 | 27216.1 |  |  |  | 278636.28 |  | 278636.28
| Nat Gas Costs ($) |  | 7725.7 | 9167.63 | 7892.01 | 9154.83 | 11663.41 | 12254.9 | 16567.86 | 14394.54 | 14545 | 11064.88 | 9343.94 | 7802.47 |  |  |  | 131577.17 |  | 131577.17
410213.45
52 | ECU - Smith-Williams Center | [16 empty] | ECU - Smith-Williams Center
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | No Data. | [15 empty] | 0 | kwhs | 0 | MMbtu
| Steam (lbs) | No Data. | [15 empty] | 0 | lbs | 0 | MMbtu
| Nat Gas (Therms) | No Data. | [15 empty] | 0 | therms | 0 | MMbtu | 0 | MMbtu
| Water (gallons) | No Data. | [15 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | No Data. | [15 empty] | 0 |  | 0
| Steam Costs ($) | No Data. | [15 empty] | 0 |  | 0
| Nat Gas Costs ($) | No Data. | [15 empty] | 0 |  | 0
0
53 | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 2 - Plaza Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 46652.0081 | 50276.001 | 50750 | 48268.9819 | 43969.0247 | 49542.9688 | 45736.0229 | 45281.0059 | 46723.999 | 44320.0073 | 41210.9985 | 43963.9893 |  |  | 556695.0073 | kwhs | 1900.0001 | MMbtu
| Steam (1000lbs) |  |  | 47.4 | 53.31 | 81.17 | 175.52 | 213.94 | 263 | 289 | 277 | 133 | 82 | 44.9199 | 80.7803 |  |  | 1741.0402 | 1000lbs | 1741.0402 | MMbtu
| Chilled Water (Dtherms) |  |  | 420.556 | 355.394 | 202.365 | 50 | 30 | 27 | 26 | 75 | 160 | 296 | 445.9106 | 458.3418 |  |  | 2546.5675 | dtherms | 2545.9595 | MMbtu | 6186.9998 | Mmbtu
| Water (CCF) |  |  | 189 | 228 | 169 | 169 | 87 | 126 | 158 | 116 | 141 | 103 | 253 | 163 |  |  | 1902 | CCF | 1422696 | gallons
| Electricity Cost ($) |  |  | 4058.7247 | 4374.0121 | 4415.25 | 4199.4014 | 3825.3051 | 4310.2383 | 3979.034 | 3939.4475 | 4064.9879 | 3855.8406 | 3585.3569 | 3824.8671 |  |  | 48432.4656 |  | 48432.4656
| Steam Costs ($) |  |  | 657.438 | 739.4097 | 1125.8279 | 2434.4624 | 2967.3478 | 3647.81 | 4008.43 | 3841.99 | 1844.71 | 1137.34 | 623.0395 | 1120.4226 |  |  | 24148.2279 |  | 24148.2279
| Chilled Water ($) |  |  | 6056.0068 | 5117.6742 | 2914.0559 | 720 | 432 | 388.8 | 374.4 | 1080 | 2304 | 4262.4 | 6421.1133 | 6600.1219 |  |  | 36670.5721 |  | 36670.5721
109251.2656
54 | UNCG - Spartan Village Building 2 | [16 empty] | UNCG - Spartan Village Building 2
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 61500 | 75600 | 60000 | 63600 | 72900 | 84900 | 90300 | 72900 | 64200 | 44400 | 48413 | 54581 |  |  | 793294 | kwhs | 2707.5124 | MMbtu
| Nat Gas (Therms) |  |  | 195 | 411 | 417 | 512 | 535 | 301 | 699 | 668 | 671 | 451 | 69 | 84 |  |  | 5013 | therms | 501.1803 | MMbtu | 3208.6927 | Mmbtu
| Water (gallons) |  |  | 91044 | 160448 | 199253 | 163433 | 167164 | 35075 | 200746 | 178358 | 161194 | 176866 | 2985 | 5224 |  |  | 1541790 | gallons | 1541790 | gallons
| Electricity Cost ($) |  |  | 5691.85 | 6551.91 | 5631.65 | 5800.03 | 6388.19 | 6954.93 | 7266.4 | 6214.87 | 5689.1 | 4492.54 | 4735.06 | 5102.08 |  |  | 70518.61 |  | 70518.61
| Nat Gas Costs ($) |  |  | 201.73 | 399.1 | 404.58 | 494.25 | 506.87 | 289.18 | 595.63 | 526.58 | 197.99 | 314.48 | 70.6 | 86.52 |  |  | 4087.51 |  | 4087.51
74606.12
55 | UNCC - PORTAL | [16 empty] | UNCC - PORTAL
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 67060 | 80854 | 88878 | 82852 | 74272 | 75624 | 76572 | 62522 | 70095 | 71961 | 72570 | 75048 |  |  |  | 898308 | kwhs | 3065.9252 | MMbtu
| Nat Gas (Therms) |  | 32 | 85 | 164 | 170 | 354 | 480 | 294 | 102 | 119 | 265 | 141 | 38 |  |  |  | 2244 | therms | 224.3464 | MMbtu
| Chilled Water mmBTU |  | 544 | 488 | 603 | 322 | 87 | 55 | 56 | 61 | 164 | 325 | 569 | 695 |  |  |  | 3969 | MMbtu | 3969 | MMbtu
| Hot Water mmBTU |  | 243 | 143 | 258 | 333 | 391 | 504 | 444 | 442 | 364 | 319 | 285 | 241 |  |  |  | 3967 | MMbtu | 3967 | MMbtu | 11226.2716 | Mmbtu
| Water (CF) |  | 250 | 280 | 267 | 271 | 941 | 219 | 6598 | 995 | 1537 | 1457 | 266 | 150 |  |  |  | 13231 | CF | 98967.88 | gallons
| Electricity Cost ($) |  | 4672.9179 | 5787.3895 | 6154.4706 | 5082.8138 | 4271.785 | 4354.5178 | 4270.501 | 3524.4855 | 4099.7922 | 4016.0056 | 4078.8614 | 4710.3295 |  |  |  | 55023.8698 |  | 55023.8698
| Nat Gas Costs ($) |  | 49.33 | 94.59 | 162.05 | 167.18 | 322.47 | 429.92 | 257.95 | 97.56 | 97.08 | 27.93 | 106.43 | 47.38 |  |  |  | 1859.87 |  | 1859.87
| Chilled Water ($) |  | 2562.2344 | 1153.7824 | 1991.8849 | 1433.5291 | 1261.4652 | 456.4407 | 222.6938 | 429.608 | 530.7505 | 1051.7921 | 2928.2109 | 4172.5599 |  |  |  | 18194.952 |  | 18194.952
| Hot Water ($) |  | 1816.2705 | 894.648 | 1692.6703 | 1680.1662 | 1930.0289 | 2023.7921 | 1835.846 | 1509.1533 | 1474.2816 | 793.4043 | 1086.9956 | 1320.1149 |  |  |  | 18057.3717 |  | 18057.3717
93136.0634
56 | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 3 - Innovation Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 42294.9982 | 42239.9902 | 42876.0071 | 41388.0005 | 39213.9893 | 42395.9961 | 40167.9993 | 40778.9917 | 41736.9995 | 38388.0005 | 39009.0332 | 40076.9653 |  |  | 490566.9708 | kwhs | 1674.3051 | MMbtu
| Steam (1000lbs) |  |  | 47.88 | 48.07 | 95.13 | 203 | 250 | 300 | 317 | 193 | 102 | 62 | 40.6799 | 97.9099 |  |  | 1756.6698 | 1000lbs | 1756.6698 | MMbtu
| Chilled Water (Dtherms) |  |  | 346.395 | 260.7379 | 131.948 | 27 | 18 | 12 | 13 | 44 | 109 | 228 | 389.7739 | 480.8262 |  |  | 2060.681 | dtherms | 2060.189 | MMbtu | 5491.1639 | Mmbtu
| Water (CCF) |  |  | 83 | 117 | 89 | 88 | 53 | 78 | 97 | 69 | 85 | 65 | 59 | 40 |  |  | 923 | CCF | 690404 | gallons
| Electricity Cost ($) |  |  | 3679.6648 | 3674.8792 | 3730.2126 | 3600.756 | 3411.6171 | 3688.4517 | 3494.6159 | 3547.7723 | 3631.119 | 3339.756 | 3393.7859 | 3486.696 |  |  | 42679.3265 |  | 42679.3265
| Steam Costs ($) |  |  | 664.0956 | 666.7309 | 1319.4531 | 2815.61 | 3467.5 | 4161 | 4396.79 | 2676.91 | 1414.74 | 859.94 | 564.2307 | 1358.0101 |  |  | 24365.0105 |  | 24365.0105
| Chilled Water ($) |  |  | 4988.0883 | 3754.626 | 1900.0512 | 388.8 | 259.2 | 172.8 | 187.2 | 633.6 | 1569.6 | 3283.2 | 5612.7445 | 6923.8969 |  |  | 29673.8068 |  | 29673.8068
96718.1438
57 | WSSU - Hill Hall Renovation | [16 empty] | WSSU - Hill Hall Renovation
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 35080.3333 | 35080.3333 | 38443 | 30014.9 | 27611 | 39068 | 36579 | 42433 | 39707.1 | 82201 | 119513 | 36485 |  |  | 562215.6667 | kwhs | 1918.8421 | MMbtu
| Steam (Nat Gas in therms) |  |  | 1823.9535 | 1975.4907 | 2361.6536 | 3515.2294 | 3694.4298 | 4184.6509 | 3641.3126 | 3085.2144 | 2278.895 | 1557.84 | 1492.7212 | 1510.2291 |  |  | 31121.6201 | therms | 3111.419 | MMbtu
| Chilled Water (kwh) |  |  | 44067.9034 | 38197.2633 | 28277.6786 | 63386.0212 | 7742.2659 | 6880.2765 | 5225.6762 | 17448.556 | 25531.9581 | 64171.0911 | 36930.1175 | 44149.1093 |  |  | 382007.917 | kwhs | 1303.793 | MMbtu | 6334.0541 | Mmbtu
| Water (CCF) |  |  | 23.1 | 29.7 | 24.1 | 23.8 | 10.4 | 24.7 | 23.75 | 23.75 | 27.3 | 12.5 | 11.9 | 11.4 |  |  | 246.4 | CCF | 184307.2 | gallons
| Electricity Cost ($) |  |  | 2490.7037 | 2490.7037 | 2729.453 | 2131.0579 | 1960.381 | 2773.828 | 2597.109 | 3012.743 | 2819.2041 | 5836.271 | 8485.423 | 2590.435 |  |  | 39917.3123 |  | 39917.3123
| Steam ($) |  |  | 912.102 | 1014.2172 | 1211.5589 | 1636.5593 | 1930.7338 | 1720.7162 | 1535.9321 | 1181.5472 | 848.4837 | 580.6324 | 605.2644 | 605.576 |  |  | 13783.3234 |  | 13783.3234
| Chilled Water ($) |  |  | 3128.8211 | 2712.0057 | 2007.7152 | 4500.4075 | 549.7009 | 488.4996 | 371.023 | 1238.8475 | 1812.769 | 4556.1475 | 2622.0383 | 3134.5868 |  |  | 27122.5621 |  | 27122.5621
80823.1978
58 | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 5 - Grove Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 31869.0033 | 33372.9858 | 31777.0081 | 29947.998 | 26263.0005 | 26403.0151 | 37998.0102 | 30710.0015 | 32835.9947 | 30931.0074 | 29625.9995 | 29063.0035 |  |  | 370797.0276 | kwhs | 1265.5303 | MMbtu
| Steam (1000lbs) |  |  | 44.53 | 57.48 | 80.06 | 141 | 161 | 181 | 211 | 143 | 86 | 57 | 52.5199 | 45.83 |  |  | 1260.42 | 1000lbs | 1260.42 | MMbtu
| Chilled Water (Dtherms) |  |  | 277.8053 | 226.1169 | 108.401 | 26 | 16 | 10.4919 | 11.4021 | 42 | 98 | 194 | 325.252 | 337.261 |  |  | 1672.7302 | dtherms | 1672.3309 | MMbtu | 4198.2811 | Mmbtu
| Water (CCF) |  |  | 38 | 61 | 584 | 55 | 23 | 39 | 53 | 39 | 54 | 28 | 24 | 15 |  |  | 1013 | CCF | 757724 | gallons
| Electricity Cost ($) |  |  | 2772.6033 | 2903.4498 | 2764.5997 | 2605.4758 | 2284.881 | 2297.0623 | 3305.8269 | 2671.7701 | 2856.7315 | 2690.9976 | 2577.462 | 2528.4813 |  |  | 32259.3414 |  | 32259.3414
| Steam Costs ($) |  |  | 617.6311 | 797.2476 | 1110.4322 | 1955.67 | 2233.07 | 2510.47 | 2926.57 | 1983.41 | 1192.82 | 790.59 | 728.4515 | 635.6623 |  |  | 17482.0247 |  | 17482.0247
| Chilled Water ($) |  |  | 4000.3963 | 3256.084 | 1560.9744 | 374.4 | 230.4 | 151.084 | 164.1902 | 604.8 | 1411.2 | 2793.6 | 4683.6281 | 4856.5582 |  |  | 24087.3152 |  | 24087.3152
73828.6814
59 | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall | [16 empty] | NCSU - Wolf Ridge at Centennial Bldg 4 - Valley Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 33423.0042 | 31042.0074 | 30466.0034 | 30248.9929 | 29457.0007 | 21910.9802 | 19745.0256 | 30752.9907 | 29761.9934 | 32721.0083 | 33212.0056 | 37614.0137 |  |  | 360355.0262 | kwhs | 1229.8917 | MMbtu
| Steam (1000lbs) |  |  | 54.9 | 47.38 | 115.62 | 288 | 176 | 223.438 | 263.6458 | 169.7242 | 89.1718 | 61.8641 | 59.496 | 53.658 |  |  | 1602.898 | 1000lbs | 1602.898 | MMbtu
| Chilled Water (Dtherms) |  |  | 268.7059 | 202.573 | 91.814 | 17 | 13 | 10.25 | 7 | 40 | 89 | 209 | 335.6401 | 345.447 |  |  | 1629.43 | dtherms | 1629.041 | MMbtu | 4461.8307 | Mmbtu
| Water (CCF) |  |  | 38 | 20 | 10 | 8 | 4 | 5 | 12 | 22 | 9 | 21 | 29 | 36 |  |  | 214 | CCF | 160072 | gallons
| Electricity Cost ($) |  |  | 2907.8014 | 2700.6546 | 2650.5423 | 2631.6624 | 2562.7591 | 1906.2553 | 1717.8172 | 2675.5102 | 2589.2934 | 2846.7277 | 2889.4445 | 3272.4192 |  |  | 31350.8873 |  | 31350.8873
| Steam Costs ($) |  |  | 761.463 | 657.1606 | 1603.6494 | 3994.56 | 2441.12 | 3099.0851 | 3656.7678 | 2354.0752 | 1236.8134 | 858.0556 | 825.209 | 744.2362 |  |  | 22232.1953 |  | 22232.1953
| Chilled Water ($) |  |  | 3869.3646 | 2917.0512 | 1322.1211 | 244.8 | 187.2 | 147.6 | 100.8 | 576 | 1281.6 | 3009.6 | 4833.218 | 4974.4371 |  |  | 23463.7919 |  | 23463.7919
77046.8744
60 | Guilford Technical Community College - Aviation Center III Building | [16 empty] | Guilford Technical Community College - Aviation Center III Building
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 53143 | 79571 | 52336 | 33992 | 30329 | 21414 | 27379 | 27186 | 26404 | 27688 | 32815 | 42452 |  |  |  | 454709 | kwhs | 1551.9218 | MMbtu
| Nat Gas (Therms) |  | 513 | 1105 | 711 | 503 | 622 | 728 | 1157 | 1520 | 577 | 224 | 127 | 115 |  |  |  | 7902 | therms | 790.0113 | MMbtu | 2341.9332 | Mmbtu
| Water (gallons) |  | 18700 | 3740 | 1496 | 2992 | 3740 | 1496 | 4488 | 2244 | 3740 | 4488 | 2992 | 1496 |  |  |  | 51612 | gallons | 51612 | gallons
| Electricity Cost ($) |  | 4660.51 | 6598.56 | 4412.95 | 2911.75 | 2687.21 | 2275.17 | 2696.42 | 2684.14 | 2634.35 | 2716.1 | 3082.43 | 3659.7 |  |  |  | 41019.29 |  | 41019.29
| Nat Gas Costs ($) |  | 1735.9 | 2786.52 | 983.91 | 715.33 | 850.03 | 992.45 | 1438.3 | 1739.67 | 556.76 | 234.97 | 127 | 109.79 |  |  |  | 12270.63 |  | 12270.63
53289.92
61 | UNCC - Martin Residence Hall | [16 empty] | UNCC - Martin Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | * Jul-15 | 2015-08-01 | 2015-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 133266 | 235067 | 119199 | 159826 | 141346 | 131900 | 130400 | 140609 | 162851 | 169035 | 164385 | 148825.5 |  |  | 1836709.5 | kwhs | 6268.6895 | MMbtu
| Nat Gas (Therms) |  |  | 1540 | 1999 | 2358 | 3838 | 4971 | 7224 | 6667 | 4630 | 3142 | 2264 | 1800 | 1670 |  |  | 42103 | therms | 4209.2948 | MMbtu | 10477.9843 | Mmbtu
| Water (CF) |  |  | 41013 | 60816 | 64336 | 48323 | 26879 | 32356 | 33538 | 35992 | 42514 | 21915 | 26888 | 33950.5 |  |  | 468520.5 | CF | 3504533.34 | gallons
| Electricity Cost ($) |  |  | 9538.9498 | 16277.5147 | 7312.6336 | 9192.459 | 8138.8669 | 7356.2017 | 7350.8991 | 8224.0913 | 9088.4025 | 9500.7626 | 10317.497 | 9928.2234 |  |  | 112226.5015 |  | 112226.5015
| Nat Gas Costs ($) |  |  | 1430.74 | 1850.17 | 2178.21 | 3509.17 | 4543.78 | 6226.92 | 5308.41 | 3149.3 | 2172.99 | 1196.68 | 1224.09 | 1327.415 |  |  | 34117.875 |  | 34117.875
[15 empty] | *estimated by averaging Jun-15 and Aug-14. |  |  |  |  | 146344.3765

## 14.15 Raw Meter
1 | ASU - Cone Residence Hall Renovation
| Building | 2014-2015 Elec Usage | 2014-2015 Steam Usage | 2014-2015 Water Usage | 2014-2015 Elec Expense | 2014-2015 Steam Expense | 2014-2015 Water & Sewer Expense
| Cone | 906743.12 | 1882789.4 | 1690223 | 79884.2058 | 39542.64 | 20136.2923
2 | UNCC - Prospector Hall Renovation |  | 06-07223-01A
|  | 2015-07-14 | 2015-08-14 | 2015-09-14 | 2015-10-14 | 2015-11-14 | 2015-12-14 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15
Consumption
| Electric (KWH) | 58248 | 73841 | 64140 | 48489 | 74632 | 62878 | 23850 | 52081 | 57328 | 60797 | 63751 | 47783
| Nat Gas (Therms) | 1544 | 1757 | 2603 | 2191 | 3206 | 2740 | 3855 | 4075 | 3194 | 2249 | 1506 | 1021
| Water (CF) | 11520 | 14330 | 19980 | 19980 | 14640 | 6652 | 13970 | 10420 | 12020 | 13120 | 7020 | 6172
| CHW BTUX10^6 | [5 empty] | 0 | 0 | 42 | 120 | 489 | 688 | 860
Costs $
| Electric | 4058.8745 | 5285.4111 | 4441.4562 | 2974.7086 | 4292.4906 | 3620.5883 | 1330.1396 | 2935.9063 | 3353.0621 | 3392.9642 | 3583.1817 | 2999.0629
| Nat Gas | 1340.56 | 1522.46 | 2244.94 | 1893.09 | 2743.17 | 2319.95 | 3115.79 | 3040.89 | 2037.24 | 0 | 683.8 | 703.85
| Water | 818.8423 | 1040.7772 | 1453.9053 | 1524.0292 | 1155.0368 | 564.5186 | 1294.6639 | 868.9753 | 990.0796 | 1027.5858 | 534.847 | 449.0675
| CHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252.9689 | 721.5973 | 2609.416 | 2878.4579 | 4181.2329
Metered data is whole building data - not just the partial renovation
| Metered data includes process loads | [7 empty] | All of April & some of May gas bills have credits from PNG for fuel over billing
Started recording chill water usage in Dec
Prospector Gets Chill Water from adjacent building - Costs are assumed to be the same as RUP1 CHW costs
3 | UNCC - Miltimore Residence Hall |  | 05-06656-01A
|  | 2015-07-14 | 2015-08-14 | 2015-09-14 | 2015-10-14 | 2015-11-14 | 2015-12-14 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15
Consumption
| Electric (KWH) | 180200 | 207501 | 167465 | 164770 | 135799 | 119754 | 138887 | 118400 | 123371 | 153382 | 149826 | 158234
| Nat Gas (Therms) | 3393 | 3385 | 3936 | 2828 | 5568 | 6248 | 8297 | 6995 | 5056 | 3796 | 3010 | 2465
| Water (CF) | 59844 | 55320 | 72656 | 53662 | 45363 | 25194 | 49194 | 68476 | 52813 | 63623 | 42380 | 46370
Costs $
| Electric | 12556.812 | 14852.5627 | 11596.3278 | 10108.3284 | 7810.5361 | 6895.5744 | 7745.874 | 6674.436 | 7215.8565 | 8559.9557 | 8421.1037 | 9931.4343
| Nat Gas | 2919.59 | 2912.76 | 3383.3 | 2522.48 | 4747.98 | 5331.75 | 6680.67 | 5204.12 | 3212.06 | 0 | 1127.55 | 1668.19
| Water | 4253.7149 | 4017.8504 | 5287.0341 | 4093.2159 | 3578.9572 | 2138.0761 | 4559.0333 | 5710.5523 | 4350.1724 | 4983.0862 | 3228.8914 | 3373.8266
4 | Agency - Building Name: NCCU Nursing Building
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14
| Electricity (KWhs) |  |  |  | 101656 | 83961 | 61140 | 51127 | 58131 | 51184 | 66259 | 77568 | 74983 | 71978 | 85948 | 66815
| Steam (lbs) | [8 empty] | 434277 | 646511 | 375662 | 311334 | 186544 | 176351 | 180505
Chilled Water (Dtherms)
| Natural Gas (Therms) |  |  |  | 42 | 46 | 43 | 47 | 27 | 45 | 49 | 48 | 44 | 44 | 42 | 36
| Water (CCF) |  |  |  | 15613 | 8642 | 2880 | 795 | 1141 | 1906 | 4043 | 8228 | 8130 | 13138 | 12157
| Electricity Cost ($) |  |  |  | 6269.63 | 5178.29 | 3770.81 | 3153.26 | 3585.23 | 3156.77 | 4086.52 | 4784.01 | 4624.58 | 4439.24 | 5300 | 4120
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) |  |  |  | 57.66 | 61.33 | 57.88 | 57.04 | 40.73 | 55.28 | 56.06 | 55.3 | 52.39 | 52.39 | 50.84 | 46.19
5 | Agency - Building Name: NCCU Chidley North Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14
| Electricity (KWhs) |  |  |  | 240288 | 181085 | 109864 | 71448 | 98048 | 80600 | 95216 | 127066 | 71760 | 85624 | 106024 | 82840
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) |  |  |  | 576 | 0 | 0 | 776 | 242 | 1458 | 1904 | 1379 | 1405 | 275 | 299 | 299
| Water (CCF) |  |  |  | 128629 | 64361 | 57810 | 34713 | 130637 | 44559 | 62488 | 58412 | 21227 | 120430 | 127683
| Electricity Cost ($) |  |  |  | 14819.76 | 11168.42 | 6775.15 | 4406.56 | 6047.11 | 4971.01 | 5872.45 | 7836.8 | 4425.8 | 5280.86 | 6539.03 | 5109.16
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) |  |  |  | 547.85 | 18.73 | 18.73 | 639.22 | 216.03 | 1153.16 | 1399.56 | 1012.81 | 1035.19 | 229.12 | 247.28 | 246.83
6 | Loudermilk Center of Excellence (375) |  |  | Aug 14 - Jul 15
Energy and Water Usage (Acct. #01012081)
| UTILITY | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
Consumption:
| ELECTRIC (kWhs) | 145460 | 148965 | 204667 | 174103 | 172559 | 153194 | 141867 | 174836 | 164868 | 156341 | 135067 | 174677
| STEAM (MLBS) | 734 | 629 | 594 | 485 | 540 | 730 | 769 | 943 | 454 | 437 | 484 | 525
| CHILLED WATER (Ton-Hrs.) | 166476 | 172661 | 142526 | 56574 | 11017 | 1310 | 1023 | 16 | 7543 | 34751 | 92308 | 151339
| NATURAL GAS (Therms) | 130 | 247 | 474 | 428 | 332 | 405 | 161 | 384 | 325 | 398 | 339 | 187
| WATER (kGal) | 132 | 183 | 184 | 133 | 97 | 29 | 82 | 67 | 102 | 122 | 309 | 431
| SEWER (kGal) | 132 | 183 | 184 | 133 | 96 | 29 | 82 | 67 | 102 | 122 | 309 | 431
| STORMWATER (ksf) | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
Costs:
| ELECTRIC ($) | 9833.1 | 10025.34 | 11911.62 | 10132.79 | 8610.69 | 8839.29 | 9334.85 | 8741.8 | 9562.34 | 9130.31 | 8104.02 | 9554.83
| STEAM ($) | 8245.83 | 7066.25 | 6673.06 | 5448.54 | 6066.41 | 8200.89 | 8639.02 | 10593.76 | 5100.28 | 4909.3 | 5437.3 | 5897.9
| CHILLED WATER ($) | 15482.27 | 16057.47 | 13254.92 | 5261.38 | 1024.58 | 121.83 | 95.14 | 1.49 | 701.5 | 3231.84 | 8584.64 | 14543.68
| NATURAL GAS ($) | 112.64 | 214.02 | 410.71 | 326.06 | 252.92 | 308.89 | 114.67 | 273.09 | 232.38 | 284.57 | 221.94 | 122.04
| WATER ($) | 1096.92 | 1520.73 | 1529.04 | 581.21 | 511.28 | 126.73 | 358.34 | 292.79 | 445.74 | 533.14 | 2567.79 | 3581.61
| SEWER ($) | 897.6 | 1244.4 | 1251.2 | 904.4 | 788.8 | 197.2 | 557.6 | 455.6 | 693.6 | 829.6 | 2101.2 | 2930.8
| STORMWATER ($) | 307.8 | 307.8 | 307.8 | 307.8 | 307.8 | 307.8 | 307.8 | 307.8 | 307.8 | 307.8 | 307.8 | 324
7 | NC Department of Agriculture & Consumer Services - Western Ag Center - Davis Events Center
| Utility | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | Annual Total
| Electricity Usage (KWhs) | 20500 | 56120 | 47040 | 67800 | 53240 | 29280 | 33400 | 33000 | 49720 | 32800 | 32200 | 38120 | 493220
| Water Usage (gallons) | 19448 | 77792 | 70312 | 72556 | 55352 | 23188 | 276760 | 58344 | 74800 | 103972 | 61336 | 19448 | 913308
| Natural Gas Therms | 166 | 114 | 96 | 302 | 1418 | 2056 | 2162 | 4388 | 6471 | 1096 | 455 | 157 | 18881
| Elecricity Cost ($) | 3902.46 | 5467.49 | 4715.73 | 6518.57 | 5215.84 | 3423.54 | 3835 | 3806.76 | 5078.95 | 3791.55 | 3745.89 | 4210.33 | 53712.11
| Water-Sewer Costs ($) | 958.51 | 1539.61 | 1465.11 | 1487.464 | 1316.11 | 995.76 | 3521.31 | 1345.91 | 1509.81 | 1815.36 | 1375.71 | 973.54 | 18304.204
| Natural Gas ($) | 172.77 | 124.42 | 107.73 | 298.43 | 1144.35 | 1520.27 | 1596.99 | 3182.58 | 4314.88 | 761.75 | 342.83 | 129.76 | 13696.76
Notes: Davis Arena & Virginia Boone Bldg on same meter
8 | NCSU - Student Health Center Addition and Renovation
| Utility |  | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 |  | Total | Units
| Electric (kWh) |  | 65168.6 | 69007.9963 | 66408.9966 | 61874.0082 | 66953.0029 | 64019.9961 | 70717 | 67461 | 68776 | 65683 | 66473 |  | 732542.6001 | kwh
| Chilled Water (Dtherms) |  | 689.78 | 315.52 | 181.24 | 92.17 | 124.6 | 125.84 | 259.69 | 409.01 | 656.94 | 953.24 | 1018.01 |  | 4826.04 | dthrms
| Steam (1,000 lbs) |  | 261 | 343 | 574 | 591 | 733 | 741 | 566 | 414 | 360 | 329 | 315 |  | 5227 | 1000 lbs
| Water (CCF) |  | 51.6854 | 57.1786 | 50.4731 | 37.1814 | 45.695 | 47.513 | 54.3797 | 54.2509 | 44 | 37.3868 | 43.3814 |  | 523.1252 | CCF
| Electric Cost ($) |  | 5669.6682 | 6003.6957 | 5777.5827 | 5383.0387 | 5824.9113 | 5569.7397 | 6152.379 | 5869.107 | 5983.512 | 5714.421 | 5783.151 |  | 63731.2062 | $
| Chilled Water Cost ($) |  | 9932.832 | 4543.488 | 2609.856 | 1327.248 | 1794.24 | 1812.096 | 3739.536 | 5889.744 | 9459.936 | 13726.656 | 13956.9171 |  | 68792.5491 | $
| Steam Cost ($) |  | 3620.07 | 4757.41 | 7961.38 | 8197.17 | 10166.71 | 10277.67 | 7850.42 | 5742.18 | 4993.2 | 4563.23 | 4542.3 |  | 72671.74 | $
| Water Cost ($) |  | 406.2472 | 449.4239 | 396.7182 | 292.246 | 359.1625 | 373.452 | 427.4248 | 426.4119 | 345.84 | 293.86 | 284.1483 |  | 4054.9347 | $
9 | UNC - ECSU - Gilchrist Education & Psychology Building
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14
| Electricity (KWhs) |  | 52224 | 55872 | 56832 | 50880 | 50112 | 50112 | 55872 | 64320 | 60480 | 43584 | 45312 | 43392 | 57984
| Steam (lbs) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water (Dtherms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas (Therms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) |  | 529.61 | 938.42 | 896.81 | 817.2 | 782 | 252.56 | 365.83 | 232.19 | 411.89 | 625.06 | 1124.08 | 563.73 | 770.37
| Electricity Cost ($) |  | 6467.55 | 6834.85 | 7158.93 | 5973.78 | 5956.18 | 6277.44 | 6560.56 | 7264.31 | 6987.37 | 5296.43 | 5969.07 | 5830.6 | 6660.13
| Steam Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | NC Department of Agriculture & Consumer Services - Southeastern Ag Center - Multi-purpose Pavilion
| Utility | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | Annual Total
| Electricity Usage (KWhs) | 2360 | 2600 | 3180 | 4320 | 4320 | 2520 | 2640 | 3040 | 1800 | 3360 | 4680 | 4360 | 39180
| Water Usage (gallons) | 30470 | 53490 | 40810 | 62630 | N/A | 53920 | 60016 | 68914 | 15210 | 5800 | 77670 | 125840 | 594770
| Natural Gas Therms | 23 | 22 | 28 | 29 | 1458 | 1195 | 1162 | 1264 | 654 | 33 | 29 | 87 | 5984
| Elecricity Cost ($) | 483.83 | 606.25 | 552.75 | 1045.67 | 856.41 | 510.76 | 570.39 | 599.9 | 405.87 | 852.49 | 890.21 | 823.7 | 8198.23
| Water-Sewer Costs ($) | 250.44 | 177.76 | 177.76 | 202.15 | 305.78 | 229.58 | 274.54 | 302.73 | 251.68 | 229.96 | 342.36 | 396.39 | 3141.13
| Natural Gas ($) | 44.55 | 43.65 | 45.91 | 38.45 | 1242.38 | 1045.21 | 926.42 | 133.03 | 947.21 | 41.76 | 39.37 | 82.67 | 4630
11 | UNCC - EPIC |  | 2014-09-01: 07-07078-02A
|  | 2015-07-14 | 2015-08-14 | 2015-09-14 | 2015-10-14 | 2015-11-14 | 2015-12-14 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15
Consumption
| Electric (KWH) | 415523 | 415560 | 377745 | 440404 | 435530 | 448250 | 455310 | 414430 | 456675 | 448690 | 453830 | 419430
| Nat Gas (Therms) | 182 | 131 | 142 | 531 | 2083 | 2611 | 979 | 805 | 689 | 1625 | 679 | 166
| Water (CF) | 4963 | 4932 | 7234 | 8982 | 9050 | 7383 | 6346 | 6550 | 10382 | 10707 | 5507 | 6686
| CHW BTUX10^6 | 2555 | 18112 | 9894 | 1481 | 640 | 685 | 456 | 486 | 1141 | 1269 | 2273 | 2539
| HW BTUX10^6 | 205 | 345 | 333 | 498 | 624 | 891 | 735 | 858 | 665 | 416 | 439 | 274
Costs $
| Electric | 28954.7402 | 29745.066 | 26157.435 | 27017.954 | 25049.6894 | 25810.7556 | 25393.1175 | 23362.2171 | 26710.5013 | 25040.5298 | 25507.9191 | 26325.1986
| Nat Gas | 177.43 | 133.87 | 143.27 | 475.47 | 1790 | 2240.91 | 807.69 | 618.37 | 456.72 | 353.28 | 428.59 | 132.86
| Water | 352.7703 | 358.2075 | 526.4039 | 685.1266 | 714.0084 | 626.5546 | 588.1129 | 546.2369 | 855.1586 | 838.5946 | 419.573 | 486.4655
| CHW | 12034.0236 | 42822.3508 | 32682.7684 | 6593.3437 | 9279.7439 | 5684.7613 | 1813.3641 | 3422.7781 | 3692.5994 | 4106.8437 | 11697.4049 | 15243.352
| HW | 1531.35 | 2577.15 | 2487.51 | 3720.06 | 4661.28 | 6655.77 | 5490.45 | 6409.26 | 4967.55 | 3107.52 | 3279.33 | 2046.78
12 | NCDVA - NC State Veterans Home- Black Mountain
| Utility | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-15 | 2015-04-01 | 2015-05-01 | 2015-06-01
| Electricity Usage (KWhs) | 155700 | 168900 | 173700 | 171400 | 202200 | 153000 | 136900 | 161700 | 160600 | 155100 | 146400 | 119900 | 166900 | 178000
| Gas usage therms | 1850 | 1648 | 1898 | 1719 | 1966 | 2064 | 2100 | 2587 | 2456 | 2408 | 2827 | 2648 | 2193 | 2219
| Water Usage (gallons) | 294732 | 307449 | 248353 | 276779 | 301464 | 261070 | 308945 | 267054 | 365049 | 323906 | 362057 | 300716 | 387490 | 306701
| Elecricity Cost ($) | 12282.69 | 13313.71 | 13329.99 | 13121.53 | 15209.35 | 11819.42 | 10615.14 | 12709.56 | 12463.86 | 11939.57 | 12358.56 | 10139.3 | 13776.57 | 14631.04
| Gas cost ($) | 1608.08 | 1474.33 | 1688.33 | 1533.74 | 1746.79 | 1820.97 | 1674.26 | 2036.34 | 1937.51 | 1784.45 | 2024.33 | 1905.52 | 1587.16 | 1605.37
| Water-Sewer Costs ($) | 3575.88 | 3699.98 | 3184.04 | 3467.14 | 3712.99 | 3310.69 | 3787.49 | 3370.29 | 4346.24 | 3936.49 | 4316.44 | 3705.54 | 4584.74 | 3765.14
13 | Pitt CC - Russell Classroom Building 08-07329-02A
| Utility | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (KWhs) | 60672 | 58872 | 52676 | 41202 | 38303 | 41087 | 39456 | 46614 | 46234 | 50102 | 62826 | 63061
| Steam (lbs) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Chilled Water (Dtherms) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Natural Gas (Therms) | 1.28 | 2.15 | 5.26 | 12.87 | 11.43 | 17.67 | 21.27 | 7.99 | 5.36 | 1.97 | 0.65 | 0.68
| Water (CCF) | 56.1 | 61.9 | 48.4 | 38.7 | 15.5 | 58 | 46.4 | 48.4 | 40.6 | 13.5 | 15.5 | 11.57
| Electricity Cost ($) | 7985 | 8153 | 6422 | 5048 | 4407 | 5081 | 4047 | 5306 | 6614 | 6576 | 8175 | 8246
| Steam Costs ($) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Chilled Water Costs ($) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Natural Gas Costs ($) | 185.13 | 292.33 | 670.57 | 1463 | 1313 | 1963 | 2337 | 955 | 653 | 248 | 104 | 107.07
14 | Bailey Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (kWhs) | 25182 | 25236 | 27426 | 22419 | 22341 | 22298 | 21389 | 19621 | 26668 | 17996 | 18459 | 18557
| Lighting submeter (kWhs) | 5267 | 6102 | 6740 | 5436 | 4842 | 5467 | 5780 | 5218 | 6594 | 4296 | 4114 | 4039
| Mechanical submeter (kWhs) | 13086 | 13595 | 14568 | 12276 | 14038 | 11750 | 10157 | 9732 | 14700 | 11516 | 12099 | 12217
| Calculated plug load (kWhs) | 6829 | 5539 | 6118 | 4707 | 3461 | 5081 | 5452 | 4671 | 5374 | 2184 | 2246 | 2301
| Steam Usage (lbs) | 9290 | 11270 | 17980 | 109290 | 109540 | 116840 | 148210 | 29320 | 14890 | 3930 | 7960 | 5030
| Water Usage (gallons) | 47500 | 62200 | 51000 | 44300 | 19000 | 42600 | 52200 | 45200 | 52300 | 15200 | 21300 | 10800
| Chilled water (ton-hrs) | 28341 | 23764 | 17575 | 10474 | 9538 | 6006 | 4472 | 8930 | 14827 | 18012 | 24276 | 20523
| Electricity Cost ($) | 1708.09 | 1806.6 | 2051.07 | 1351.18 | 1372.39 | 1346.37 | 1259.52 | 1219.31 | 1543.43 | 1041.53 | 1211.79 | 1074
| Water Cost ($) | 337.09 | 441.62 | 362.1 | 314.53 | 134 | 302.46 | 370.62 | 320.92 | 371.33 | 107.92 | 151.23 | 76.68
| Steam Cost ($) | 72.58 | 88.05 | 140.48 | 853.89 | 855.85 | 912.88 | 1157.98 | 229.08 | 116.34 | 30.71 | 62.2 | 39.3
15 | UNCG - Coit Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (kWhs) | 22964 | 22523 | 21812 | 17902 | 17834 | 18258 | 19041 | 18479 | 22274 | 14896 | 14053 | 15739
| Lighting submeter (kWhs) | 5164 | 5947 | 6461 | 5361 | 4862 | 5245 | 5393 | 5168 | 6433 | 4094 | 3545 | 4197
| Mechanical submeter (kWhs) | 11442 | 11241 | 9615 | 7992 | 9835 | 8494 | 8621 | 8875 | 10485 | 8814 | 8575 | 9488
| Calculated plug load (kWhs) | 6358 | 5335 | 5736 | 4549 | 3137 | 4519 | 5027 | 4436 | 5356 | 1988 | 1933 | 2054
| Steam Usage (lbs) | 7620 | 7720 | 8150 | 8080 | 4490 | 2190 | 1990 | 3970 | 8830 | 3510 | 1760 | 2150
| Water Usage (gallons) | 32800 | 53900 | 47600 | 42600 | 13800 | 42500 | 59300 | 85000 | 62700 | 18900 | 2400 | 4400
| Chilled water (ton-hrs) | 23987 | 18955 | 15893 | 12571 | 11494 | 11455 | 10102 | 12252 | 13560 | 14870 | 16792 | 18529
| Electricity Cost ($) | 1557.65 | 1612.38 | 1631.22 | 1078.95 | 1095.53 | 1102.43 | 1121.25 | 1148.42 | 1289.13 | 862.12 | 922.54 | 910.9
| Water Costs ($) | 232.77 | 382.69 | 337.96 | 302.46 | 97.98 | 301.75 | 421.03 | 604.92 | 445.17 | 134.19 | 17.04 | 31.24
| Steam Cost ($) | 59.53 | 60.32 | 63.68 | 63.13 | 35.08 | 17.11 | 15.55 | 31.02 | 68.98 | 27.42 | 13.75 | 16.8
16 | UNCG - Cotten Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (kWhs) | 24495 | 25411 | 26518 | 22416 | 21871 | 21506 | 22596 | 22466 | 27110 | 18572 | 18579 | 19064
| Lighting submeter (kWhs) | 5248 | 6628 | 6524 | 5545 | 4582 | 5393 | 5658 | 5321 | 6803 | 4193 | 4111 | 3928
| Mechanical submeter (KWhs) | 12546 | 13599 | 14504 | 12105 | 13811 | 11400 | 11772 | 9732 | 14737 | 11888 | 12146 | 12947
| Calculated plug load (kWhs) | 6701 | 5184 | 5490 | 4766 | 3478 | 4713 | 5166 | 7413 | 5570 | 2491 | 2322 | 2189
| Steam Usage (lbs) | 17550 | 12732 | 9979 | 38280 | 39810 | 43710 | 41860 | 36410 | 31070 | 24400 | 25670 | 12939
| Water Usage (gallons) | 38200 | 59400 | 53900 | 55900 | 14100 | 51700 | 53200 | 71000 | 58900 | 18000 | 37200 | 14300
| Chilled water (ton-hrs) | 20417 | 18544 | 13312 | 7876 | 6822 | 5563 | 3988 | 8682 | 11908 | 12609 | 16985 | 19231
| Electricity Cost ($) | 1661.49 | 1819.12 | 1983.16 | 1351 | 1343.52 | 1298.55 | 1330.59 | 1396.2 | 1569.01 | 1074.87 | 1219.67 | 1103.35
| Water Costs ($) | 271.09 | 421.74 | 384.69 | 396.89 | 100.11 | 367.07 | 377.72 | 504.1 | 418.19 | 127.8 | 264.12 | 101.53
| Steam Cost ($) | 137.11 | 99.48 | 77.97 | 299.08 | 311.04 | 341.51 | 327.06 | 284.47 | 242.75 | 190.64 | 200.56 | 101.09
17 | UNCG - Gray Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (kWhs) | 24553 | 23453 | 25958 | 21316 | 21784 | 19256 | 19638 | 21133 | 24940 | 18405 | 18933 | 19003
| Lighting submeter (kWhs) | 5304 | 5852 | 6387 | 5464 | 5258 | 5419 | 5604 | 5181 | 6861 | 4711 | 4335 | 4484
| Mechanical submeter (kWhs) | 12579 | 12273 | 13712 | 11149 | 13218 | 9146 | 8771 | 9864 | 12436 | 11389 | 12156 | 12202
| Calculated plug load (kWhs) | 6670 | 5328 | 5859 | 4703 | 3308 | 4691 | 5263 | 6088 | 5643 | 2305 | 2442 | 2317
| Steam Usage (lbs) | 8350 | 10920 | 8520 | 10990 | 49270 | 36690 | 88540 | 57360 | 46910 | 12810 | 4460 | 2990
| Water Usage (gallons) | 39200 | 61200 | 55100 | 52400 | 18000 | 45300 | 62400 | 56700 | 58900 | 16100 | 21400 | 10100
| Chilled water (ton-hrs) | 18369 | 15458 | 8036 | 2089 | 680 | 963 | 1142 | 3540 | 6454 | 10571 | 17518 | 18910
| Electricity Cost ($) | 1665.43 | 1678.95 | 1941.28 | 1284.71 | 1338.18 | 1162.69 | 1185.75 | 1276.02 | 1443.42 | 1065.2 | 1242.9 | 1099.82
| Water Costs ($) | 278.19 | 434.52 | 391.21 | 372.04 | 127.8 | 321.63 | 443.04 | 402.57 | 418.19 | 114.31 | 151.94 | 71.71
| Steam Cost ($) | 65.24 | 85.32 | 66.57 | 85.86 | 384.95 | 286.66 | 691.77 | 448.82 | 366.51 | 100.08 | 34.85 | 23.36
18 | UNCG - Hinshaw Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (kWhs) | 31432 | 30723 | 33436 | 27231 | 28302 | 27151 | 25452 | 25746 | 31702 | 22632 | 22465 | 21988
| Lighting submeter (kWhs) | 5665 | 6598 | 6505 | 5960 | 4554 | 6162 | 6040 | 6076 | 6448 | 5201 | 4055 | 4178
| Mechanical submeter (kWhs) | 14860 | 15432 | 16432 | 13128 | 14633 | 12527 | 10462 | 11688 | 15088 | 12512 | 13565 | 12675
| Calculated plug load (kWhs) | 10907 | 8693 | 10499 | 8143 | 9115 | 8462 | 8950 | 7982 | 10166 | 4914 | 4845 | 5135
| Steam Usage (lbs) | 16160 | 19240 | 21050 | 25010 | 19710 | 42370 | 61490 | 30000 | 22580 | 8290 | 6020 | 4390
| Water Usage (gallons) | 46000 | 61400 | 61600 | 57900 | 35600 | 61800 | 62700 | 55300 | 58800 | 15500 | 14800 | 4700
| Chilled water (ton-hrs) | 24184 | 20787 | 13290 | 7131 | 5843 | 4637 | 3069 | 8030 | 12007 | 14003 | 19467 | 18284
| Electricity Cost ($) | 2132.3 | 2199.4 | 2500.53 | 1641.2 | 1738.57 | 1639.39 | 1498.77 | 1600.04 | 1834.78 | 1309.85 | 1474.77 | 1272.57
| Water Costs ($) | 326.44 | 435 | 437.36 | 411.09 | 252.76 | 438.78 | 445.17 | 392.63 | 403.28 | 110.05 | 105.08 | 33.37
| Steam Cost ($) | 126.25 | 150.32 | 164.45 | 195.39 | 153.98 | 331.01 | 480.39 | 234.37 | 176.41 | 64.76 | 47.03 | 34.3
19 | UNCG - Jamison Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (kWhs) | 25698 | 25723 | 28328 | 23316 | 22429 | 22776 | 23748 | 23139 | 27712 | 19002 | 16703 | 18376
| Lighting submeter (kWhs) | 5479 | 6473 | 7051 | 5909 | 4680 | 5580 | 6080 | 5489 | 6979 | 4209 | 3187 | 3756
| Mechanical submeter (kWhs) | 13390 | 14090 | 15662 | 12706 | 14178 | 12429 | 12385 | 12865 | 15196 | 12089 | 11541 | 12480
| Calculated plug load (kWhs) | 6829 | 5160 | 5615 | 4701 | 3571 | 4767 | 5283 | 4785 | 5537 | 2704 | 1975 | 2140
| Steam Usage (lbs) | 7090 | 10100 | 12230 | 27480 | 22220 | 70310 | 73750 | 24070 | 6400 | 1960 | 1840 | 1690
| Water Usage (gallons) | 43600 | 56000 | 54000 | 54600 | 22000 | 50200 | 75900 | 71900 | 69200 | 19300 | 2900 | 5600
| Chilled water (ton-hrs) | 90670 | 87000 | 58900 | 36370 | 34920 | 29920 | 20640 | 26810 | 33920 | 38460 | 19340 | 18740
| Electricity Cost ($) | 1743.09 | 1841.46 | 2118.52 | 1405.24 | 1377.8 | 1375.23 | 1398.43 | 1438.02 | 1603.85 | 1099.76 | 1096.51 | 1063.53
| Water Costs ($) | 309.41 | 397.6 | 383.4 | 387.66 | 156.2 | 356.42 | 538.89 | 510.49 | 491.32 | 137.03 | 20.59 | 39.76
| Steam Cost ($) | 55.39 | 78.91 | 95.55 | 214.69 | 173.59 | 549.3 | 576.17 | 188.05 | 50 | 15.32 | 14.38 | 13.2
20 | UNCG - Shaw Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-14 | 2014-11-01 | 2014-12-14 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15 | 2015-07-15
| Electricity (kWhs) | 44245 | 47094 | 53020 | 44629 | 46112 | 44102 | 44996 | 44367 | 51886 | 38929 | 38420 | 37831
| Lighting submeter (kWhs) | 11199 | 12266 | 13742 | 11872 | 11653 | 11636 | 12100 | 11429 | 13725 | 9826 | 10353 | 9561
| Mechanical submeter (kWhs) | 14506 | 17453 | 19949 | 16619 | 18980 | 16386 | 16245 | 16838 | 19282 | 16561 | 16279 | 16772
| Calculated plug load (kWhs) | 18540 | 17375 | 19328 | 16138 | 15479 | 16080 | 16651 | 16100 | 18879 | 12542 | 11788 | 11498
| Steam Usage (lbs) | 12360 | 88760 | 98090 | 73480 | 75810 | 96760 | 97940 | 50950 | 8810 | 10820 | 2980 | 1480
| Water Usage (gallons) | 66600 | 101200 | 97600 | 95900 | 48700 | 87300 | 121900 | 101400 | 109300 | 38200 | 42400 | 15300
| Chilled water (ton-hrs) | 55574 | 50017 | 37051 | 30148 | 29138 | 27972 | 21820 | 26412 | 29447 | 37054 | 46880 | 47976
| Electricity Cost ($) | 3001.13 | 3371.37 | 3965.13 | 2689.77 | 2832.63 | 2662.91 | 2649.64 | 2757.28 | 3002.94 | 2253.05 | 2522.18 | 2189.5
| Water Costs ($) | 472.63 | 718.82 | 692.96 | 680.89 | 345.77 | 619.83 | 865.49 | 719.94 | 776.03 | 271.22 | 301.04 | 108.63
| Steam Cost ($) | 96.56 | 693.5 | 766.3 | 574.1 | 592.2 | 755.9 | 765.1 | 398.1 | 68.83 | 84.53 | 23.28 | 11.56
21 | WCU - Harrill Residence Hall
| Utility | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | Total
| Electricity (kWh) | 60739 | 78737 | 86657 | 75803 | 77415 | 51474 | 78316 | 82982 | 73544 | 74750 | 59697 | 56519 | 856633
| Electricity Cost ($) | 4405.3389 | 5802.8382 | 6285.4055 | 4442.0558 | 4660.383 | 3237.7146 | 4612.8124 | 4622.0974 | 4383.2224 | 4440.15 | 3540.0321 | 4238.925 | 54670.9753
| Water (Gallons) | 14690 | 114850 | 226300 | 198250 | 167200 | 79360 | 144200 | 197810 | 167900 | 180230 | 55320 | 7730 | 1553840
| Water Cost ($) | 45.539 | 356.035 | 701.53 | 614.575 | 518.32 | 246.016 | 447.02 | 613.211 | 520.49 | 558.713 | 171.492 | 23.963 | 4816.904
22 | UNCP - Health Science Building
| Utility | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | Total
| Electricity Usage (KWhs) | 124350 | 124506 | 157696 | 138410 | 115773 | 107197 | 96118 | 110983 | 90056 | 131594 | 122952 | 119384 | 1439019
| Electricity Cost | 10042.506 | 10055.1046 | 12735.529 | 11177.9916 | 9349.8275 | 8657.2297 | 7762.4897 | 8962.9871 | 7272.9226 | 10627.5314 | 9929.6035 | 9641.4518 | 116215.1744
| Natural Gas (Therms) | 878 | 1123 | 1488 | 1741 | 1756 | 2813 | 2829 | 3202 | 3083 | 2150 | 1769 | 1707 | 24539
| Natural Gas Cost | 352.6048 | 450.9968 | 597.5808 | 699.1856 | 705.2096 | 1129.7008 | 1136.1264 | 1285.9232 | 1238.1328 | 863.44 | 710.4304 | 685.5312 | 9854.8624
| Natural Gas Transportation Cost | 152.5964 | 195.1774 | 258.6144 | 302.5858 | 305.1928 | 488.8994 | 491.6802 | 556.5076 | 535.8254 | 373.67 | 307.4522 | 296.6766 | 4264.8782
| Total Natural Gas Charges | 505.2012 | 646.1742 | 856.1952 | 1001.7714 | 1010.4024 | 1618.6002 | 1627.8066 | 1842.4308 | 1773.9582 | 1237.11 | 1017.8826 | 982.2078 | 14119.7406
| Water Usage (Gallons) | 147700 | 141500 | 131000 | 67100 | 31250 | 18300 | 9750 | 10120 | 26800 | 50000 | 94225 | 120500 | 848245
| Water Cost | 4181.387 | 4005.865 | 3708.61 | 1899.601 | 884.6875 | 518.073 | 276.0225 | 286.4972 | 758.708 | 1415.5 | 2667.5097 | 3411.355 | 24013.816
The water usage has been estimated based on normal cooling tower evaperation and additional building water usage per month. We will be replacing the borken meter soon.
23 | FSU, Renaissance Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14
| Electricity (KWhs) | n/a |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Steam (lbs)
Chilled Water (Dtherms)
Natural Gas (Therms)
| Water (CCF) |  |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Electricity Cost ($) |  |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Steam Costs ($)
Chilled Water Costs ($)
Natural Gas Costs ($)
24 | UNCA - Overlook Residence Hall
25 | UNC - ECSU - VIKING TOWER
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14
| Electricity (KWhs) |  | 46151 | 49957 | 57090 | 57474 | 52506 | 46523 | 49953 | 50798 | 50829 | 54029 | 50270 | 42143 | 40760
| Steam (lbs) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water (Dtherms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas (Therms) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) |  | 12794.38 | 33655.54 | 33655.54 | 41491.73 | 41491.73 | 32685.43 | 32685.43 | 35705.26 | 35705.26 | 29886.57 | 11631.36 | 12968.16 | 1278.38
| Electricity Cost ($) |  | 4859.69 | 5365.42 | 6102.94 | 6120.96 | 5691.63 | 5024.47 | 5280.02 | 5562.35 | 5403.08 | 5678.49 | 5308.49 | 4513.52 | 3713.22
| Steam Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chilled Water Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas Costs ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | [UNCW]TEACHING LAB | 2014-07-09 | 2014-08-09 | 2014-09-09 | 2014-10-09 | 2014-11-09 | 2014-12-09 | 2015-01-09 | 2015-02-09 | 2015-03-09 | 2015-04-09 | 2015-05-09 | 2015-06-09 | TOTAL YTD
ELECTRIC
| METER READING | 2370218 | 2448422 | 2541645 | 2651808 | 2761074 | 2883909 | 3019561 | 3138775 | 3244845 | 3348873 | 3430743 | 3512065 | -----
| PREVIOUS READING | 2269373 | 2370218 | 2448422 | 2541645 | 2651808 | 2761074 | 2883909 | 3019561 | 3138775 | 3244845 | 3348873 | 3430743 | -----
| CHANGE | 100845 | 78204 | 93223 | 110163 | 109266 | 122835 | 135652 | 119214 | 106070 | 104028 | 81870 | 81322 | -----
| KWH | 100845 | 78204 | 93223 | 110163 | 109266 | 122835 | 135652 | 119214 | 106070 | 104028 | 81870 | 81322 | 1242692
| COST/KWH | 0.0832 | 0.0816 | 0.0809 | 0.0724 | 0.0764 | 0.0768 | 0.0755 | 0.074 | 0.0751 | 0.0766 | 0.0744 | 0.0833 | 0.0772
| COST | 8390.3 | 6381.45 | 7541.74 | 7975.8 | 8347.92 | 9433.73 | 10241.73 | 8821.84 | 7965.86 | 7968.54 | 6091.13 | 6774.12 | 95934.16
WATER
| METER READING high | 737823 | 768831 | 813568 | 857088 | 891595 | 920592 | 953834 | 982581 | 1013187 | 1045293 | 1066106 | 1082486
| PREVIOUS READING | 708452 | 737823 | 768831 | 813568 | 857088 | 891595 | 920592 | 953834 | 982581 | 1013187 | 1045293 | 1066106
| CHANGE - GAL | 29371 | 31008 | 44737 | 43520 | 34507 | 28997 | 33242 | 28747 | 30606 | 32106 | 20813 | 16380
| METER READING low | 403760 | 433073 | 482013 | 532290 | 580666 | 619482 | 668825 | 719012 | 765656 | 812123 | 835739 | 857459
| PREVIOUS READING | 373144 | 403760 | 433073 | 482013 | 532290 | 580666 | 619482 | 668825 | 719012 | 765656 | 812123 | 835739
| CHANGE - GAL | 30616 | 29313 | 48940 | 50277 | 48376 | 38816 | 49343 | 50187 | 46644 | 46467 | 23616 | 21720
| TOTAL GALLONS | 59987 | 60321 | 93677 | 93797 | 82883 | 67813 | 82585 | 78934 | 77250 | 78573 | 44429 | 38100 | 858349
| COST/GAL | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.004 | 0.004 | 0.0041 | 0.0041 | 0.004 | 0.004
| COST | 233.95 | 235.25 | 365.34 | 365.81 | 323.24 | 264.47 | 322.08 | 315.74 | 309 | 322.15 | 182.16 | 152.4 | 3391.59
SEWAGE
| COST/GAL | 0.005 | 0.0054 | 0.0054 | 0.0053 | 0.0053 | 0.0057 | 0.0057 | 0.0046 | 0.0046 | 0.0063 | 0.0063 | 0.0042 | 0.0053
| COST | 299.94 | 325.73 | 505.86 | 497.12 | 439.28 | 386.53 | 470.73 | 363.1 | 355.35 | 495.01 | 279.9 | 160.02 | 4578.57
| HEATING HOT WATER IN MBTU | 185760.6375 | 182846.5875 | 177215.625 | 195564.5625 | 353043.625 | 353908.8375 | 422476.1375 | 495615.6625 | 317742.1625 | 195338.2 | 202179.6875 | 187366.975 | 3269058.7
| COST (Calculated by SF) | 1991.48 | 1230.58 | 1424.64 | 1651.44 | 2368.8 | 3424.12 | 2639.52 | 1759.68 | 2454.05 | 1963.63 | 1263.33 | 1306.98 | 23478.25
| CHILLED WATER IN TON-HRS | 184925.65 | 187610.7146 | 161643.9156 | 92603.6313 | 42747.975 | 24144.9792 | 20962.699 | 9090.1406 | 41390.976 | 73507.149 | 122285.9531 | 189833.1719 | 1150746.9552
| COST (Calculated by SF) | 16199.1 | 12131.34 | 11104.35 | 7007.04 | 3332.03 | 3691.6 | 1790.24 | 1136.79 | 4071.71 | 7374.51 | 8692.64 | 10220.77 | 86752.12
FUEL OIL
| GALLONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2014-07-09 to 2015-06-09
| TOTAL UTILITIES | 8924.19 | 6942.43 | 8412.94 | 8838.73 | 9110.44 | 10084.73 | 11034.54 | 9500.68 | 8630.21 | 8785.7 | 6553.19 | 115432.07 | 212249.85
= | bar: 2014-07-09 to 2015-06-09
| TRASH | 98.65 | 118.38 | 177.57 | 177.57 | 157.84 | 138.11 | 157.84 | 157.84 | 177.57 | 177.57 | 118.38 | 78.92 | 1736.24
| Jul usage 7/1/14-8/6/14 | 2014-07-09: Sep usage 9/2/14-10/1/14; 2014-09-09: Nov usage 11/3/14-12/1/14; 2014-11-09: Jan usage 1/5/15-2/3/15; 2015-01-09: Mar usage 3/2/15-4/1/15; 2015-03-09: May usage 5/4/15-6/1/15
| Aug usage 8/6/14-9/2/14 | 2014-07-09: Oct usage 10/1/14-11/3/14; 2014-09-09: Dec usage 12/1/14-1/5/15; 2014-11-09: Feb usage 2/3/15-3/2/15; 2015-01-09: Apr usage 4/1/15-5/4/15; 2015-03-09: Jun usage 6/1/15-6/30/15
27 | UNCA - Rhoades Hall Renovation
28 | ECU - Ledyard E. Ross Hall
| Utility | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (KWhs) | 190224.69 | 191998.96 | 188596.37 | 199761.09 | 187643.35 | 182052.4 | 193078.83 | 174839.47 | 188608.53 | 184840.94 | 192226.79 | 190063.41 | 195786.52
Steam (lbs)
| Chilled Water (tons) | 114762 | 107728 | 102847 | 80668 | 23516 | 22610 | 19803 | 15782 | 28793 | 54040 | 81870 | 115647
| Natural Gas (Therms) | 77.026 | 0 | 140.656 | 226.952 | 48.166 | 364.778 | 1599.237 | 661.081 | 274.463 | 189.666 | 1.835 | 60.306 | 52.323
| Heating Hot Water (MBTU) | 45222 | 51661 | 62621 | 134085 | 253880 | 186640 | 326266 | 492071 | 177387 | 11663 | 91807 | 60670
Water (CCF)
| Electricity Cost ($) | 17919.1658 | 18086.302 | 17765.7781 | 18817.4947 | 17676.0036 | 17149.3361 | 18188.0258 | 16469.8781 | 17766.9235 | 17412.0165 | 18107.7636 | 17903.9732 | 18443.0902
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 64.2532 | 0 | 117.3318 | 189.3178 | 40.1789 | 304.2889 | 1334.0444 | 551.4576 | 228.9503 | 158.2147 | 1.5307 | 50.3058 | 43.6466
29 | Gaston College-Lena Sue Beam Building
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14
| Electricity (KWhs) |  |  | 22640 | 30070 | 32560 | 22040 | 25200 | 25000 | 24040 | 25480 | 24280 | 23760 | 22840 | 21920
Steam (lbs)
Chilled Water (Dtherms)
Natural Gas (Therms)
| Water (gallons) |  |  | 2390 | 2465 | 4500 | 9480 | 8375 | 9463 | 7783 | 11358 | 13838 | 7592 | 3017 | 2421
| Electricity Cost ($) |  |  | 1803.9552 | 2809.7408 | 2521.772 | 1753.282 | 1884.708 | 1886.75 | 1765.4976 | 1967.5656 | 1781.4236 | 1796.9688 | 2093.7428 | 1878.8728
Steam Costs ($)
Chilled Water Costs ($)
Natural Gas Costs ($)
30 | NCSU - Hunt Library
| Utility |  | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 |  | Total | Units
| Electric (kWh) |  | 373878.1738 | 383077.8809 | 368188.9648 | 376896.9727 | 373953.125 | 339479.0039 | 379661.1328 | 373618.6523 | 372617.1875 | 363661.1328 | 370893.0664 |  | 4075925.293 | kwh
| Chilled Water (Dtherms) |  | 1005 | 768.36 | 928.36 | 802.45 | 905.56 | 790.99 | 345.92 | 529.256 | 850.312 | 1236.704 | 1341.952 |  | 9504.864 | dthrms
| Steam (1,000 lbs) |  | 358 | 405.2969 | 723.3047 | 785.5 | 1123.5 | 1139 | 760 | 405.5 | 334.5938 | 299.7969 | 290.8125 |  | 6625.3047 | 1000 lbs
| Water (CCF) |  | 394 | 300 | 156 | 113 | 104 | 156 | 135 | 183 | 202 | 310 | 206 |  | 2259 | CCF
| Electric Cost ($) |  | 31405.7666 | 32178.542 | 30927.873 | 32790.0366 | 32533.9219 | 29534.6733 | 33030.5186 | 32504.8228 | 32417.6953 | 31638.5186 | 32267.6968 |  | 351230.0654 | $
| Chilled Water Cost ($) |  | 14472 | 11064.384 | 13368.384 | 11555.28 | 13040.064 | 11390.256 | 4981.248 | 7621.2864 | 12244.4928 | 17808.5376 | 19324.1088 |  | 136870.0416 | $
| Steam Cost ($) |  | 4965.46 | 5621.4677 | 10032.236 | 10894.885 | 15582.945 | 15797.93 | 10541.2 | 5624.285 | 4640.8153 | 4158.1827 | 4033.5694 |  | 91892.976 | $
| Water Cost ($) |  | 3096.84 | 2358 | 1226.16 | 888.18 | 817.44 | 1226.16 | 1061.1 | 1438.38 | 1587.72 | 2436.6 | 1619.16 |  | 17755.74 | $
31 | UNCC - Judy W. Rose Football Center |  | 2014-09-01: 08-07833-02A
|  | 2015-07-14 | 2015-08-14 | 2015-09-14 | 2015-10-14 | 2015-11-14 | 2015-12-14 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15
Consumption
| Electric (KWH) | 173510 | 179450 | 178020 | 171290 | 152680 | 146750 | 119470 | 137560 | 127360 | 189280 | 180300 | 220612
| Nat Gas (Therms) | 1124 | 1391 | 1882 | 1911 | 2927 | 3666 | 5134 | 4366 | 3219 | 2360 | 1947 | 1394
| Water (CF) | 25696 | 28456 | 23223 | 16207 | 35992 | 14311 | 25039 | 6083 | 8008 | 20030 | 41158 | 55695
excludes irrigation
Costs $
| Electric | 12090.6351 | 12844.7206 | 12327.2223 | 10508.3181 | 8781.4538 | 8450.0355 | 6662.9675 | 7754.5221 | 7449.1694 | 10563.3544 | 10133.922 | 13846.5411
| Nat Gas | 981.88 | 1209.9 | 1629.21 | 1653.97 | 2506 | 3137.48 | 4142.24 | 3256.47 | 2053.01 | 0 | 955.55 | 952.95
| Water | 1826.4731 | 2066.7381 | 1689.892 | 1236.2333 | 2839.6232 | 1214.4958 | 2320.4788 | 507.2915 | 659.6137 | 1568.7914 | 3135.7884 | 4052.3026
Added field lights
32 | NCDVA - NC State Veterans Home- Kinston
| Utility | 2014-07-14 | 2014-08-14 | 2014-09-14 | 2014-10-14 | 2014-11-14 | 2014-12-14 | 2015-01-14 | 2015-02-14 | 2015-03-14 | 2015-04-14 | 2015-05-14 | 2015-06-14
| Electricity Usage (KWhs) | 192600 | 188400 | 206400 | 154200 | 170800 | 165800 | 167000 | 171800 | 170600 | 159800 | 187400 | 194000
| Steam Usage (lbs) Gas | 1161 | 1190 | 1404 | 1379 | 1566 | 1997 | 1716 | 1693 | 1835 | 1666 | 1780 | 1119
| Water Usage (gallons) | 201000 | 188100 | 237890 | 210120 | 231200 | 221300 | 255000 | 266000 | 263700 | 260400 | 313240 | 344100
| Elecricity Cost ($) | 15850.18 | 15546.24 | 16838.5 | 12947.88 | 13953.54 | 14184.53 | 14604.67 | 14923.05 | 14541.59 | 13785.35 | 16256.28 | 17028.24
| Steam Costs ($) Gas | 1096 | 1110.93 | 1306.47 | 1289.61 | 1446.05 | 1750.52 | 1413.28 | 1192.94 | 1187.67 | 1090.97 | 1284.46 | 1019.18
| Water-Sewer Costs ($) | 1381.57 | 1312.3 | 1579.67 | 1454.23 | 1543.74 | 1513.74 | 1676.55 | 1735.62 | 1718.27 | 1727.93 | 1984.3 | 2180.4
33 | Randolph | Community | 2014-09-01: College; 2014-11-01: 2014-2015; 2015-01-01: Continuing; 2015-02-01: Education; 2015-03-01: Industrial; 2015-04-01: Center
|  | July | August | September | October | November | December | January | February | March | April | May | June | Totals
| 83301 1830392826 CEIC 413 Ind. Pk. Ave. |  | 2015-01-01: Water
| Usage (CF) | 215 | 255 | 191 | 252 | 134 | 72 | 153 | 110 | 187 | 187 | 137 | 136 | 2029
| Days in Period | 34 | 30 | 29 | 33 | 29 | 32 | 30 | 29 | 29 | 31 | 30 | 33
| Water | 15.69 | 16.79 | 15.03 | 16.7 | 13.91 | 13.91 | 13.99 | 13.91 | 14.92 | 14.92 | 13.91 | 13.91 | 177.59
| Sewer | 19 | 20.13 | 18.33 | 20.05 | 17.18 | 17.18 | 17.26 | 17.18 | 18.22 | 18.22 | 17.18 | 17.18 | 217.11
| Total | 34.69 | 36.92 | 33.36 | 36.75 | 31.09 | 31.09 | 31.25 | 31.09 | 33.14 | 33.14 | 31.09 | 31.09 | 394.7
| 053 029 3190 TJ9935 CEIC |  | 2015-01-01: Power
| kWh Usage | 72500 | 64200 | 78300 | 57500 | 46600 | 42400 | 41300 | 45900 | 53900 | 56200 | 60400 | 81900 | 701100
| KW | 125 | 120 | 132 | 148 | 121 | 109 | 104 | 116 | 126 | 122 | 114 | 147 | 123.6667
| Days in period | 30 | 28 | 33 | 29 | 29 | 30 | 33 | 30 | 31 | 30 | 29 | 32
| Amount | 5040.51 | 4579.16 | 5420.69 | 4157.26 | 3400.43 | 3178.99 | 3122.74 | 3455.04 | 3949.99 | 4085.09 | 4235.71 | 5787.36 | 50412.97
| Lighting | 767.92 | 767.92 | 767.92 | 767.92 | 767.92 | 780.41 | 788.9 | 789.01 | 789.01 | 789.01 | 789.01 | 785.97 | 9350.92
| 7% Sales Tax | 406.59 | 374.3 | 433.2 | 344.76 | 291.78 | 277.16 | 273.81 | 297.08 | 331.73 | 341.19 | 351.73 | 460.13 | 4183.46
| Total Bill | 6215.02 | 5721.38 | 6621.81 | 5269.94 | 4460.13 | 4236.56 | 4185.45 | 4541.13 | 5070.73 | 5215.29 | 5376.45 | 7033.46 | 63947.35
| 1003287462001 859461 CEIC 413 Industrial Pk |  | 2015-01-01: Natural Gas; 2015-05-01: One time; 2015-06-01: April; 2015-07-01: May | June | Total
| Therms Used | 260 | 282 | 368 | 487 | 618 | 722 | 1268 | 1416 | 1106 | credit | 553 | 558 | 547 | 8185
| Amount | 244.04 | 262.83 | 336.27 | 445.84 | 540.51 | 631.85 | 1004.54 | 1039.15 | 667.55 |  | 353.14 | 361.82 | 405.28 | 6292.82
| State Sales Tax | 17.08 | 18.4 | 23.54 | 31.21 | 37.84 | 44.23 | 70.32 | 72.74 | 46.73 |  | 24.72 | 25.33 | 28.37 | 440.51
| Total Bill | 261.12 | 281.23 | 359.81 | 477.05 | 578.35 | 676.08 | 1074.86 | 1111.89 | 714.28 | -287.01 | 377.86 | 387.15 | 433.65 | 6446.32
34 | ASU - Plemmons Student Union Addition
| Building | 2014-2015 Elec Usage | 2014-09-01: 2014-2015 Steam Usage; 2014-10-01: 2014-2015 Water Usage; 2014-11-01: 2014-2015 Elec Expense; 2014-12-01: 2014-2015 Steam Expense; 2015-01-01: 2014-2015 Water & Sewer Expense
| Plemmons | 1893162.9599 | 2014-09-01: 6221463.6; 2014-10-01: 2355608.9999; 2014-11-01: 167507.1405; 2014-12-01: 130664.16; 2015-01-01: 30614.1709
35 | ASU - Summit Residence Hall and Appalachian Hall
| Building | 2014-2015 Elec Usage | 2014-09-01: 2014-2015 Steam Usage; 2014-10-01: 2014-2015 Water Usage; 2014-11-01: 2014-2015 Elec Expense; 2014-12-01: 2014-2015 Steam Expense; 2015-01-01: 2014-2015 Water & Sewer Expense
| Summit & Annex | 1120233.9199 | 2014-09-01: 4900925; 2014-10-01: 2745167.9999; 2014-11-01: 100287.1136; 2014-12-01: 119841.2; 2015-01-01: 32220.9368
36 | [UNCW] MARBIONIC FACILITY | 2014-07-09 | 2014-08-09 | 2014-09-09 | 2014-10-09 | 2014-11-09 | 2014-12-09 | 2015-01-09 | 2015-02-09 | 2015-03-09 | 2015-04-09 | 2015-05-09 | 2015-06-09 | TOTAL YTD
ELECTRIC
| KWH | 366800 | 369800 | 388600 | 286000 | 250000 | 216800 | 209000 | 204400 | 245800 | 272800 | 331200 | 384600 | 3525800
| DEMAND | 714 | 752 | 698 | 570 | 556 | 496 | 446 | 0 | 0 | 0 | 0 | 0 | 4232
| COST | 27540.53 | 28192.91 | 28393.57 | 20454.03 | 17877.04 | 16461.45 | 15806.64 | 14454.17 | 17442.59 | 19280.93 | 22945.36 | 29672.26 | 258521.48
GAS
| MCF | 628.1 | 614.7 | 683.6 | 765 | 874.8 | 1261.3 | 1183.4 | 1312.6 | 1061.3 | 918 | 809 | 759.9 | 10871.7
| COST | 5582.74 | 5467.48 | 6073.21 | 7190.09 | 8071.29 | 11596.27 | 10014.6 | 10147.68 | 2069.12 | 5485.29 | 4943.11 | 5428.9 | 82069.78
WATER
| METER READING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PREVIOUS READING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GAL CHANGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST/GAL | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.004 | 0.004 | 0.0041 | 0.004
| COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEWAGE
| COST/GAL | 0.005 | 0.0054 | 0.0054 | 0.0053 | 0.0053 | 0.0057 | 0.0057 | 0.0057 | 0.0046 | 0.0046 | 0.0063 | 0.0042
| COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2014-07-09 to 2015-06-09
| TOTAL UTILITIES | 33123.27 | 33660.39 | 34466.78 | 27644.12 | 25948.33 | 28057.72 | 25821.24 | 24601.85 | 19511.71 | 24766.22 | 27888.47 | 35101.16 | 340591.26
= | bar: 2014-07-09 to 2015-06-09
| TOTAL TRASH | 256.49 | 256.49 | 256.49 | 276.22 | 217.03 | 197.3 | 177.6 | 236.76 | 236.76 | 256.49 | 236.76 | 256.49 | 2860.88
MARBIONC - 25%
| ELECTRIC | 6885.13 | 7048.23 | 7098.39 | 5113.51 | 4469.26 | 4115.36 | 3951.66 | 3613.54 | 4360.65 | 4820.23 | 5736.34 | 7418.07 | 64630.37
| GAS | 1395.69 | 1366.87 | 1518.3 | 1797.52 | 2017.82 | 2899.07 | 2503.65 | 2536.92 | 517.28 | 1371.32 | 1235.78 | 1357.23 | 20517.45
| WATER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SEWER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2014-07-09 to 2015-06-09
| TOTAL UTILITIES | 8280.82 | 8415.1 | 8616.69 | 6911.03 | 6487.08 | 7014.43 | 6455.31 | 6150.46 | 4877.93 | 6191.55 | 6972.12 | 8775.3 | 85147.82
= | bar: 2014-07-09 to 2015-06-09
| TRASH | 64.12 | 64.12 | 64.12 | 69.06 | 54.26 | 49.33 | 44.4 | 59.19 | 59.19 | 64.12 | 59.19 | 64.12 | 715.22
UNCW - 75%
| ELECTRIC | 20655.4 | 21144.68 | 21295.18 | 15340.52 | 13407.78 | 12346.09 | 11854.98 | 10840.63 | 13081.94 | 14460.7 | 17209.02 | 22254.2 | 193891.12
| GAS | 4187.06 | 4100.61 | 4554.91 | 5392.57 | 6053.47 | 8697.2 | 7510.95 | 7610.76 | 1551.84 | 4113.97 | 3707.33 | 4071.68 | 61552.35
| WATER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SEWER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2014-07-09 to 2015-06-09
| TOTAL UTILITIES | 24842.46 | 25245.29 | 25850.09 | 20733.09 | 19461.25 | 21043.29 | 19365.93 | 18451.39 | 14633.78 | 18574.67 | 20916.35 | 26325.88 | 255443.47
= | bar: 2014-07-09 to 2015-06-09
| TRASH | 192.37 | 192.37 | 192.37 | 207.17 | 162.77 | 147.98 | 133.2 | 177.57 | 177.57 | 192.37 | 177.57 | 192.37 | 2145.68
No water or sewer charges. No water meter at the facility and awaiting information about how to charge for water and sewer.
Mar- under billed trash by $4.93
37 | The North Carolina State Bar-Electricity and Water Usage 5/2013 thru 9/2014
| Utility | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01
| Electricity Usage (KWhs) | 65400 | 62600 | 75400 | 72000 | 75000 | 83000 | 83000 | 87600 | 78000 | 87200 | 88200 | 72600 | 71200 | 77200 | 0
| Water Usage (CCF) | 16 | 27 | 23 | 22 | 21 | 19 | 17 | 15 | 20 | 59 | 17 | 21 | 24 | 37 | 0
0
| Elecricity Cost ($) | 5628.77 | 5526.73 | 6463.28 | 6206.95 | 6454.92 | 7033.84 | 7257.95 | 7902.84 | 7022.37 | 7897.36 | 7767.58 | 6580.62 | 6484.38 | 6845.41 | 0
| Water-Sewer Costs ($) | 197.87 | 304.75 | 276.69 | 269.68 | 262.66 | 248.63 | 234.6 | 220.57 | 255.65 | 529.22 | 234.6 | 262.66 | 283.71 | 402.57 | 0
38 | FSU, Science & Technology
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14
| Electricity (KWhs) | n/a |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Steam (lbs)
Chilled Water (Dtherms)
| Natural Gas (Therms) |  |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Water (CCF) |  |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Electricity Cost ($) |  |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) |  |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
39 | RECREATION CENTER | 2014-07-09 | 2014-08-09 | 2014-09-09 | 2014-10-09 | 2014-11-09 | 2014-12-09 | 2015-01-09 | 2015-02-09 | 2015-03-09 | 2015-04-09 | 2015-05-09 | 2015-06-09 | TOTAL YTD
ELECTRIC
| METER READING | 26340 | 26467 | 26621 | 26782 | 26905 | 27033 | 27164 | 27293 | 27426 | 27579 | 27704 | 27844
| PREVIOUS READING | 26173 | 26340 | 26467 | 26621 | 26782 | 26905 | 27033 | 27164 | 27293 | 27426 | 27579 | 27704
| CHANGE | 167 | 127 | 154 | 161 | 123 | 128 | 131 | 129 | 133 | 153 | 125 | 140
| KWH (CHANGE X1000) | 167000 | 127000 | 154000 | 161000 | 123000 | 128000 | 131000 | 129000 | 133000 | 153000 | 125000 | 140000 | 1671000
| COST/KWH | 0.0832 | 0.0816 | 0.0809 | 0.0724 | 0.0764 | 0.0768 | 0.0755 | 0.074 | 0.0751 | 0.0766 | 0.0744 | 0.0833 | 0.0776
| COST | 13894.4 | 10363.2 | 12458.6 | 11656.4 | 9397.2 | 9830.4 | 9890.5 | 9546 | 9988.3 | 11719.8 | 9300 | 11662 | 129706.8
GAS
| METER READING | 11764 | 11781 | 11802 | 11829 | 11850 | 11865 | 11892 | 11914 | 11935 | 11955 | 11973 | 11987
| PREVIOUS READING | 11744 | 11764 | 11781 | 11802 | 11829 | 11850 | 11865 | 11892 | 11914 | 11935 | 11955 | 11973
| MCF CHANGE | 20 | 17 | 21 | 27 | 21 | 15 | 27 | 22 | 21 | 20 | 18 | 14 | 243
| COST/MCF | 5.72 | 5.08 | 5.25 | 5.25 | 5.25 | 5.86 | 4.7 | 4.23 | 4.27 | 3.71 | 3.7 | 4.02 | 4.76
| COST | 114.4 | 86.36 | 110.25 | 141.75 | 110.25 | 87.9 | 126.9 | 93.06 | 89.67 | 74.2 | 66.6 | 56.28 | 1157.62
WATER
| METER READING | 32883900 | 32997800 | 33111300 | 33253800 | 33338900 | 33390800 | 33513200 | 33651600 | 33768000 | 33884500 | 33951000 | 34019600
| PREVIOUS READING | 32858900 | 32883900 | 32997800 | 33111300 | 33253800 | 33338900 | 33390800 | 33513200 | 33651600 | 33768000 | 33884500 | 33951000
| CHANGE IN GAL | 25000 | 113900 | 113500 | 142500 | 85100 | 51900 | 122400 | 138400 | 116400 | 116500 | 66500 | 68600 | #REF!
| COST/GAL | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.0039 | 0.004 | 0.004 | 0.0041 | 0.004 | #REF!
| COST | 97.5 | 444.21 | 442.65 | 555.75 | 331.89 | 202.41 | 477.36 | 539.76 | 465.6 | 466 | 272.65 | 274.4 | 4570.18
SEWAGE
| COST/GAL | 0.005 | 0.0054 | 0.0054 | 0.0053 | 0.0053 | 0.0057 | 0.0057 | 0.0057 | 0.0046 | 0.0046 | 0.0063 | 0.0042 | #REF!
| COST | 125 | 615.06 | 612.9 | 755.25 | 451.03 | 295.83 | 697.68 | 788.88 | 535.44 | 535.9 | 418.95 | 288.12 | 6120.04
| HEATING HOT WATER IN MBTU | 337499.136 | 367200.256 | 363899.904 | 314600.448 | 586699.776 | 638300.16 | 942000.128 | 738999.296 | 412600.32 | 359700.48 | 199000.064 | 119899.136 | 5380399.104
| COST (Calculated by SF) | 1618.07 | 999.85 | 1157.52 | 1341.8 | 1924.65 | 2782.09 | 2144.61 | 1429.74 | 1993.92 | 1595.45 | 1026.45 | 1061.92 | 19076.07
| CHILLED WATER IN TON-HRS | 173808.2987 | 174383.2747 | 148383.4027 | 86333.2693 | 35283.456 | 25399.9787 | 27408.2133 | 19616.768 | 66858.3253 | 91574.9547 | 108125.0133 | 150958.4213 | 1108133.376
| COST (Calculated by SF) | 13161.77 | 9856.71 | 9022.28 | 5693.22 | 2707.28 | 2999.43 | 1454.57 | 923.64 | 3308.26 | 5991.79 | 7062.77 | 8304.37 | 70486.09
FUEL OIL
| GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2014-07-09 to 2015-06-09
| TOTAL UTILITIES | 29011.14 | 22365.39 | 23804.2 | 20144.17 | 14922.3 | 16198.06 | 14791.62 | 13321.08 | 16381.19 | 20383.14 | 18147.42 | 21647.09 | 231116.8
= | bar: 2014-07-09 to 2015-06-09
TRASH
| BASIC SERVICE | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 512.98
| EXTRA PICK UP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.73 | 0 | 0 | 0 | 0 | 19.73
- | bar: 2014-07-09 to 2015-06-09
| TOTAL TRASH | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 39.46 | 59.19 | 59.19 | 39.46 | 39.46 | 39.46 | 532.71
= | bar: 2014-07-09 to 2015-06-09
Gross Sqft: 69644
Net Sqft: 65721
Jul. estimated water. Meter was under water and could not read.
Extra trash pick up on 2/28/15.
| Jul usage 7/1/14-8/6/14 | 2014-07-09: Sep usage 9/2/14-10/1/14; 2014-09-09: Nov usage 11/4/14-12/1/14; 2014-11-09: Jan usage 1/5/15-2/3/15; 2015-01-09: Mar usage 3/2/15-4/1/15; 2015-03-09: May usage 5/4/15-6/1/15
| Aug usage 8/6/14-9/2/14 | 2014-07-09: Oct usage 10/1/14-11/4/14; 2014-09-09: Dec usage 12/1/14-1/5/15; 2014-11-09: Feb usage 2/3/15-3/2/15; 2015-01-09: Apr usage 4/1/15-5/4/15; 2015-03-09: Jun usage 6/1/15-6/30/15
40 | Winston-Salem State University, D. J. Reeves Student Activities Center
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (KWhs) building meter |  |  | 90148 | 98775 | 95992 | 90698 | 65871 | 97417 | 90794 | 99425 | 95630 | 179402 | 67828 | 68049
| Steam from Central Plant (lbs) - natural gas therms |  |  | 4609.7442 | 4992.7299 | 5968.6934 | 8884.1676 | 9337.0674 | 10576.021 | 9202.8224 | 7797.375 | 5759.5345 | 3937.186 | 3772.6089 | 3816.8572
| Chilled Water from Central Plant (Dtherms) kwh |  |  | 111374.4222 | 96537.339 | 71467.2103 | 160197.8071 | 19567.3114 | 17388.7743 | 13207.0424 | 44098.373 | 64527.8505 | 162181.943 | 93334.8353 | 111579.6569
| Natural Gas (Therms) other than from central steam plant |  |  | 678 | 765 | 765 | 851 | 613 | 999 | 942 | 763 | 1071 | 1126 | 1400 | 2270
| Water (CCF) |  |  | 99.75 | 106 | 78.79 | 82.91 | 33.7 | 99.76 | 81.82 | 81.82 | 86.51 | 30.02 | 32.47 | 23.01
| Electricity Cost ($) building meter (kwh) x blended rate (.071/kwh) |  |  | 6400.508 | 7013.025 | 6815.432 | 6439.558 | 4676.841 | 6916.607 | 6446.374 | 7059.175 | 6789.73 | 12737.542 | 4815.788 | 4831.479
| Steam from Central Plant Cost ($) for Natural Gas |  |  | 2305.1888 | 2563.2683 | 3062.0171 | 4136.1361 | 4879.6141 | 4348.829 | 3881.8173 | 2986.1674 | 2144.4039 | 1467.4534 | 1529.7069 | 1530.4944
| Chilled Water from Central Plant Cost ($) kwh x $.071/wh |  |  | 7907.584 | 6854.1511 | 5074.1719 | 11374.0443 | 1389.2791 | 1234.603 | 937.7 | 3130.9845 | 4581.4774 | 11514.918 | 6626.7733 | 7922.1556
| Natural Gas Costs ($) other than from central steam. |  |  | 601.01 | 675.3 | 691.29 | 735.3 | 546.88 | 798.14 | 702.95 | 466.52 | 663.31 | 699.83 | 1002.98 | 1612.59
| Water Costs ($) |  |  | 684.94 | 727.79 | 587.92 | 617.22 | 332.09 | 725.2 | 619.235 | 619.235 | 639.47 | 297.89 | 297.76 | 246.91
41 | Haywood Community College - Creative Arts Building
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | Total
| Electricity (KWhs) | [15 empty] | 282277
| Steam (lbs) |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Chilled Water (Dtherms) |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Natural Gas (Therms) |  |  |  | 209 | 297 | 1409 | 1424 | 1364 | 1765 | 369 | 179 | 75 | 146 | 54 | 63 | 7354
| Water (Gallons) | [15 empty] | 154338
| Electricity Cost ($) | [15 empty] | 16996
| Steam Costs ($) |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Chilled Water Costs ($) |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Natural Gas Costs ($) |  |  |  | 211.96 | 278.95 | 1127.56 | 1139.7 | 1063.67 | 1294.34 | 300.27 | 155.67 | 76.11 | 130.26 | 68.79 | 77.14 | 5924.42
| PV (Kwhs) | [15 empty] | 127955
As per our conversation we do not have monthly data for Electricity or Water usage because the building is not metered separately by our utility providers. The totals listed above for Electricity and Water have been taken from our Building Controls Software and the cost has been calculated based on monthly kwh rates.
42 | UNCC - Belk Residence Hall | 2014-08-09: 10-08450-02A
|  | 2015-07-14 | 2015-08-14 | 2015-09-14 | 2015-10-14 | 2015-11-14 | 2015-12-14 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15
Consumption
| Electric (KWH) | 143000 | 187917 | 159676 | 202458 | 155992 | 144957 | 136202 | 137208 | 157337 | 157170 | 167331 | 179152
| Nat Gas (Therms) | 531 |  | 2633 | 2708 | 4733 | 5292 | 7672 | 6684 | 4793 | 3129 | 1935 | 1910
| Water (CF) | 110859.6257 | 255355.615 | 263399.7326 | 64045.4545 | 58498.6631 | 33775.4011 | 62363.6364 | 64815.508 | 64834.2246 | 76471.9251 | 38299.4652 | 39816.8449
Costs $
| Electric | 9964.6177 | 13450.7738 | 11056.9686 | 12420.4161 | 8971.9449 | 8346.7924 | 7596.1288 | 7734.6792 | 9202.4966 | 8771.3568 | 9404.9878 | 11244.3363
| Nat Gas | 475.47 | 1718.02 | 2270.56 | 2334.6 | 4039.25 | 4519.31 | 6179.08 | 4973.72 | 3046.12 |  | 610.46 | 1297.55
| Water | 7879.9085 | 18546.2879 | 19167.08 | 4885.2423 | 4615.3079 | 2866.3324 | 5779.5238 | 5405.2858 | 5340.3529 | 5989.4408 | 2917.9994 | 2897.0268
43 | NCSU - Early College High School/Cherry
| Utility |  | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 |  | Total | Units
| Electric (kWh) |  | 29200 | 23900 | 24200 | 25900 | 28100 | 26700 | 33200 | 22200 | 26500 | 29900 | 34000 |  | 303800 | kwh
| Water (CCF) |  | 14.6769 | 18.7516 | 21.2852 | 16.4701 | 10.2581 | 5.6081 | 5.7214 | 8.9348 | 12.7715 | 21.6856 | 24 |  | 160.1633 | CCF
| Natural Gas (therms) |  | 193 | 375 | 1182 | 1546 | 1495 | 2357 | 536 | 307 | 195 | 99 | 68 |  | 8353 | therms
| Electric Cost ($) |  | 2676.13 | 1930.46 | 1915.03 | 1983.12 | 2187.26 | 2132.69 | 2531.18 | 1892.42 | 2296.74 | 2862.01 | 3057.41 |  | 25464.45 | $
| Water Cost ($) |  | 115.3606 | 147.388 | 167.3018 | 129.4548 | 80.6284 | 44.0794 | 44.9704 | 70.2277 | 100.3842 | 170.4485 | 188.64 |  | 1258.8838 | $
| Natural Gas ($) |  | 197.25 | 350.15 | 952.44 | 1233.77 | 1167.48 | 1717.28 | 425.16 | 253.6 | 167.92 | 94.38 | 70.6 |  | 6630.03 | $
44 | UNCC - Hunt Residence Hall |  | 2014-09-01: 10-08610-03A
|  | 2015-07-14 | 2015-08-14 | 2015-09-14 | 2015-10-14 | 2015-11-14 | 2015-12-14 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15
Consumption
| Electric (KWH) | 64434 | 94275 | 101437 | 110986 | 90523 | 83795 | 95329 | 94561 | 97703 | 99476 | 77330 | 70230
| Nat Gas (Therms) | 96 | 191 | 663 | 598 | 764 | 583 | 762 | 961 | 772 | 878 | 449 | 72
| Water (CF) | 2075 | 23674 | 45449 | 42205 | 36231 | 16964 | 37109 | 33000 | 33000 | 33225 | 11740 | 3143
| Chill water mmBTU (BTUX10^6) | 452 | 598 | 526 | 340 | 126 | 83 | 87 | 87 | 135 | 280 | 348 | 474
| Hot water mmBTU | 134 | 107 | 116 | 149 | 183 | 268 | 223 | 215 | 180 | 86 | 76 | 71
Costs $
| Electric | 4489.9313 | 6748.0414 | 7024.1346 | 6808.7816 | 5206.4681 | 4825.0134 | 5316.5986 | 5330.5856 | 5714.5587 | 5551.5651 | 4346.4015 | 4407.9315
| Nat Gas | 103.98 | 185.11 | 588.2 | 532.69 | 670.46 | 517.45 | 633.54 | 733.94 | 509.09 | 194.97 | 290.86 | 70.08
| Water | 147.4911 | 1719.425 | 3307.2343 | 3219.3019 | 2858.4794 | 1439.6413 | 3439.061 | 2752.0332 | 2718.1885 | 2602.2514 | 894.4593 | 228.681
| Chill water | 3283.2235 | 6324.0974 | 5166.6005 | 2728.385 | 2340.7605 | 1782.0125 | 1219.1588 | 390.3426 | 2281.8506 | 1476.3234 | 1732.957 | 3040.8767
| Hot water | 5556.8312 | 2986.3489 | 3705.0382 | 3014.2207 | 3481.9795 | 7267.4249 | 6064.6244 | 3400.5636 | 3628.7419 | -306.4548 | 1132.0232 | 1509.3893
45 | NCSU - Wolf Ridge Building 6
| Utility |  |  | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 |  | Total | Units
| Electric (kWh) |  |  | 40170 | 39189.9996 | 37159.0004 | 31248.0011 | 35535.9955 | 35292.9993 | 35611.9995 | 36420.0134 | 35029.9988 | 33445.9839 | 34214.0198 |  | 393318.0112 | kwh
| Chilled Water (Dtherms) |  |  | 286 | 189 | 97 | 83 | 99 | 81 | 112 | 161 | 236 | 338 | 359 |  | 2041 | dthrms
| Steam (1,000 lbs) |  |  | 49.85 | 81.02 | 148 | 181.1 | 236.26 | 259 | 184 | 117 | 68 | 41.9898 | 70 |  | 1436.2198 | 1000 lbs
| Water (CCF) |  |  | 100 | 81 | 80 | 43 | 63 | 80 | 57 | 72 | 51 | 41 | 34 |  | 702 | CCF
| Electric Cost ($) |  |  | 3494.79 | 3409.53 | 3232.833 | 2718.5761 | 3091.6316 | 3070.4909 | 3098.244 | 3168.5412 | 3047.6099 | 2909.8006 | 2976.6197 |  | 34218.667 | $
| Chilled Water Cost ($) |  |  | 4118.4 | 2721.6 | 1396.8 | 1195.2 | 1425.6 | 1166.4 | 1612.8 | 2318.4 | 3398.4 | 4867.2 | 5169.6 |  | 29390.4 | $
| Steam Cost ($) |  |  | 691.4195 | 1123.7474 | 2052.76 | 2511.857 | 3276.9262 | 3592.33 | 2552.08 | 1622.79 | 943.16 | 582.398 | 970.9 |  | 19920.3681 | $
| Water Cost ($) |  |  | 786 | 636.66 | 628.8 | 337.98 | 495.18 | 628.8 | 448.02 | 565.92 | 400.86 | 322.26 | 267.24 |  | 5517.72 | $
46 | NCSU - Wolf Ridge Building 1
| Utility |  |  | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 |  | Total | Units
| Electric (kWh) |  |  | 141682.9834 | 141580.9326 | 129261.1084 | 118741.9434 | 136548.9502 | 133772.0947 | 141210.8765 | 140703.0029 | 131492.1875 | 121101.1556 | 123175.0259 |  | 1459270.2611 | kwh
| Chilled Water (Dtherms) |  |  | 824.968 | 473.8459 | 155.5774 | 85.0735 | 122.8071 | 144.7073 | 286.1628 | 485.854 | 765.8796 | 1051.1902 | 1027.9653 |  | 5424.0312 | dthrms
| Steam (1,000 lbs) |  |  | 198.1319 | 303.5922 | 495.3952 | 542.0977 | 714.7441 | 825.057 | 627.2033 | 351.6739 | 279.3356 | 258.1463 | 235.0534 |  | 4830.4306 | 1000 lbs
| Water (CCF) |  |  | 345 | 335 | 335 | 170 | 132 | 134 | 265 | 345 | 180 | 110 | 85 |  | 2436 | CCF
| Natural Gas (thms) |  |  | 1113 | 1377 | 1217 | 1159 | 768 | 995 | 1220 | 1167 | 1255 | 854 | 764 |  | 11889 | thms
| Electric Cost ($) |  |  | 12326.4196 | 12317.5411 | 11245.7164 | 10330.5491 | 11879.7587 | 11638.1722 | 12285.3463 | 12241.1613 | 11439.8203 | 10535.8005 | 10716.2273 |  | 126956.5127 | $
| Chilled Water Cost ($) |  |  | 11879.5395 | 6823.3816 | 2240.3145 | 1225.0582 | 1768.4227 | 2083.7848 | 4120.7449 | 6996.2977 | 11028.6668 | 15137.1387 | 14802.7008 |  | 78106.05 | $
| Steam Cost ($) |  |  | 2748.0892 | 4210.8234 | 6871.1312 | 7518.8956 | 9913.5 | 11443.5409 | 8699.3094 | 4877.7166 | 3874.3853 | 3580.4895 | 3260.1911 |  | 66998.0723 | $
| Water Cost ($) |  |  | 2711.7 | 2633.1 | 2633.1 | 1336.2 | 1037.52 | 1053.24 | 2082.9 | 2711.7 | 1414.8 | 864.6 | 668.1 |  | 19146.96 | $
| Natural Gas ($) |  |  | 1035.18 | 1269.93 | 1120.15 | 959.37 | 626.92 | 832.28 | 941.44 | 888.38 | 960.95 | 679.15 | 604.79 |  | 9918.54 | $
47 | UNCG - Spartan Village # 1
| Lee Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15 | 2015-07-15
700 Highland Avenue
| Electricity (kWhs) | 51376 | 67310 | 58835 | 64810 | 75371 | 86365 | 94925 | 71614 | 63508 | 55389 | 80642 | 87080
| Water Usage (gallons) | 33660 | 183582 | 231343 | 259701 | 96269 | 129105 | 210448 | 204478 | 164179 | 179105 | 126865 | 123134
| Natural Gas (Therms) | 122 | 465 | 460 | 564 | 569 | 412 | 750 | 742 | 752 | 541 | 452 | 451
| Electricity Cost ($) | 4890.97 | 5840.79 | 5375.91 | 5689.39 | 6337.58 | 7133.63 | 7684.1 | 6134.2 | 5636.92 | 5138.84 | 6688.05 | 7073.86
| Water Costs ($) | 954.95 | 2102.66 | 2468.1 | 2645.08 | 1434.59 | 1685.83 | 2308.22 | 2262.54 | 1954.2 | 2078.4 | 1678.7 | 1702.41
| Natural Gas Cost ($) | 135.02 | 448.45 | 443.88 | 542.06 | 537.58 | 387.14 | 635.13 | 575.35 | 225.89 | 372.43 | 331.84 | 361.68
48 | UNCG - Spartan Village # 3
| Haywood Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15 | 2015-07-15
1001 Union Street
| Electricity (kWhs) | 32916 | 41890 | 33239 | 39016 | 55321 | 64709 | 66639 | 46837 | 38846 | 26591 | 29312 | 34899
| Water Usage (gallons) | 2992 | 79105 | 94776 | 99254 | 60448 | 23880 | 94776 | 83582 | 70895 | 80597 | 5970 | 2985
| Natural Gas (Therms) | 195 | 257 | 254 | 309 | 327 | 229 | 434 | 428 | 423 | 282 | 71 | 82
| Electricity Cost ($) | 3046.58 | 3579.35 | 3084.03 | 3404.64 | 4401.52 | 5053.94 | 5576.07 | 3900.93 | 3410.71 | 2658.9 | 2825.83 | 3164.91
| Water Costs ($) | 720.84 | 1303.26 | 1423.17 | 1457.43 | 1160.51 | 880.72 | 1423.17 | 1337.52 | 1250.45 | 1324.68 | 753.68 | 769.15
| Natural Gas Cost ($) | 201.73 | 258.38 | 255.63 | 307.63 | 327.09 | 225.63 | 379.2 | 349.65 | 137.79 | 205.6 | 71.97 | 85.02
49 | UNCG - Spartan Village # 4
| Union Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15 | 2015-07-15
917 Union Street
| Electricity (kWhs) | 39247 | 53964 | 44200 | 51002 | 59338 | 66087 | 69213 | 54411 | 47866 | 35981 | 41225 | 47471
| Water Usage (gallons) | 14212 | 132835 | 169403 | 176119 | 100000 | 63433 | 151492 | 131343 | 117164 | 132836 | 6716 | 6716
| Natural Gas (Therms) | 119 | 446 | 430 | 492 | 489 | 287 | 622 | 638 | 602 | 423 | 141 | 143
| Electricity Cost ($) | 3731.22 | 4611.42 | 4057.39 | 4431.6 | 4943.22 | 5372.3 | 5576.07 | 4662.3 | 4260.77 | 3531.66 | 3853.37 | 4231.56
| Water Costs ($) | 806.49 | 1714.38 | 1994 | 2045.56 | 1463.14 | 1183.35 | 1857.13 | 1702.96 | 1604.47 | 1724.38 | 759.39 | 798.01
| Natural Gas Cost ($) | 132.27 | 431.08 | 416.47 | 475.87 | 465.31 | 276.82 | 532.81 | 559.6 | 165.82 | 296.22 | 119.71 | 130.75
50 | Winston-Salem State University, Martin Schexnider Residence Hall
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14
| Electricity (KWhs) building meter |  |  | 35938 | 46762 | 37721 | 36427 | 24293 | 35096 | 43165 | 34692 | 33878.5 | 76057 | 34350 | 36421
| Steam from Central Plant (lbs) - natural gas therms |  |  | 2677.1659 | 2899.5896 | 3466.3925 | 5159.5902 | 5422.6173 | 6142.155 | 5344.6529 | 4528.4219 | 3344.9209 | 2286.5695 | 2190.9892 | 2216.687
| Chilled Water from Central Plant (Dtherms) kwh |  |  | 64682.0727 | 56065.2532 | 41505.466 | 93036.8572 | 11363.958 | 10098.7457 | 7670.1532 | 25610.6753 | 37475.347 | 94189.1686 | 54205.3596 | 64801.2653
| Natural Gas (Therms) other than from central steam plant |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) |  |  | 413.55 | 280.07 | 318.23 | 242.52 | 88.36 | 207.83 | 214.64 | 214.64 | 312.91 | 296.62 | 271.37 | 206.02
| Electricity Cost ($) building meter x blended rate ($.071/kwh) |  |  | 2551.598 | 3320.102 | 2678.191 | 2586.317 | 1724.803 | 2491.816 | 3064.715 | 2463.132 | 2405.3735 | 5400.047 | 2438.85 | 2585.891
| Steam from Central Plant Cost ($) for Natural Gas |  |  | 1338.7669 | 1488.6497 | 1778.3043 | 2402.1122 | 2833.8962 | 2525.6362 | 2254.4134 | 1734.2537 | 1245.3891 | 852.2417 | 888.3962 | 888.8536
| Chilled Water from Central Plant Cost ($) kwh x $.071/wh |  |  | 4592.4272 | 3980.633 | 2946.8881 | 6605.6169 | 806.841 | 717.0109 | 544.5809 | 1818.3579 | 2660.7496 | 6687.431 | 3848.5805 | 4600.8898
| Natural Gas Cost ($) other than from central steam. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Costs ($) |  |  | 2226.02 | 1646.03 | 1896 | 1542.01 | 669.99 | 1381.88 | 1273.41 | 1273.41 | 1875.61 | 1805.33 | 1670.72 | 1369.51
51
Cape Fear CC- Union Station
Notes | Utility | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01
| Electricity (KWhs) | 305600 | 314800 | 358400 | 294000 | 258000 | 249600 | 259200 | 238800 | 271200 | 294400 | 280800 | 375600
1 | Steam (lbs) | bar: 2014-08-01 to 2015-07-15
2 | Chilled Water (Dtherms)
| Natural Gas (Therms) | 8429 | 10007 | 8611 | 9993 | 12959 | 13657 | 18058 | 17223 | 18541 | 17712 | 14560 | 12141
3 | Water (CCF) | 2014-08-01: 883; 2014-10-01: 979; 2014-12-01: 735; 2015-02-15: 389; 2015-04-15: 374; 2015-06-15: 648
| Electricity Cost ($) | 25329.44 | 25902.54 | 29201.72 | 24706.17 | 21704.77 | 21436.37 | 22465.23 | 20920.68 | 18876.21 | 20686.22 | 20190.83 | 27216.1
Steam Costs ($) | bar: 2014-08-01 to 2015-07-15
Chilled Water Costs ($)
| Natural Gas Costs ($) | 7725.7 | 9167.63 | 7892.01 | 9154.83 | 11663.41 | 12254.9 | 16567.86 | 14394.54 | 14545 | 11064.88 | 9343.94 | 7802.47
Notes
1 | We do not produe or use steam
2 | Having troble with CW meter. Sending data without CHW info.
3 | Billed from CFPUA every two months
52 | ECU - Smith-Williams Center
| Utility | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
| Electricity (KWhs) | 44983 | 25635 | 39109 | 37459 | 36155 | 44986 | 34874 | 28796 | 38499 | 40725 | 43798 | 37952 | 45087
Steam (lbs)
Chilled Water (Dtherms)
Natural Gas (Therms)
Water (CCF)
| Electricity Cost ($) | 4237.3986 | 2414.817 | 3684.0678 | 3528.6378 | 3405.801 | 4237.6812 | 3285.1308 | 2712.5832 | 3626.6058 | 3836.295 | 4125.7716 | 3575.0784 | 4247.1954
Steam Costs ($)
Chilled Water Costs ($)
| Natural Gas Costs ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | NCSU - Wolf Ridge Building 2
| Utility |  | 2014-08-31 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 |  | Total | Units
| Electric (kWh) |  | 46652.0081 | 50276.001 | 50750 | 48268.9819 | 43969.0247 | 49542.9688 | 45736.0229 | 45281.0059 | 46723.999 | 44320.0073 | 41210.9985 | 43963.9893 |  | 556695.0073 | kwh
| Chilled Water (Dtherms) |  | 420.556 | 355.394 | 202.365 | 50 | 30 | 27 | 26 | 75 | 160 | 296 | 445.9106 | 458.3418 |  | 2546.5675 | dthrms
| Steam (1,000 lbs) |  | 47.4 | 53.31 | 81.17 | 175.52 | 213.94 | 263 | 289 | 277 | 133 | 82 | 44.9199 | 80.7803 |  | 1741.0402 | 1000 lbs
| Water (CCF) |  | 189 | 228 | 169 | 169 | 87 | 126 | 158 | 116 | 141 | 103 | 253 | 163 |  | 1902 | CCF
| Electric Cost ($) |  | 4058.7247 | 4374.0121 | 4415.25 | 4199.4014 | 3825.3051 | 4310.2383 | 3979.034 | 3939.4475 | 4064.9879 | 3855.8406 | 3585.3569 | 3824.8671 |  | 48432.4656 | $
| Chilled Water Cost ($) |  | 6056.0068 | 5117.6742 | 2914.0559 | 720 | 432 | 388.8 | 374.4 | 1080 | 2304 | 4262.4 | 6421.1133 | 6600.1219 |  | 36670.5721 | $
| Steam Cost ($) |  | 657.438 | 739.4097 | 1125.8279 | 2434.4624 | 2967.3478 | 3647.81 | 4008.43 | 3841.99 | 1844.71 | 1137.34 | 623.0395 | 1120.4226 |  | 24148.2279 | $
| Water Cost ($) |  | 1485.54 | 1792.08 | 1328.34 | 1328.34 | 683.82 | 990.36 | 1241.88 | 911.76 | 1108.26 | 809.58 | 1988.58 | 1281.18 |  | 14949.72 | $
54 | UNCG - Spartan Village # 2
| Highland Residence Hall | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15 | 2015-07-15
701 Highland Avenue
| Electricity (kWhs) | 61500 | 75600 | 60000 | 63600 | 72900 | 84900 | 90300 | 72900 | 64200 | 44400 | 48413 | 54581
| Water Usage (gallons) | 91044 | 160448 | 199253 | 163433 | 167164 | 35075 | 200746 | 178358 | 161194 | 176866 | 2985 | 5224
| Natural Gas (Therms) | 195 | 411 | 417 | 512 | 535 | 301 | 699 | 668 | 671 | 451 | 69 | 84
| Electricity Cost ($) | 5691.85 | 6551.91 | 5631.65 | 5800.03 | 6388.19 | 6954.93 | 7266.4 | 6214.87 | 5689.1 | 4492.54 | 4735.06 | 5102.08
| Water Costs ($) | 1394.62 | 1925.65 | 2222.57 | 1948.49 | 1977.04 | 966.37 | 2233.99 | 2062.69 | 1931.36 | 2061.27 | 730.84 | 786.59
| Natural Gas Cost ($) | 201.73 | 399.1 | 404.58 | 494.25 | 506.87 | 289.18 | 595.63 | 526.58 | 197.99 | 314.48 | 70.6 | 86.52
55 | UNCC - PORTAL | 2014-09-01: 08-07560-03A
|  | 2015-07-14 | 2015-08-14 | 2015-09-14 | 2015-10-14 | 2015-11-14 | 2015-12-14 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15
Consumption
| Electric (KWH) | 67060 | 80854 | 88878 | 82852 | 74272 | 75624 | 76572 | 62522 | 70095 | 71961 | 72570 | 75048
| Nat Gas (Therms) | 32 | 85 | 164 | 170 | 354 | 480 | 294 | 102 | 119 | 265 | 141 | 38
| Water (CF) | 250 | 280 | 267 | 271 | 941 | 219 | 6598 | 995 | 1537 | 1457 | 266 | 150
| Chill water mmBTU (BTUX10^6) | 544 | 488 | 603 | 322 | 87 | 55 | 56 | 61 | 164 | 325 | 569 | 695
| Hot water mmBTU | 243 | 143 | 258 | 333 | 391 | 504 | 444 | 442 | 364 | 319 | 285 | 241
Costs $
| Electric | 4672.9179 | 5787.3895 | 6154.4706 | 5082.8138 | 4271.785 | 4354.5178 | 4270.501 | 3524.4855 | 4099.7922 | 4016.0056 | 4078.8614 | 4710.3295
| Nat Gas | 49.33 | 94.59 | 162.05 | 167.18 | 322.47 | 429.92 | 257.95 | 97.56 | 97.08 | 27.93 | 106.43 | 47.38
| Water | 17.77 | 20.3362 | 19.4291 | 20.6713 | 74.2411 | 18.5853 | 611.4669 | 82.978 | 126.6017 | 114.1153 | 20.2663 | 10.9138
| Chill water | 2562.2344 | 1153.7824 | 1991.8849 | 1433.5291 | 1261.4652 | 456.4407 | 222.6938 | 429.608 | 530.7505 | 1051.7921 | 2928.2109 | 4172.5599
| Hot water | 1816.2705 | 894.648 | 1692.6703 | 1680.1662 | 1930.0289 | 2023.7921 | 1835.846 | 1509.1533 | 1474.2816 | 793.4043 | 1086.9956 | 1320.1149
56 | NCSU - Wolf Ridge Building 3
| Utility |  | 2014-08-31 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 |  | Total | Units
| Electric (kWh) |  | 42294.9982 | 42239.9902 | 42876.0071 | 41388.0005 | 39213.9893 | 42395.9961 | 40167.9993 | 40778.9917 | 41736.9995 | 38388.0005 | 39009.0332 | 40076.9653 |  | 490566.9708 | kwh
| Chilled Water (Dtherms) |  | 346.395 | 260.7379 | 131.948 | 27 | 18 | 12 | 13 | 44 | 109 | 228 | 389.7739 | 480.8262 |  | 2060.681 | dthrms
| Steam (1,000 lbs) |  | 47.88 | 48.07 | 95.13 | 203 | 250 | 300 | 317 | 193 | 102 | 62 | 40.6799 | 97.9099 |  | 1756.6698 | 1000 lbs
| Water (CCF) |  | 83 | 117 | 89 | 88 | 53 | 78 | 97 | 69 | 85 | 65 | 59 | 40 |  | 923 | CCF
| Electric Cost ($) |  | 3679.6648 | 3674.8792 | 3730.2126 | 3600.756 | 3411.6171 | 3688.4517 | 3494.6159 | 3547.7723 | 3631.119 | 3339.756 | 3393.7859 | 3486.696 |  | 42679.3265 | $
| Chilled Water Cost ($) |  | 4988.0883 | 3754.626 | 1900.0512 | 388.8 | 259.2 | 172.8 | 187.2 | 633.6 | 1569.6 | 3283.2 | 5612.7445 | 6923.8969 |  | 29673.8068 | $
| Steam Cost ($) |  | 664.0956 | 666.7309 | 1319.4531 | 2815.61 | 3467.5 | 4161 | 4396.79 | 2676.91 | 1414.74 | 859.94 | 564.2307 | 1358.0101 |  | 24365.0105 | $
| Water Cost ($) |  | 652.38 | 919.62 | 699.54 | 691.68 | 416.58 | 613.08 | 762.42 | 542.34 | 668.1 | 510.9 | 463.74 | 314.4 |  | 7254.78 | $
57 | Winston-Salem State University, Hill Hall - Student Success Center
| Utility | Jun-14 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-14
| Electricity (KWhs) building meter |  |  | 35080.3333 | 35080.3333 | 38443 | 30014.9 | 27611 | 39068 | 36579 | 42433 | 39707.1 | 82201 | 119513 | 36485
| Steam from Central Plant (lbs) - natural gas therms |  |  | 1823.9535 | 1975.4907 | 2361.6536 | 3515.2294 | 3694.4298 | 4184.6509 | 3641.3126 | 3085.2144 | 2278.895 | 1557.84 | 1492.7212 | 1510.2291
| Chilled Water from Central Plant (Dtherms) kwh |  |  | 44067.9034 | 38197.2633 | 28277.6786 | 63386.0212 | 7742.2659 | 6880.2765 | 5225.6762 | 17448.556 | 25531.9581 | 64171.0911 | 36930.1175 | 44149.1093
| Natural Gas (Therms) other than from central steam plant |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water (CCF) |  |  | 23.1 | 29.7 | 24.1 | 23.8 | 10.4 | 24.7 | 23.75 | 23.75 | 27.3 | 12.5 | 11.9 | 11.4
| Electricity Cost ($) building meter x blended rate ($.071/kwh) |  |  | 2490.7037 | 2490.7037 | 2729.453 | 2131.0579 | 1960.381 | 2773.828 | 2597.109 | 3012.743 | 2819.2041 | 5836.271 | 8485.423 | 2590.435
| Steam from Central Plant Cost ($) for Natural Gas |  |  | 912.102 | 1014.2172 | 1211.5589 | 1636.5593 | 1930.7338 | 1720.7162 | 1535.9321 | 1181.5472 | 848.4837 | 580.6324 | 605.2644 | 605.576
| Chilled Water from Central Plant Cost ($) kwh x $.071/wh |  |  | 3128.8211 | 2712.0057 | 2007.7152 | 4500.4075 | 549.7009 | 488.4996 | 371.023 | 1238.8475 | 1812.769 | 4556.1475 | 2622.0383 | 3134.5868
| Natural Gas Cost ($) other than from central steam. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Costs ($) |  |  | 151.86 | 192.47 | 166.39 | 165.38 | 86.73 | 171.78 | 169.355 | 169.355 | 187.01 | 97.2 | 90.14 | 88.71
58 | NCSU - Wolf Ridge Building 5
| Utility |  | 2014-08-31 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 |  | Total | Units
| Electric (kWh) |  | 31869.0033 | 33372.9858 | 31777.0081 | 29947.998 | 26263.0005 | 26403.0151 | 37998.0102 | 30710.0015 | 32835.9947 | 30931.0074 | 29625.9995 | 29063.0035 |  | 370797.0276 | kwh
| Chilled Water (Dtherms) |  | 277.8053 | 226.1169 | 108.401 | 26 | 16 | 10.4919 | 11.4021 | 42 | 98 | 194 | 325.252 | 337.261 |  | 1672.7302 | dthrms
| Steam (1,000 lbs) |  | 44.53 | 57.48 | 80.06 | 141 | 161 | 181 | 211 | 143 | 86 | 57 | 52.5199 | 45.83 |  | 1260.42 | 1000 lbs
| Water (CCF) |  | 38 | 61 | 584 | 55 | 23 | 39 | 53 | 39 | 54 | 28 | 24 | 15 |  | 1013 | CCF
| Electric Cost ($) |  | 2772.6033 | 2903.4498 | 2764.5997 | 2605.4758 | 2284.881 | 2297.0623 | 3305.8269 | 2671.7701 | 2856.7315 | 2690.9976 | 2577.462 | 2528.4813 |  | 32259.3414 | $
| Chilled Water Cost ($) |  | 4000.3963 | 3256.084 | 1560.9744 | 374.4 | 230.4 | 151.084 | 164.1902 | 604.8 | 1411.2 | 2793.6 | 4683.6281 | 4856.5582 |  | 24087.3152 | $
| Steam Cost ($) |  | 617.6311 | 797.2476 | 1110.4322 | 1955.67 | 2233.07 | 2510.47 | 2926.57 | 1983.41 | 1192.82 | 790.59 | 728.4515 | 635.6623 |  | 17482.0247 | $
| Water Cost ($) |  | 298.68 | 479.46 | 4590.24 | 432.3 | 180.78 | 306.54 | 416.58 | 306.54 | 424.44 | 220.08 | 188.64 | 117.9 |  | 7962.18 | $
59 | NCSU - Wolf Ridge Building 4
| Utility |  | 2014-08-31 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 |  | Total | Units
| Electric (kWh) |  | 33423.0042 | 31042.0074 | 30466.0034 | 30248.9929 | 29457.0007 | 21910.9802 | 19745.0256 | 30752.9907 | 29761.9934 | 32721.0083 | 33212.0056 | 37614.0137 |  | 360355.0262 | kwh
| Chilled Water (Dtherms) |  | 268.7059 | 202.573 | 91.814 | 17 | 13 | 10.25 | 7 | 40 | 89 | 209 | 335.6401 | 345.447 |  | 1629.43 | dthrms
| Steam (1,000 lbs) |  | 54.9 | 47.38 | 115.62 | 288 | 176 | 223.438 | 263.6458 | 169.7242 | 89.1718 | 61.8641 | 59.496 | 53.658 |  | 1602.898 | 1000 lbs
| Water (CCF) |  | 38 | 20 | 10 | 8 | 4 | 5 | 12 | 22 | 9 | 21 | 29 | 36 |  | 214 | CCF
| Electric Cost ($) |  | 2907.8014 | 2700.6546 | 2650.5423 | 2631.6624 | 2562.7591 | 1906.2553 | 1717.8172 | 2675.5102 | 2589.2934 | 2846.7277 | 2889.4445 | 3272.4192 |  | 31350.8873 | $
| Chilled Water Cost ($) |  | 3869.3646 | 2917.0512 | 1322.1211 | 244.8 | 187.2 | 147.6 | 100.8 | 576 | 1281.6 | 3009.6 | 4833.218 | 4974.4371 |  | 23463.7919 | $
| Steam Cost ($) |  | 761.463 | 657.1606 | 1603.6494 | 3994.56 | 2441.12 | 3099.0851 | 3656.7678 | 2354.0752 | 1236.8134 | 858.0556 | 825.209 | 744.2362 |  | 22232.1953 | $
| Water Cost ($) |  | 298.68 | 157.2 | 78.6 | 62.88 | 31.44 | 39.3 | 94.32 | 172.92 | 70.74 | 165.06 | 227.94 | 282.96 |  | 1682.04 | $
60 | Guilford Technical Community College - Aviation Center III Building
61 | UNCC - Martin Residence Hall |  | 2014-08-31: 11-09156-02a
|  | 2015-07-14 | 2015-08-14 | 2015-09-14 | 2015-10-14 | 2015-11-14 | 2015-12-14 | 2015-01-15 | 2015-02-15 | 2015-03-15 | 2015-04-15 | 2015-05-15 | 2015-06-15
Consumption
| Electric (KWH) | 0 | 133266 | 235067 | 119199 | 159826 | 141346 | 131900 | 130400 | 140609 | 162851 | 169035 | 164385
| Nat Gas (Therms) |  | 1540 | 1999 | 2358 | 3838 | 4971 | 7224 | 6667 | 4630 | 3142 | 2264 | 1800
| Water (CF) | 0 | 41013 | 60816 | 64336 | 48323 | 26879 | 32356 | 33538 | 35992 | 42514 | 21915 | 26888
Costs $
| Electric | 0 | 9538.9498 | 16277.5147 | 7312.6336 | 9192.459 | 8138.8669 | 7356.2017 | 7350.8991 | 8224.0913 | 9088.4025 | 9500.7626 | 10317.497
| Nat Gas |  | 1430.74 | 1850.17 | 2178.21 | 3509.17 | 4543.78 | 6226.92 | 5308.41 | 3149.3 |  | 1196.68 | 1224.09
| Water | 0 | 2978.7436 | 4425.4606 | 4907.4045 | 3812.4893 | 2281.0728 | 2998.5787 | 2796.8997 | 2964.6376 | 3329.7852 | 1669.6827 | 1956.3392
acccepted 8/13/2015
Note on K628: Feb and March bill covered both months. Divided the use and cost evenly.
Note on L628: Feb and March bill covered both months. Divided the use and cost evenly.
Note on E838: Averaged value for August and September

## 2014 Summary
State of North Carolina - Department of Administration State Construction Office - Energy Benchmarking Project
2104-09-22 | PACKAGE DATA (Pages 1 - 6) | [10 empty] | 2104-09-22 | ANNUAL ENERGY USAGE (x1,000,000 BTU/YEAR) (Pages 7 -12) | [11 empty] | 2104-09-22 | ANNUAL ENERGY USAGE ($/YEAR) (pages 13-18) | [9 empty] | 2104-09-22 | ANNUAL INDOOR WATER USAGE (GALLONS/YEAR) (Pages 19 - 24) | [11 empty] | 2104-09-22 | Construction and Design Costs and Fees (Pages 25 - 30)
Project | Agency or Institution | Energy Contact | SCO ID# | Energy Model Report Date | Energy Model Report Phase | Construction Contract Award Date | Actual or Projected Acceptance Date | Principal Use(s) | Number of Beds | Size (GSF from building code summary) | Floors (from building code summary) | Project | ASHRAE Standard | Baseline | EUI Baseline (kBtu/Sq Ft/yr) | Proposed | EUI Proposed (kBtu/Sq Ft/yr) | Proposed improvement in energy efficiency | Proposed Energy Savings | Year of Meter Data (updated annually Oct 1) | Metered Energy Usage | EUI Metered (kBtu/Sq Ft/yr) | Metered improvement in energy efficiency | Metered Energy Savings | Project | Baseline | Baseline ($/Yr/Sq Ft) | Proposed | Proposed ($/Yr/Sq Ft) | Proposed % improvement in energy cost | Proposed Savings in Energy Cost | Metered | Metered ($/Yr/Sq Ft) | Metered % improvement in energy cost | Metered Savings in Energy Cost | Project | Baseline (Gallons/Year) | Baseline (Gal/Res/Yr) | Baseline (Gal/Sq Ft/Yr) | Proposed (Gallons/Year) | Proposed (Gal/Res/Yr) | Proposed (Gal/Sq Ft/Yr) | Proposed % improvement in water usage | Proposed Savings (Gallons/Year) | Metered (Gallons/Year) | Metered (Gal/Res/Yr) | Metered (Gal/Sq Ft/Yr) | Metered improvement in water usage | Project | Cost Estimate or Original Amount Construction Contract | Construction Cost/SF | Designer's Baseline (non-SB668) Estimate | Original Total Design Fee (without amendments) | Additional Design Fees (LEED or SB 668 - included in OTDF) | Advance Planning Contract Item G | Commissioning Fee | Simple Payback in Years (Net Savings Required /HB 628) | Modeler | ASHRAE Standard
Cone Residence Hall Renovation | ASU | Jerry Marshall | 08-07272-01A | 2009-01-20 | CD | 2009-09-14 | 2010-06-23 | Residence Hall | 278 | 58803 | 8 | Cone Residence Hall Renovation | 90.1-2004 | 3467 | 58.9596 | 1993 | 33.8928 | 42.52% | 1474 | 4th | 5419.3773 | 92.1616 | -56.31% | -1952.3773 | Cone Residence Hall Renovation | 81830 | 1.3916 | 43969 | 0.74773 | 46.27% | 37861 | 131154.0577 | 2.2304 | -60.28% | -49324.0577 | Cone Residence Hall Renovation | 2000376 | 7195.5971 | 34.0183 | 1397116 | 5025.5971 | 23.7593 | 30.16% | 603260 | 1686813.173 | 6067.6733 | 28.6858 | 15.68% | Cone Residence Hall Renovation | 7585100 | 128.9917 | 5965486 | 883660 | 0 |  | 62500 | 44.4287 | SKA | 90.1-2004
Prospector Hall Renovation Phase II | UNCC | Tony Schallert | 06-07223-01A | 2013-03-15 | LEED submit. | 2010-08-12 | 2011-05-30 | Food Service/Dining | NA | 22705 | 2 | Prospector Hall Renovation Phase II | 90.1-2004 | 2082 | 91.6979 | 1477 | 65.0518 | 29.06% | 605 | 3rd | 5698.8223 | 250.9942 | -173.7% | -3616.8223 | Prospector Hall Renovation Phase II | 30538 | 1.345 | 21943 | 0.96644 | 28.15% | 8595 | 72532.8399 | 3.1946 | -137.5% | -41994.8399 | Prospector Hall Renovation Phase II | 48654 | NA | 2.1429 | 27934 | NA | 1.2303 | 42.59% | 20720 | 1535270 | NA | 67.6181 | -3055% | Prospector Hall Renovation Phase II | 4029200 | 177.4587 | 3944812 | 295500 | 0 |  | 65100 | 17.3924 | M&C | 90.1-2004
Miltimore Residence Hall | UNCC | Tony Schallert | 05-06656-01A | 2009-06-10 | CD | 2009-07-22 | 2011-07-19 | Residence Hall | 431 | 173086 | 5 | Miltimore Residence Hall | 90.1-2004 | 38283 | 221.1791 | 32882 | 189.9749 | 14.11% | 5401 | 3rd | 12027.5275 | 69.4887 | 68.58% | 26255.4725 | Miltimore Residence Hall | 478677 | 2.7655 | 411144 | 2.3754 | 14.11% | 67533 | 163500.3447 | 0.94462 | 65.84% | 315176.6553 | Miltimore Residence Hall | 6961135 | 16151.1253 | 40.2178 | 5188175 | 12037.529 | 29.9746 | 25.47% | 1772960 | 4537323.12 | 10527.4318 | 26.2143 | 34.82% | Miltimore Residence Hall | 32995620 | 190.6314 | 33000165 | 2747550 | 58700 |  | 177000 | 3.4228 | CN | 90.1-2004
Nursing Building | NCCU | Eric Frazier | 07-07203-02A | 2009-12-22 | CD | 2010-01-25 | 2011-08-05 | Offices/Classrooms | NA | 69610 | 5 | Nursing Building | 90.1-2004 | 6048.6 | 86.8927 | 2596.2 | 37.2964 | 57.08% | 3452.4 | 1st | Meters not operational |  |  |  | Nursing Building | 148249 | 2.1297 | 61035 | 0.87681 | 58.83% | 87214 | Meters not operational |  |  |  | Nursing Building | 871150 | NA | 12.5147 | 601563 | NA | 8.6419 | 30.95% | 269587 | 1129435.12 | NA | 16.2252 | -29.65% | Nursing Building | 16198787 | 232.7078 | 16003466 | 1795875 | 82875 | 16175 | 265694 | 6.4217 | RMF | 90.1-2004
Chidley North Residence Hall | NCCU | Eric Frazier | 05-07248-02A | 2012-03-23 | LEED submit. | 2009-08-03 | 2011-08-10 | Residence Hall | 528 | 133570 | 4 | Chidley North Residence Hall | 90.1-2004 | 16482 | 123.396 | 10635 | 79.6212 | 35.48% | 5847 | 3rd | 5625.2607 | 42.1147 | 65.87% | 10856.7393 | Chidley North Residence Hall | 292778 | 2.1919 | 198708 | 1.4877 | 32.13% | 94070 | 100460 | 0.75211 | 65.69% | 192318 | Chidley North Residence Hall | 6283057 | 11899.7292 | 47.0394 | 4373148 | 8282.4773 | 32.7405 | 30.4% | 1909909 | 3417529.72 | 6472.5942 | 25.5861 | 45.61% | Chidley North Residence Hall | 23276802 | 174.2667 | 21956196 | 2186050 | 173500 |  | 104934 | 16.9984 | SWA | 90.1-2004
The Loudermilk Center for Excellence (Kenan Stadium East End Zone Facility) | UNC-CH | Chris Martin | 09-07851-01A | 2010-05-17 | CD | No Contract (Found. Proj) | 2011-08-18 | Offices/Locker rooms/Club | NA | 170189 | 6 | The Loudermilk Center for Excellence (Kenan Stadium East End Zone Facility) | 90.1-2004 | 10672 | 62.7068 | 7143 | 41.971 | 33.07% | 3529 | 1st | 25122.2828 | 147.614 | -135.4% | -14450.2828 | The Loudermilk Center for Excellence (Kenan Stadium East End Zone Facility) | 116674 | 0.68556 | 78320 | 0.46019 | 32.87% | 38354 | 269941.97 | 1.5861 | -131.4% | -153267.97 | The Loudermilk Center for Excellence (Kenan Stadium East End Zone Facility) | 1518337 | NA | 8.9215 | 991995 | NA | 5.8288 | 34.67% | 526342 | 1089000 | NA | 6.3988 | 28.28% | The Loudermilk Center for Excellence (Kenan Stadium East End Zone Facility) | Foundation Project | [7 empty] | MSWG | 90.1-2004
Davis Arena Add & Renov | DoAG&CS | Debbie Robertson <debbie.robertson@ncagr.gov> | 08-07347-02A | 2010-05-06 | CD | 2010-10-26 | 2011-08-19 | Assembly | NA | 67904 | 1 | Davis Arena Add & Renov | 90.1-2004 | 2961 | 43.6057 | 1736 | 25.5655 | 41.37% | 1225 | 1st | 3354 | 49.3933 | -13.27% | -393 | Davis Arena Add & Renov | 72840 | 1.0727 | 42637 | 0.6279 | 41.46% | 30203 | 61917.13 | 0.91183 | 15% | 10922.87 | Davis Arena Add & Renov | 109500 | NA | 1.6126 | 87313 | NA | 1.2858 | 20.26% | 22187 |  | NA |  |  | Davis Arena Add & Renov | 5507600 | 81.1086 | 5351000 | 484000 | 15000 |  | 43640 | 7.1264 |  | 90.1-2004
Student Health Center Add and Renovation | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 07-07345-02 | 2010-03-12 | CD | 2010-06-10 | 2011-09-12 | Offices/Clinics | NA | 24663 | 2 | Student Health Center Addition and Renovation | 90.1-2004 | 2746 | 111.3409 | 1547 | 62.7255 | 43.66% | 1199 | 3rd | 13048.6619 | 197.3243 | -375.2% | -10302.6619 | Student Health Center Addition and Renovation | 69316 | 2.8105 | 38688 | 1.5687 | 44.19% | 30628 | 215008.2644 | 3.2514 | -210.2% | -145692.2644 | Student Health Center Addition and Renovation | 320198 | NA | 12.9829 | 230958 | NA | 9.3646 | 27.87% | 89240 | 417081.1667 | NA | 6.3072 | -30.26% | Student Health Center Addition and Renovation | 6017900 | 244.0052 | 5778782 | 634045 | 65575 |  | 106438 | 13.4234 | RMF | 90.1-2004
Gilchrist Education and Psychology Complex | ECSU | Elizabeth Linney | 07-07081-02A | 2010-01-11 | CD | 2010-01-05 | 2012-02-01 | Office/Classroom | NA | 48112 | 3 | Gilchrist Education and Psychology Complex | 90.1-2004 | 3078 | 63.9757 | 1625 | 33.7754 | 47.21% | 1453 | 2nd | 2061.5612 | 42.8492 | 33.02% | 1016.4388 | Gilchrist Education and Psychology Complex | 64655 | 1.3438 | 34128 | 0.70934 | 47.22% | 30527 | 74545.31 | 1.5494 | -15.3% | -9890.31 | Gilchrist Education and Psychology Complex | 1506938 | NA | 31.3215 | 1056525 | NA | 21.9597 | 29.89% | 450413 | 50815.66 | NA | 1.0562 | 96.63% | Gilchrist Education and Psychology Complex | 14394127 | 299.1796 | 13822099 | 1654600 | 35000 |  | 57000 | 21.7522 | AEI | 90.1-2004
SENC Ag Center | DoAG&CS | Debbie Robertson <debbie.robertson@ncagr.gov> | 08-07348-02A | 2010-06-28 | DD | 2011-03-22 | 2012-04-12 | Equine & Livestock | NA | 55605 | 1 | SENC Ag Center | 90.1-2004 | 1743 | 31.3461 | 749 | 13.47 | 57.03% | 994 | 0 |  |  |  |  | SENC Ag Center | 42886 | 0.77126 | 28420 | 0.51111 | 33.73% | 14466 |  |  |  |  | SENC Ag Center | 243256 | NA | 4.3747 | 171756 | NA | 3.0889 | 29.39% | 71500 |  | NA |  |  | SENC Ag Center | 4072395 | 73.2379 | 3919435 | 363080 | 0 |  | 11870 | 11.3943 |  | 90.1-2004
EPIC | UNCC | Tony Schallert | 07-07078-02A | 2009-08-21 | CD | 2009-09-30 | 2012-04-12 | Offices/Labs/Classrooms | NA | 200164 | 4 | EPIC | 90.1-2004 | 30494.5 | 152.3476 | 18910.6 | 94.4755 | 37.99% | 11583.9 | 1st | 42942.022 | 214.5342 | -40.82% | -12447.522 | EPIC | 284103 | 1.4194 | 165774 | 0.82819 | 41.65% | 118329 | 439009.3809 | 2.1932 | -54.52% | -154906.3809 | EPIC | 3172838 | NA | 15.8512 | 1985718 | NA | 9.9205 | 37.42% | 1187120 | 1002604.24 | NA | 5.0089 | 68.4% | EPIC | 61500000 | 307.2481 | 51725930 | 5792635 | 221084 |  | 404815 | 87.8903 | M&L | 90.1-2004
Veteran's Nursing Home - Swannanoa | NCDOA-VA | diane.norris@doa.nc.gov | 06-06924-05A | 2009-12-22 | CD | 2010-05-24 | 2012-05-31 | Nursing Home | 100 | 108770 | 1 | Veteran's Nursing Home - Swananoa | 90.1-2004 | 8495 | 78.1006 | 5163 | 47.4671 | 39.22% | 3332 | 1st | 8733.6021 | 80.2942 | -2.809% | -238.6021 | Veteran's Nursing Home - Swananoa | 213106 | 1.9592 | 120807 | 1.1107 | 43.31% | 92299 | 176086.44 | 1.6189 | 17.37% | 37019.56 | Veteran's Nursing Home - Swananoa | 4378540 | 43785.4 | 40.255 | 3400982 | 34009.82 | 31.2676 | 22.33% | 977558 | 498115.64 | 4981.1564 | 4.5795 | 88.62% | Veteran's Nursing Home - Swananoa | 16135100 | 148.3415 | 15834228 | 1250000 | 0 |  | 96941 | 4.31 | MCBH | 90.1-2004
Russell Classroom Building | Pitt CC | Don Heisey 'dheisey@email.pittcc.edu' | 08-07329-02A | 2010-04-12 | CD | 2010-12-06 | 2012-06-27 | Office/Classroom | NA | 50434 | 2 | Russell Classroom Building | 90.1-2004 | 3018 | 59.8406 | 1900 | 37.673 | 37.04% | 1118 | 1st | 4167 | 82.6228 | -38.07% | -1149 | Russell Classroom Building | 91928 | 1.8227 | 56777 | 1.1258 | 38.24% | 35151 | 53735.175 | 1.0655 | 41.55% | 38192.825 | Russell Classroom Building | 1217970 | NA | 24.1498 | 954495 | NA | 18.9256 | 21.63% | 263475 | 295475 | NA | 5.8586 | 75.74% | Russell Classroom Building | 7393799 | 146.6035 | 7243287 | 943138 | 52150 |  | 42310 | 6.9691 | PDC | 90.1-2004
Bailey Residence Hall Renovation | UNC-G | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Bailey Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2nd | 4244.1871 | 138.0897 | -4.64% | -188.1871 | Bailey Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 24482.76 | 0.79658 | 58.93% | 35125.24 | Bailey Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 430300 | 5003.4884 | 14.0003 | -31.24% | Bailey Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Coit Residence Hall Renovation | UNC-G | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Coit Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2nd | 3338.7712 | 108.6309 | 17.68% | 717.2288 | Coit Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 18646.9 | 0.6067 | 68.72% | 40961.1 | Coit Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 422800 | 4916.2791 | 13.7563 | -28.95% | Coit Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Cotton Residence Hall Renovation | UNC-G | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Cotton Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2nd | 3787.8639 | 123.2427 | 6.611% | 268.1361 | Cotton Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 27071.85 | 0.88082 | 54.58% | 32536.15 | Cotton Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 443300 | 5154.6512 | 14.4233 | -35.2% | Cotton Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Gray Residence Hall Renovation | UNC-G | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Gray Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2nd | 2552.0621 | 83.0344 | 37.08% | 1503.9379 | Gray Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 21730.89 | 0.70704 | 63.54% | 37877.11 | Gray Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 407900 | 4743.0233 | 13.2715 | -24.41% | Gray Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Hinshaw Residence Hall Renovation | UNC-G | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Hinshaw Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2nd | 3528.0014 | 114.7877 | 13.02% | 527.9986 | Hinshaw Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 40689.55 | 1.3239 | 31.74% | 18918.45 | Hinshaw Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 386000 | 4488.3721 | 12.559 | -17.73% | Hinshaw Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Jamison Residence Hall Renovation | UNC-G | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 86 | 30735 | 4 | Jamison Residence Hall Renovation | 90.1-2004 | 4056 | 131.9668 | 3076 | 100.0813 | 24.16% | 980 | 2nd | 9693.4978 | 315.3896 | -139% | -5637.4978 | Jamison Residence Hall Renovation | 59608 | 1.9394 | 46163 | 1.502 | 22.56% | 13445 | 21007.97 | 0.68352 | 64.76% | 38600.03 | Jamison Residence Hall Renovation | 327880 | 3812.5581 | 10.668 | 209536 | 2436.4651 | 6.8175 | 36.09% | 118344 | 391330 | 4550.3488 | 12.7324 | -19.35% | Jamison Residence Hall Renovation | 6196641.1429 | 201.6151 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Shaw Residence Hall Renovation | UNC-G | Douglas Cato | 09-07927-03A | 2010-09-15 | CD | 2010-11-29 | 2012-07-01 | Residence Hall | 118 | 54847 | 4 | Shaw Residence Hall Renovation | 90.1-2004 | 4056 | 73.9512 | 3076 | 56.0833 | 24.16% | 980 | 2nd | 11456.9746 | 208.8897 | -182.5% | -7400.9746 | Shaw Residence Hall Renovation | 59608 | 1.0868 | 46163 | 0.84167 | 22.56% | 13445 | 69732.88 | 1.2714 | -16.99% | -10124.88 | Shaw Residence Hall Renovation | 327880 | 2778.6441 | 5.9781 | 209536 | 1775.7288 | 3.8204 | 36.09% | 118344 | 684000 | 5796.6102 | 12.4711 | -108.6% | Shaw Residence Hall Renovation | 6196641.1429 | 112.9805 | 6016156 | 600745 | 11428.5714 |  | 40878.7143 | 17.3144 | SWA | 90.1-2004
Harrill Residence Hall Renovation | WCU | David King <dbking@email.wcu.edu> | 03-07291-02A | 2011-01-07 | CD | 2011-08-03 | 2012-08-02 | Residence Hall | 350 | 71505 | 10 | Harrill Residence Hall Renovation | 90.1-2004 | 5122 | 71.6314 | 3189 | 44.5983 | 37.74% | 1933 | 2nd | 3084.9766 | 43.1435 | 39.77% | 2037.0234 | Harrill Residence Hall Renovation | 114129 | 1.5961 | 82978 | 1.1605 | 27.29% | 31151 | 57797.92 | 0.80831 | 49.36% | 56331.08 | Harrill Residence Hall Renovation | 2675470 | 7644.2 | 37.4165 | 1801347 | 5146.7057 | 25.1919 | 32.67% | 874123 | 1235936 | 3531.2457 | 17.2846 | 53.8% | Harrill Residence Hall Renovation | 13435000 | 187.889 | 11750000 | 998800 | 0 |  | 153235 | 59.0105 | Optima | 90.1-2004
Health Science Building | UNCP | Terry W. Divine <terry.divine@uncp.edu> | 06-06859-02A | 2009-11-17 | CD | 2010-07-16 | 2012-08-07 | Office/Classroom | NA | 87000 | 3 | Health Science Building | 90.1-2004 | 7163 | 82.3333 | 4954 | 56.9425 | 30.84% | 2209 | 2nd | 7071.8136 | 81.2852 | 1.273% | 91.1864 | Health Science Building | 98379 | 1.1308 | 65154 | 0.7489 | 33.77% | 33225 | 120780.2784 | 1.3883 | -22.77% | -22401.2784 | Health Science Building | 2606625 | NA | 29.9612 | 1672375 | NA | 19.2227 | 35.84% | 934250 | 848245 | NA | 9.7499 | 67.46% | Health Science Building | 14834300 | 170.5092 | 14419316 | 2004260 | 47460 |  | 0 | 13.9186 | MSWG | 90.1-2004
Renaissance Res Hall (Foundation Project) | FSU | Jon Parsons | 11-08594-01A | 2011-09-12 | CD | No Contract (Found. Proj) | 2012-08-07 | Residence Hall | 340 | 85000 | 3 | Renaissance Res Hall (Foundation Project) | 90.1-2004 | 5499 | 64.6941 | 3624 | 42.6353 | 34.1% | 1875 | 1st | 1980 | 23.2941 | 63.99% | 3519 | Renaissance Res Hall (Foundation Project) | 174915 | 2.0578 | 88110 | 1.0366 | 49.63% | 86805 |  |  |  |  | Renaissance Res Hall (Foundation Project) | 2636463 | 7754.3029 | 31.0172 | 1734140 | 5100.4118 | 20.4016 | 34.22% | 902323 |  |  |  |  | Renaissance Res Hall (Foundation Project) | (Foundation Project) |  |  | (Foundation Project) | (Foundation Project) |  | (Foundation Project) |  | Optima | 90.1-2004
Overlook Residence Hall | UNCA | 'dtodd@unca.edu' | 09-07924-02B | 2011-02-28 | CD | 2011-07-14 | 2012-08-08 | Residence Hall | 300 | 91370 | 6 | Overlook Residence Hall | 90.1-2004 | 5737 | 62.7887 | 3460 | 37.868 | 39.69% | 2277 | 1st | 4293 | 46.9848 | 25.17% | 1444 | Overlook Residence Hall | 89281 | 0.97714 | 63609 | 0.69617 | 28.75% | 25672 | 107053 | 1.1716 | -19.91% | -17772 | Overlook Residence Hall | 2888310 | 9627.7 | 31.6111 | 1728304 | 5761.0133 | 18.9154 | 40.16% | 1160006 | 1738352 | 5794.5067 | 19.0254 | 39.81% | Overlook Residence Hall | 16467600 | 180.2298 | 14927082 | 1685000 | 0 |  | 85000 | 63.3187 | MSWG | 90.1-2004
Viking Tower Residence Hall | ECSU | Elizabeth Linney | 00-06539-03A | 2010-09-03 | CD | 2011-01-25 | 2012-08-17 | Residence Hall | 210 | 53896 | 3 | Viking Tower Residence Hall | 90.1-2004 | 9118 | 169.1777 | 6399 | 118.7287 | 29.82% | 2719 | 2nd | 2153.2685 | 39.9523 | 76.38% | 6964.7315 | Viking Tower Residence Hall | 217417 | 4.034 | 145256 | 2.6951 | 33.19% | 72161 | 66675.82 | 1.2371 | 69.33% | 150741.18 | Viking Tower Residence Hall | 1193460 | 5683.1429 | 22.1438 | 938250 | 4467.8571 | 17.4085 | 21.38% | 255210 | 1744309 | 8306.2333 | 32.3643 | -46.16% | Viking Tower Residence Hall | 12474496 | 231.455 | 12222788 | 1199950 | 40000 |  | 85000 | 5.2204 | RMF | 90.1-2004
Teaching Laboratory Building | UNCW | Steve Sharpe | 07-07129-02A | 2010-08-06 | CD | 2011-01-21 | 2012-08-24 | Office/Classroom/Labs | NA | 85000 | 3 | Teaching Laboratory Building | 90.1-2004 | 7739 | 91.0471 | 4808 | 56.5647 | 37.87% | 2931 | 1st | 14655.276 | 172.415 | -89.37% | -6916.276 | Teaching Laboratory Building | 142633 | 1.678 | 90792 | 1.0681 | 36.35% | 51841 | 197908.31 | 2.3283 | -38.75% | -55275.31 | Teaching Laboratory Building | 751030 | NA | 8.8356 | 507514 | NA | 5.9708 | 32.42% | 243516 | 626923 | NA | 7.3756 | 16.52% | Teaching Laboratory Building | 15645200 | 184.0612 | 15440699 | 2615450 | 156820 |  | 0 | 6.9698 | RMF | 90.1-2004
Rhoades Hall Renovation | UNCA | 'dtodd@unca.edu' | 06-06994-02B | 2009-05-11 | CD | 2010-04-26 | 2012-09-10 | Classroom/Lab/Offices | NA | 40434 | 3 and 4 | Rhoades Hall Renovation | 90.1-2004 | 3231 | 79.908 | 1185 | 29.307 | 63.32% | 2046 | 0 | No data |  |  |  | Rhoades Hall Renovation | 98370 | 2.4329 | 43014 | 1.0638 | 56.27% | 55356 |  |  |  |  | Rhoades Hall Renovation | 957500 | NA | 23.6806 | 655500 | NA | 16.2116 | 31.54% | 302000 |  |  |  |  | Rhoades Hall Renovation | 5996300 | 148.2985 | 5834600 | 859165 | 76500 |  | 0 |  | ESE | 90.1-2004
School of Dental Medicine / Ledyard E. Ross Hall | ECU | Les Hewlett hewlettl14@ecu.edu | 07-07054-02A | 2010-04-16 | CD | 2010-07-01 | 2012-09-14 | Offices/Classrooms/Labs | NA | 157410 | 5 | School of Dental Medicine / Ledyard E. Ross Hall | 90.1-2004 | 43253 | 274.7792 | 27864 | 177.0154 | 35.58% | 15389 | 1st | no meter data |  |  |  | School of Dental Medicine / Ledyard E. Ross Hall | 420065 | 2.6686 | 302543 | 1.922 | 27.98% | 117522 |  |  |  |  | School of Dental Medicine / Ledyard E. Ross Hall | 1373584 | NA | 8.7262 | 905161 | NA | 5.7503 | 34.1% | 468423 |  |  |  |  | School of Dental Medicine / Ledyard E. Ross Hall | 33176057 | 210.7621 | 32922547 | 5394860 | 100000 |  | 346397 |  | BR+A | 90.1-2004
Lena Sue Beam Renovation | Gaston CC | Cynthia McCrory | 07-07395-02A | 2011-03-03 | CD | 2011-07-29 | 2012-10-03 | Office/Classroom | NA | 31418 | 2 | Lena Sue Beam Renovation | 90.1-2004 | 1732 | 55.1276 | 1161 | 36.9533 | 32.97% | 571 | 1st | no meter data |  |  |  | Lena Sue Beam Renovation | 36406 | 1.1588 | 25403 | 0.80855 | 30.22% | 11003 |  |  |  |  | Lena Sue Beam Renovation | 689715 | NA | 21.9529 | 403299 | NA | 12.8366 | 41.53% | 286416 |  |  |  |  | Lena Sue Beam Renovation | 4701800 | 149.6531 | 4657494 | 474000 | 0 |  | 56984 | 9.2057 | M&L | 90.1-2004
Hunt Library | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 07-07171-02A | 2010-08-06 | CD-2 | 2009-08-25 | 2012-10-18 | Library/Offices/Lecture Hall/Meeting | NA | 253028 | 4 | Hunt Library | 90.1-2004 | 15191 | 60.0368 | 10342 | 40.8729 | 31.92% | 4849 | 1st | 61448.3697 | 242.8521 | -304.5% | -46257.3697 | Hunt Library | 268448 | 1.0609 | 184680 | 0.72988 | 31.2% | 83768 | 1030347.1539 | 4.0721 | -283.8% | -761899.1539 | Hunt Library | 4536750 | NA | 17.9298 | 2948625 | NA | 11.6534 | 35.01% | 1588125 | 1866456.3085 | NA | 7.3765 | 58.86% | Hunt Library | 81306000 | 321.332 | 80844228 | 9829956 | 200000 |  | 605005 |  | AEI | 90.1-2004
Judy W. Rose Football Center | UNCC | Tony Schallert | 08-07833-02A | 2010-12-10 | CD | 2011-03-29 | 2012-10-31 | Lockerrooms/Offices | NA | 43290 | 2 | Judy W. Rose Football Center | 90.1-2004 | 8320 | 192.1922 | 5184 | 119.7505 | 37.69% | 3136 | 1st | 9183.5274 | 212.1397 | -10.38% | -863.5274 | Judy W. Rose Football Center | 65175 | 1.5055 | 44151 | 1.0199 | 32.26% | 21024 | 138366.5075 | 3.1963 | -112.3% | -73191.5075 | Judy W. Rose Football Center | 1349491 | NA | 31.1733 | 1113354 | NA | 25.7185 | 17.5% | 236137 | 772504.48 | NA | 17.8449 | 42.76% | Judy W. Rose Football Center | 12987000 | 300 | 12521456 | 3448472 | 45000 |  | 99500 |  | M&C | 90.1-2004
Veteran's Nursing Home - Kinston | NCDOA-VA | diane.norris@doa.nc.gov | 06-06924-05A | 2009-12-22 | CD | 2010-05-24 | 2012-10-31 | Nursing Home | 100 | 108770 | 1 | Veteran's Nursing Home - Kinston | 90.1-2004 | 8495 | 78.1006 | 5163 | 47.4671 | 39.22% | 3332 | 1st | 7567.2234 | 69.5709 | 10.92% | 927.7766 | Veteran's Nursing Home - Kinston | 213106 | 1.9592 | 120807 | 1.1107 | 43.31% | 92299 | 167570.51 | 1.5406 | 21.37% | 45535.49 | Veteran's Nursing Home - Kinston | 4378540 | 43785.4 | 40.255 | 3400982 | 34009.82 | 31.2676 | 22.33% | 977558 | 1567490 | 15674.9 | 14.4111 | 64.2% | Veteran's Nursing Home - Kinston | 12903000 | 118.6265 | 12602128 | 1077600 | 0 |  | 107804 | 4.4277 | MCBH | 90.1-2004
Klaussner Building Renovation | Randolph CC | Cindi Goodwin | 07-07252-03A | 2010-12-08 | CD | 2011-10-14 | 2012-11-27 | Office/Classroom/Labs | NA | 43967 | 1 | Klaussner Building | 90.1-2004 | 2940 | 66.8683 | 1839 | 41.8268 | 37.45% | 1101 | 1st | 3017.583 | 68.6329 | -2.639% | -77.583 | Klaussner Building | 67485 | 1.5349 | 43675 | 0.99336 | 35.28% | 23810 | 68964.5 | 1.5686 | -2.192% | -1479.5 | Klaussner Building | 544858 | NA | 12.3924 | 436998 | NA | 9.9392 | 19.8% | 107860 | 1167628 | NA | 26.5569 | -114.3% | Klaussner Building | 6361300 | 144.6835 | 6060565 | 363200 | 0 |  | 49800 | 14.7222 | PDC | 90.1-2004
Plemmons Student Union Addition | ASU | Jerry Marshall | 08-07327-02A | 2010-08-19 | CD | 2010-06-08 | 2012-12-18 | Office/Classroom/Conference | NA | 50560 | 4 | Plemmons Student Union | 90.1-2004 | 2185 | 43.216 | 1346 | 26.6218 | 38.4% | 839 | 1st | 15303.0469 | 141.6568 | -600.4% | -13118.0469 | Plemmons Student Union | 53367 | 1.0555 | 32912 | 0.65095 | 38.33% | 20455 | 357284.9634 | 3.3073 | -569.5% | -303917.9634 | Plemmons Student Union | 1220706 | NA | 24.1437 | 950466 | NA | 18.7988 | 22.14% | 270240 | 4243580.459 | NA | 39.2819 | -247.6% | Plemmons Student Union | 15232506 | 301.2758 | 14629006 | 985521.6 | 90950 |  | 71248.14 | 37.4333 | SKA | 90.1-2004
Summit Residence Hall & Appalachian Hall | ASU | Jerry Marshall | 08-07327-02A | 2010-08-19 | CD | 2010-06-08 | 2012-12-18 | Residence Hall / Office Classrooms | 333 | 128585 | 11 and 3 | Summit Residence Hall & Appalachian Hall | 90.1-2004 | 6323 | 49.1737 | 3660 | 28.4637 | 42.12% | 2663 | 1st | 9131.9133 | 71.0185 | -44.42% | -2808.9133 | Summit Residence Hall & Appalachian Hall | 153208 | 1.1915 | 89024 | 0.69234 | 41.89% | 64184 | 228963.9489 | 1.7806 | -49.45% | -75755.9489 | Summit Residence Hall & Appalachian Hall | 3388865 | 10176.7718 | 26.3551 | 1928009 | 5789.8168 | 14.994 | 43.11% | 1460856 | 2066184.368 | 6204.7579 | 16.0686 | 39.03% | Summit Residence Hall & Appalachian Hall | 40691217 | 316.4538 | 39309739 | 2664558.4 | 94925 |  | 192633.86 | 26.0039 | SKA | 90.1-2004
MARBIONC | UNCW | Steve Sharpe | 07-07853-02A | 2010-06-03 | DD | 2011-08-01 | 2013-01-29 | Labs/Offices | NA | 68000 | 2 | MARBIONIC | 90.1-2004 | 31233 | 459.3088 | 19781 | 290.8971 | 36.67% | 11452 | 1st | 17208.4869 | 253.066 | 44.9% | 14024.5131 | MARBIONIC | 425995 | 6.2646 | 301801 | 4.4383 | 29.15% | 124194 | 291901.88 | 4.2927 | 31.48% | 134093.12 | MARBIONIC | 5139169 | NA | 75.576 | 4083469 | NA | 60.051 | 20.54% | 1055700 | no meter data |  |  |  | MARBIONIC | 24371201 | 358.4 | 19975000 | 2804957 | 110280 |  | 294243 | 38.655 | CRB/AEI | 90.1-2004
NC State Bar HQ (Private bldg state land) | DOA | Joe Cerone <jcerone@ncbar.gov> | 09-07858-01A | 2011-05-31 | CD | 2011-11-28 | 2013-04-25 | Office/Courtroom | NA | 54565 | 4 | NC State Bar HQ | 90.1-2004 | 1689 | 30.9539 | 1116 | 20.4527 | 33.93% | 573 | 1st | 3008.9008 | 55.1434 | -78.15% | -1319.9008 | NC State Bar HQ | 45238 | 0.82907 | 29457 | 0.53985 | 34.88% | 15781 | 75973.5 | 1.3923 | -67.94% | -30735.5 | NC State Bar HQ | 175310 | NA | 3.2129 | 116629 | NA | 2.1374 | 33.47% | 58681 | 175780 | NA | 3.2215 | -0.2681% | NC State Bar HQ | 12962700 | 237.5644 | 12687413 | 1125000 | 6000 |  | 56200 | 21.3857 | CJMW | 90.1-2004
Science and Technology Building | FSU | Jon Parsons | 06-06971-02A | 2011-01-11 | Final | 2011-06-27 | 2013-05-21 | Office/Classrooms/Labs | NA | 65861 | 4 | Science and Technology Building | 90.1-2004 | 13356 | 202.7907 | 9641 | 146.3841 | 27.82% | 3715 | 0 | No data |  |  |  | Science and Technology Building | 151889 | 2.3062 | 100888 | 1.5318 | 33.58% | 51001 |  |  |  |  | Science and Technology Building | 2163492 | NA | 32.8494 | 1785946 | NA | 27.1169 | 17.45% | 377546 |  |  |  |  | Science and Technology Building | 17028032 | 258.545 | 16327000 | 1576000 | 135000 |  | 290182 | 22.0822 | M&C | 90.1-2004
Student Recreation Facility Addition | UNCW | Steve Sharpe | 07-07060-03A | 2010-06-02 | CD | 2011-04-25 | 2013-05-22 | Gym/pool/fitness/courts/lockerrom | NA | 93917 | 2 | Student Recreation Facility Addition | 90.1-2004 | 22917 | 244.0133 | 15931 | 169.6285 | 30.48% | 6986 | 1st | 34139.341 | 363.5054 | -48.97% | -11222.341 | Student Recreation Facility Addition | 351452 | 3.7422 | 248190 | 2.6427 | 29.38% | 103262 | 242520.84 | 2.5823 | 30.99% | 108931.16 | Student Recreation Facility Addition | 810220 | NA | 8.627 | 634243 | NA | 6.7532 | 21.72% | 175977 | 1167500 | NA | 12.4312 | -44.1% | Student Recreation Facility Addition | 21478228 | 228.6937 | 20845432 | 2510110 | 215000 |  | 126000 | 9.4303 | SWA | 90.1-2004
CSS Neuse Gunboat Facility NOT SB668 | DoCR |  | 04-06449-01C | 2010-09-30 | CD | 2011-03-28 | 2013-06-21 | Museum/Exhibits | NA | 30000 | 2 | CSS Neuse Gunboat Facility NOT SB668 | 90.1-2004 | 1854 | 61.8 | 1119 | 37.3 | 39.64% | 735 | 0 |  |  |  |  | CSS Neuse Gunboat Facility NOT SB668 | 81247 | 2.7082 | 62132 | 2.0711 | 23.53% | 19115 |  |  |  |  | CSS Neuse Gunboat Facility NOT SB668 | 36402 | NA | 1.2134 | 28077 | NA | 0.9359 | 22.87% | 8325 |  |  |  |  | CSS Neuse Gunboat Facility NOT SB668 | 2610700 |  |  | 846024 | 10000 |  | 0 |  | Atl | 90.1-2004
Reaves Student Activities Center | WSSU | Dick Kabis | 06-07181-01A | 2010-10-25 | CD | 2011-05-17 | 2013-06-24 | Gym/Food Service/ | NA | 91513 | 3 | Reaves Student Activities Center | 90.1-2004 | 7587 | 82.9063 | 5004 | 54.6808 | 34.05% | 2583 | 1st | 10913.3464 | 119.2546 | -43.84% | -3326.3464 | Reaves Student Activities Center | 105529 | 1.1532 | 66125 | 0.72257 | 37.34% | 39404 | 165975.109 | 1.8137 | -57.28% | -60446.109 | Reaves Student Activities Center | 1434603 | NA | 15.6765 | 990985 | NA | 10.8289 | 30.92% | 443618 | 679393.971 | NA | 7.424 | 52.64% | Reaves Student Activities Center | 25393206 | 277.482 | 25315267 | 2408119 | 177240 |  | 287625 | 13.7754 | Sud | 90.1-2004
Belk/Walnut Residence Hall (Phase X) | UNCC | Tony Schallert | 10-08450-02A | 2011-12-22 | CD-2 | 2012-01-17 | 2013-07-09 | Residence Hall | 400 | 164377 | 5 | Belk/Walnut Residence Hall (Phase X) | 90.1-2004 | 10765 | 65.4897 | 7239 | 44.039 | 32.75% | 3526 | 1st | 10913.3464 | 66.3922 | -1.378% | -148.3464 | Belk/Walnut Residence Hall (Phase X) | 149183 | 0.90757 | 97190 | 0.59126 | 34.85% | 51993 | 153565.9875 | 0.93423 | -2.938% | -4382.9875 | Belk/Walnut Residence Hall (Phase X) | 2719308 | 6798.27 | 16.5431 | 1869230 | 4673.075 | 11.3716 | 31.26% | 850078 | 4496320 | 11240.8 | 27.3537 | -65.35% | Belk/Walnut Residence Hall (Phase X) | 30027284 | 182.6733 | 30027284 | 2167790 | 126000 |  | 186000 |  |  | 90.1-2004
Cherry Building Renovation | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 10-08698-02A | 2011-11-17 | CD | 2012-07-12 | 2013-07-15 | Office/Classroom | NA | 22482 | 2.5 | Cherry Building Renovation | 90.1-2004 | 1449 | 64.4516 | 1017 | 45.2362 | 29.81% | 432 | 1st | 707.1029 | 31.452 | 51.2% | 741.8971 | Cherry Building Renovation | 27666 | 1.2306 | 21821 | 0.9706 | 21.13% | 5845 | 15342.1 | 0.68242 | 44.55% | 12323.9 | Cherry Building Renovation | 166500 | NA | 7.4059 | 120425 | NA | 5.3565 | 27.67% | 46075 | 8228 | NA | 0.36598 | 95.06% | Cherry Building Renovation | 2670270 | 118.7737 | 2645494 | 292501 | 0 |  | 0 |  | SWA | 90.1-2004
Hunt Residence Hall (Phase XI) | UNCC | Tony Schallert | 10-08610-03A | 2012-02-24 | CD | 2012-01-17 | 2013-07-29 | Residence Hall | 436 | 144175 | 5 | Hunt Residence Hall | 90.1-2004 | 11671 | 80.9502 | 6976 | 48.3856 | 40.23% | 4695 | 1st | 13345.2725 | 92.563 | -14.35% | -1674.2725 | Hunt Residence Hall | 141674 | 0.98265 | 87499 | 0.60689 | 38.24% | 54175 | 108713.3726 | 0.75404 | 23.27% | 32960.6274 | Hunt Residence Hall | 1100206 | 2523.4083 | 7.631 | 860579 | 1973.805 | 5.969 | 21.78% | 239627 | 3310737.76 | 7593.4352 | 22.9633 | -200.9% | Hunt Residence Hall | 24655367 | 171.01 | 22816693 | 2078598 | 0 |  | 297680 |  |  | 90.1-2004
Wolf Ridge at Centennial Bldg 6 - Tower Hall | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-08-01 | Residence Hall | 151 | 67202 | 6 | Wolf Ridge at Centennial Bldg 6 | 90.1-2004 | 4126 | 61.397 | 2853 | 42.4541 | 30.85% | 1273 | 1st | 1586.1423 | 23.6026 | 61.56% | 2539.8577 | Wolf Ridge at Centennial Bldg 6 | 76622 | 1.1402 | 51093 | 0.76029 | 33.32% | 25529 | 75688.0681 | 1.1263 | 1.219% | 933.9319 | Wolf Ridge at Centennial Bldg 6 | 1630661 | 10799.0795 | 24.2651 | 1029702 | 6819.2185 | 15.3225 | 36.85% | 600959 | 967912 | 6410.0132 | 14.403 | 40.64% | Wolf Ridge at Centennial Bldg 6 | 14207759 | 211.4187 | 11410139.74 | 995826.9923 | 0 |  | 47050.2499 |  | Dewberry | 90.1-2004
Wolf Ridge at Centennial Bldg 1 - Lakeview Hall | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-08-01 | Residence Hall | 251 | 154726 | 6 | Wolf Ridge at Centennial Bldg 1 | 90.1-2004 | 12056 | 77.9184 | 8300 | 53.6432 | 31.15% | 3756 | 1st | 5779.4535 | 37.3528 | 52.06% | 6276.5465 | Wolf Ridge at Centennial Bldg 1 | 220350 | 1.4241 | 143383 | 0.92669 | 34.93% | 76967 | 295899.1122 | 1.9124 | -34.29% | -75549.1122 | Wolf Ridge at Centennial Bldg 1 | 5618485 | 22384.4024 | 36.3125 | 4483837 | 17863.8924 | 28.9792 | 20.19% | 1134648 | 1626900 | 6481.6733 | 10.5147 | 71.04% | Wolf Ridge at Centennial Bldg 1 | 32712171 | 211.42 | 26270927.62 | 2292793.7742 | 0 |  | 108328.5759 |  | Dewberry | 90.1-2004
Spartan Village -1 - Lee | UNCG | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 243 | 116224 | 5 | Spartan Village - Building 1 | 90.1-2004 | 5889 | 50.6694 | 4141 | 35.6295 | 29.68% | 1748 | 1st | 6865.098 | 59.0678 | -16.57% | -976.098 | Spartan Village - Building 1 | 127318 | 1.0955 | 80286 | 0.69079 | 36.94% | 47032 | 76867 | 0.66137 | 39.63% | 50451 | Spartan Village - Building 1 | 2900134 | 11934.7078 | 24.953 | 2258696 | 9295.0453 | 19.434 | 22.12% | 641438 | 1823624 | 7504.6255 | 15.6906 | 37.12% | Spartan Village - Building 1 | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Spartan Village - 3 - Haywood | UNCG | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 130 | 56295 | 5 | Spartan Village - Building 3 | 90.1-2004 | 5889 | 104.6096 | 4141 | 73.5589 | 29.68% | 1748 | 1st | 2459.3069 | 43.6861 | 58.24% | 3429.6931 | Spartan Village - Building 3 | 127318 | 2.2616 | 80286 | 1.4262 | 36.94% | 47032 | 53426.13 | 0.94904 | 58.04% | 73891.87 | Spartan Village - Building 3 | 1736095 | 13354.5769 | 30.8392 | 1384588 | 10650.6769 | 24.5952 | 20.25% | 351507 | 1306008 | 10046.2154 | 23.1994 | 24.77% | Spartan Village - Building 3 | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Spartan Village - Building 4 | UNCG | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2013-08-07 | Residence Hall | 209 | 89104 | 5 | Spartan Village - Building 4 | 90.1-2004 | 5889 | 66.0913 | 4141 | 46.4738 | 29.68% | 1748 | 1st | 2092.5003 | 23.4838 | 64.47% | 3796.4997 | Spartan Village - Building 4 | 127318 | 1.4289 | 80286 | 0.90104 | 36.94% | 47032 | 50951.17 | 0.57182 | 59.98% | 76366.83 | Spartan Village - Building 4 | 2627757 | 12573 | 29.4909 | 2069683 | 9902.7895 | 23.2277 | 21.24% | 558074 | 1306008 | 6248.8421 | 14.6571 | 50.3% | Spartan Village - Building 4 | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | SWA | 90.1-2004
Martin-Schexnider Residence Hall | WSSU | Dick Kabis | 11-09099-02A | 2012-07-18 | CD | No Contract (Privately Funded) | 2013-08-13 | Residence Hall | 227 | 55626 | 5 | Martin-Schexnider Residence Hall | 90.1-2004 | 6193 | 111.3328 | 4672 | 83.9895 | 24.56% | 1521 | 1st | 7952.971 | 142.9722 | -28.42% | -1759.971 | Martin-Schexnider Residence Hall | 87219 | 1.568 | 53012 | 0.95301 | 39.22% | 34207 | 62831.3647 | 1.1295 | 27.96% | 24387.6353 | Martin-Schexnider Residence Hall | 2317437 | 10208.9736 | 41.661 | 1848705 | 8144.0749 | 33.2345 | 20.23% | 468732 | 1375634.028 | 6060.0618 | 24.7301 | 40.64% | Martin-Schexnider Residence Hall | 10000000 |  | 9516280 | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  | M&C | 90.1-2004
Union Station | Cape Fear CC | Ken Pearce | 07-07399-03A | 2010-05-05 | CD | 2010-11-10 | 2013-08-22 | Office/Classroom/Auditorium | NA | 233900 | 6 | Union Station | 90.1-2004 | 12463 | 53.2835 | 8391 | 35.8743 | 32.67% | 4072 | 0 | No data |  |  |  | Union Station | 407210 | 1.741 | 294497 | 1.2591 | 27.68% | 112713 |  |  |  |  | Union Station | 1939781 | NA | 8.2932 | 1222056 | NA | 5.2247 | 37% | 717725 |  |  |  |  | Union Station | 38141300 | 163.0667 | 37627193 | 6113085 | 339250 |  | 237711 | 9.6801 | Cheatham | 90.1-2004
Smith-Williams Center Minges Practice Facility | ECU | Les Hewlett hewlettl14@ecu.edu | 08-07305-01F | 2012-03-01 | CD | 2012-05-01 | 2013-08-27 | Gym/Office | NA | 49170 | 2 | Minges Practice Facility | 90.1-2004 | 2396 | 48.7289 | 1518 | 30.8725 | 36.64% | 878 | 1st | meter data incomplete |  |  |  | Minges Practice Facility | 48568 | 0.98776 | 38507 | 0.78314 | 20.72% | 10061 | meter data incomplete |  |  |  | Minges Practice Facility | 347984 | NA | 7.0772 | 227682 | NA | 4.6305 | 34.57% | 120302 | meter data incomplete |  |  |  | Minges Practice Facility | 13828376 | 281.236 | 12357348 | 736500 |  |  | 128800 |  | Edi | 90.1-2004
Wolf Ridge at Centennial Bldg 2 | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2013-12-05 | Residence Hall | 223 | 84876 | 6 | Wolf Ridge at Centennial Bldg 2 | 90.1-2004 | 5653 | 66.603 | 3934 | 46.35 | 30.41% | 1719 | 0 |  |  |  |  | Wolf Ridge at Centennial Bldg 2 | 102040 | 1.2022 | 70049 | 0.82531 | 31.35% | 31991 |  |  |  |  | Wolf Ridge at Centennial Bldg 2 | 2385879 | 10699.009 | 28.1102 | 1498371 | 6719.1525 | 17.6536 | 37.2% | 887508 |  |  |  |  | Wolf Ridge at Centennial Bldg 2 | 17944484 | 211.42 | 14286216 | 1257727.6242 | 0 |  | 59424.3774 |  |  | 90.1-2004
Spartan Village - Building 2 | UNCG | Douglas Cato | 11-08879-01A | 2011-10-24 | DD | No Contract (Privately Funded) | 2014-01-09 | Residence Hall | 231 | 110627 | 5 | Spartan Village - Building 2 | 90.1-2004 | 5889 | 53.2329 | 4141 | 37.4321 | 29.68% | 1748 | 0 |  |  |  |  | Spartan Village - Building 2 | 127318 | 1.1509 | 80286 | 0.72574 | 36.94% | 47032 |  |  |  |  | Spartan Village - Building 2 | 2916495 | 12625.5195 | 26.3633 | 2297942 | 9947.8009 | 20.772 | 21.21% | 618553 |  |  |  |  | Spartan Village - Building 2 | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | 90.1-2004
PORTAL | UNCC | Tony Schallert | 08-07560-03A | 2011-02-03 | CD | 2012-04-09 | 2014-01-28 | Office | NA | 102914 | 4 | PORTAL | 90.1-2004 | 7934 | 77.0935 | 5513 | 53.569 | 30.51% | 2421 | 0 |  |  |  |  | PORTAL | 142246 | 1.3822 | 98494 | 0.95705 | 30.76% | 43752 |  |  |  |  | PORTAL | 776459 | NA | 7.5447 | 565009 | NA | 5.4901 | 27.23% | 211450 |  |  |  |  | PORTAL | 25748184 | 250.1913 |  | 2215000 | none noted |  | 240424 |  | M&C | 90.1-2004
Wolf Ridge at Centennial Bldg 3 | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-02-06 | Residence Hall | 219 | 88512 | 6 | Wolf Ridge at Centennial Bldg 3 | 90.1-2004 | 5069 | 57.2691 | 3543 | 40.0285 | 30.1% | 1526 | 0 |  |  |  |  | Wolf Ridge at Centennial Bldg 3 | 91459 | 1.0333 | 63494 | 0.71735 | 30.58% | 27965 |  |  |  |  | Wolf Ridge at Centennial Bldg 3 | 2343922 | 10702.8402 | 26.4814 | 1472334 | 6722.9863 | 16.6343 | 37.19% | 871588 |  |  |  |  | Wolf Ridge at Centennial Bldg 3 | 18713207 | 211.42 |  | 1311607.3739 | none noted |  | 61970.0562 |  | Dewberry | 90.1-2004
Hill Hall Renovation - Student Success Center | WSSU | Dick Kabis | 11-08884-03A | 2012-09-27 | CD | 2012-12-13 | 2014-03-25 | Offices | NA | 37898 | 3 | Hill Hall Renovation - Student Success Center | 90.1-2007 | 2638 | 69.6079 | 1913 | 50.4776 | 27.48% | 725 | 0 |  |  |  |  | Hill Hall Renovation - Student Success Center | 41267 | 1.0889 | 25579 | 0.67494 | 38.02% | 15688 |  |  |  |  | Hill Hall Renovation - Student Success Center | 2719308 | NA | 71.7533 | 1869230 | NA | 49.3227 | 31.26% | 850078 |  |  |  |  | Hill Hall Renovation - Student Success Center | 10890470 | 287.3627 |  | 1125000 | 100000 |  | 90000 |  | CN | 90.1-2007
Wolf Ridge at Centennial Bldg 5 | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-04-09 | Residence Hall | 144 | 62645 | 6 | Wolf Ridge at Centennial Bldg 5 | 90.1-2004 | 3959 | 63.1974 | 2756 | 43.9939 | 30.39% | 1203 | 0 |  |  |  |  | Wolf Ridge at Centennial Bldg 5 | 73439 | 1.1723 | 49084 | 0.78353 | 33.16% | 24355 |  |  |  |  | Wolf Ridge at Centennial Bldg 5 | 1557237 | 10814.1458 | 24.8581 | 984137 | 6834.2847 | 15.7097 | 36.8% | 573100 |  |  |  |  | Wolf Ridge at Centennial Bldg 5 | 13244406 | 211.42 |  | 928299.4841 | none noted |  | 43859.7498 |  | Dewberry | 90.1-2004
Wolf Ridge at Centennial Bldg 4 | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 08-07880-02B | 2011-10-03 | CD | 2011-09-30 | 2014-05-09 | Residence Hall | 219 | 83460 | 6 | Wolf Ridge at Centennial Bldg 4 | 90.1-2004 | 5197 | 62.2694 | 3476 | 41.6487 | 33.12% | 1721 | 0 |  |  |  |  | Wolf Ridge at Centennial Bldg 4 | 96219 | 1.1529 | 61768 | 0.74009 | 35.8% | 34451 |  |  |  |  | Wolf Ridge at Centennial Bldg 4 | 2343922 | 10702.8402 | 28.0844 | 1472334 | 6722.9863 | 17.6412 | 37.19% | 871588 |  |  |  |  | Wolf Ridge at Centennial Bldg 4 | 17645113 | 211.42 |  | 1236744.7513 | none noted |  | 58432.9909 |  | Dewberry | 90.1-2004
Aviation Classroom Bldg | GTCC |  | 08-07309-02A | 2012-03-09 | CD | 2012-09-17 | 2014-07-21 | Office/Classroom | NA | 42087 | 4 | Aviation Classroom Bldg | 90.1-2004 | 2425 | 57.6187 | 1699 | 40.3688 | 29.94% | 726 | 0 |  |  |  |  | Aviation Classroom Bldg | 68705 | 1.6325 | 55378 | 1.3158 | 19.4% | 13327 |  |  |  |  | Aviation Classroom Bldg | 1135125 | NA | 26.9709 | 550575 | NA | 13.0818 | 51.5% | 584550 |  |  |  |  | Aviation Classroom Bldg | 6535600 | 155.2879 |  | 686500 | 20000 |  | 149249 |  | SWA | 90.1-2004
Martin Residence Hall (Phase XII) | UNCC | Tony Schallert | 11-09156-02A | 2012-12-19 | CD | 2013-04-05 | 2014-08-13 | Residence Hall | 408 | 174657 | 6 | Martin Residence Hall (Phase XII) | 90.1-2007 | 21396 | 122.503 | 13060 | 74.7751 | 38.96% | 8336 | 0 |  |  |  |  | Martin Residence Hall (Phase XII) | 306609 | 1.7555 | 210750 | 1.2067 | 31.26% | 95859 |  |  |  |  | Martin Residence Hall (Phase XII) | 4970906 | 12183.5931 | 28.461 | 3510140 | 8603.2843 | 20.0973 | 29.39% | 1460766 |  |  |  |  | Martin Residence Hall (Phase XII) | 35192772 | 201.4965 | 29686104 | 2733245 | 15000 |  | 175000 | 59.4276 |  | 90.1-2007
New Library Building | UNCSA |  | 06-06981-05A | 2012-07-27 | FI | 2013-01-18 | 2014-09-09 | Library/Offices | NA | 73432 | 4 | New Library Building | 90.1-2004 | 6402 | 87.1827 | 4631 | 63.0651 | 27.66% | 1771 | 0 |  |  |  |  | New Library Building | 90245 | 1.229 | 62106 | 0.84576 | 31.18% | 28139 |  |  |  |  | New Library Building | 706800 | NA | 9.6252 | 478350 | NA | 6.5142 | 32.32% | 228450 |  |  |  |  | New Library Building | 15433000 | 210.1672 | 17328709 | 1833332 | 0 |  | 108825 | -63.502 |  | 90.1-2004
South Village Dining Facility | UNCC | Tony Schallert | 10-08633-03A | 2013-04-17 | FI | 2012-10-04 | 2014-10-02 | Food Service/Dining | NA | 56146 | 2 | South Village Dining Facility | 90.1-2004 | 12578 | 224.0231 | 7334 | 130.6237 | 41.69% | 5244 | 0 |  |  |  |  | South Village Dining Facility | 163454 | 2.9112 | 113314 | 2.0182 | 30.68% | 50140 |  |  |  |  | South Village Dining Facility | 546557 | NA | 9.7346 | 435029 | NA | 7.7482 | 20.41% | 111528 |  |  |  |  | South Village Dining Facility | 26618418.39 | 474.0929 | 25649718.39 | 1918410 | 78000 |  | 182024 | 24.5059 | M&C | 90.1-2004
Student Health Center | NCA&T |  | 08-08109-01A | 2011-12-21 | DD | 2013-04-08 | 2014-10-07 | Offices/Clinics | NA | 27548 | 2 | Student Health Center | 90.1-2004 | 1911 | 69.3698 | 1336 | 48.4972 | 30.09% | 575 | 0 |  |  |  |  | Student Health Center | 50033 | 1.8162 | 33648 | 1.2214 | 32.75% | 16385 |  |  |  |  | Student Health Center | 154588 | NA | 5.6116 | 101825 | NA | 3.6963 | 34.13% | 52763 |  |  |  |  | Student Health Center | 7444000 | 270.2193 |  | 785500 | 92000 |  | 51400 |  |  | 90.1-2004
Center for Design Innovation | WSSU | Dick Kabis | 06-06646-03A | 2013-05-03 | FI | 2012-04-12 | 2014-10-12 | Office/Labs | NA | 23982 | 3 | Center for Design Innovation | 90.1-2007 | 4288 | 178.8008 | 2361 | 98.4488 | 44.94% | 1927 | 0 |  |  |  |  | Center for Design Innovation | 106582 | 4.4442 | 65369 | 2.7258 | 38.67% | 41213 |  |  |  |  | Center for Design Innovation | 67775 | NA | 2.8261 | 44733 | NA | 1.8653 | 34% | 23042 |  |  |  |  | Center for Design Innovation | 8727727 | 363.9282 | 6497174 | 700000 | 50000 |  | 80300 | 57.2842 | RMF | 90.1-2007
Film School Production Design Facility | UNCSA |  | 08-08115-03A | 2012-03-30 | CD | 2013-04-11 | 2014-10-30 | Various | NA | 29936 | 2 | Film School Production Design Facility | 90.1-2004 | 8887 | 296.8666 | 5860 | 195.7509 | 34.06% | 3027 | 0 |  |  |  |  | Film School Production Design Facility | 148285 | 4.9534 | 99346 | 3.3186 | 33% | 48939 |  |  |  |  | Film School Production Design Facility | 55005 | NA | 1.8374 | 40257 | NA | 1.3448 | 26.81% | 14748 |  |  |  |  | Film School Production Design Facility | 7820696 | 261.2472 |  | 827850 | none noted |  | 47760 |  |  | 90.1-2004
Dining Hall Renovation | UNCG | Douglas Cato | 08-07382-02A | 2011-04-28 | CD | 2011-06-06 | 2014-10-31 | Food Service/Dining | NA | 111160 | 2 | Dining Hall Renovation | 90.1-2004 | 18584 | 167.1824 | 12522 | 112.6484 | 32.62% | 6062 | 0 |  |  |  |  | Dining Hall Renovation | 269366 | 2.4232 | 187898 | 1.6903 | 30.24% | 81468 |  |  |  |  | Dining Hall Renovation | 6216053 | NA | 55.9199 | 3532573 | NA | 31.7792 | 43.17% | 2683480 |  |  |  |  | Dining Hall Renovation | 28459035 | 256.0187 |  | 2837884 | 60000 |  | 283540 |  | M&L | 90.1-2004
Campus Police Facility | UNCG | Douglas Cato | 10-08905-03A | 2012-03-29 | CD | 2012-11-01 | 2014-10-31 | Offices | NA | 25877 | 2 | Campus Police Facility | 90.1-2004 | 2330 | 90.0413 | 1242 | 47.9963 | 46.7% | 1088 | 0 |  |  |  |  | Campus Police Facility | 44281 | 1.7112 | 29471 | 1.1389 | 33.45% | 14810 |  |  |  |  | Campus Police Facility | 617945 | NA | 23.8801 | 478128 | NA | 18.4769 | 22.63% | 139817 |  |  |  |  | Campus Police Facility | 6143700 | 237.4193 |  | 854040 | 43000 |  | 81680 |  | SWA | 90.1-2004
Central Storage Facility | UNCSA |  | 08-07844-03A | 2012-05-23 | CD | 2013-05-01 | 2014-10-31 | Warehouse/Storage | NA | 43637 | 2 | Central Storage Facility | 90.1-2007 | 1506 | 34.512 | 754 | 17.2789 | 49.93% | 752 | 0 |  |  |  |  | Central Storage Facility | 27891 | 0.63916 | 14976 | 0.34319 | 46.31% | 12915 |  |  |  |  | Central Storage Facility | 128138 | NA | 2.9365 | 58898 | NA | 1.3497 | 54.04% | 69240 |  |  |  |  | Central Storage Facility | 5260039 | 120.5408 | 1412707 | 596884 | 0 |  | 65343 |  |  | 90.1-2007
Campus Police Facility | UNCSA |  | 08-07845-03A | 2012-04-05 | CD | 2013-05-30 | 2014-10-31 | Offices | NA | 9023 | 2 | Campus Police Facility | 90.1-2004 | 1171 | 129.7795 | 689 | 76.3604 | 41.16% | 482 | 0 |  |  |  |  | Campus Police Facility | 18288 | 2.0268 | 12209 | 1.3531 | 33.24% | 6079 |  |  |  |  | Campus Police Facility | 289717 | NA | 32.1087 | 195438 | NA | 21.66 | 32.54% | 94279 |  |  |  |  | Campus Police Facility | 3059704 | 339.1005 |  | 292220 | none noted |  | 68561 |  | SWA | 90.1-2004
Jones Student Center - Renovation and Addition | FSU | Jon Parsons | 11-09090-03A | 2013-06-28 | FI | 2013-05-16 | 2015-01-16 | Assembly/Dining/Offices | NA | 82961 | 2 | Jones Student Center - Renovation and Addition | 90.1-2007 | 14304 | 172.4184 | 11048 | 133.171 | 22.76% | 3256 | 0 |  |  |  |  | Jones Student Center - Renovation and Addition | 215110 | 2.5929 | 143121 | 1.7252 | 33.47% | 71989 |  |  |  |  | Jones Student Center - Renovation and Addition | 4017684 | NA | 48.4286 | 3910346 | NA | 47.1348 | 2.672% | 107338 |  |  |  |  | Jones Student Center - Renovation and Addition | 17090447 | 206.0058 | 16915711 | 1536300 | 0 |  | 207560 | 5.3105 | Optima | 90.1-2007
Talley Student Center Renovation and Addition | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 08-07847-03A | 2012-02-22 | CD | 2011-02-21 | 2015-02-03 | Offices/Theater/Conference/Food Service/Book Store | NA | 294736 | 5 | Talley Student Center Renovation and Addition | 90.1-2004 | 41725 | 141.5674 | 27808 | 94.3488 | 33.35% | 13917 | 0 |  |  |  |  | Talley Student Center Renovation and Addition | 940212 | 3.19 | 699461 | 2.3732 | 25.61% | 240751 |  |  |  |  | Talley Student Center Renovation and Addition | 1088442 | NA | 3.6929 | 869385 | NA | 2.9497 | 20.13% | 219057 |  |  |  |  | Talley Student Center Renovation and Addition | 89115690 | 302.3577 |  | 9079497 | 178918 |  | 526000 |  | SWA | 90.1-2004
Belk Residence Hall Replacement East and West | ECU | Les Hewlett hewlettl14@ecu.edu | 11-09246-03A | 2013-10-03 | CD | 2013-05-22 | 2015-03-25 | Residence Hall | 720 | 208077 | 5 | Belk Residence Hall Replacement East and West | 90.1-2007 | 22829 | 109.7142 | 15444 | 74.2225 | 32.35% | 7385 | 0 |  |  |  |  | Belk Residence Hall Replacement East and West | 519318 | 2.4958 | 339219 | 1.6303 | 34.68% | 180099 |  |  |  |  | Belk Residence Hall Replacement East and West | 11970900 | 16626.25 | 57.5311 | 7250002 | 10069.4472 | 34.8429 | 39.44% | 4720898 |  |  |  |  | Belk Residence Hall Replacement East and West | 48137413 | 231.3442 | 41707231 | 3917050 | 91100 |  | 322840 | 38.002 | SWA | 90.1-2007
CE and BLET | Nash CC |  | 09-07972-03A | 2012-11-19 | CD | 2013-11-05 | 2015-04-03 | Offices/Classrooms/Gym/Training | NA | 79295 | 2 | CE and BLET | 90.1-2007 | 5941 | 74.9228 | 4122 | 51.9831 | 30.62% | 1819 | 0 |  |  |  |  | CE and BLET | 95436 | 1.2036 | 64835 | 0.81764 | 32.06% | 30601 |  |  |  |  | CE and BLET | 2356578 | NA | 29.7191 | 1527392 | NA | 19.2621 | 35.19% | 829186 |  |  |  |  | CE and BLET | 11310270 | 142.6353 |  | 861998 | None Noted |  | 52620 |  | SWA | 90.1-2007
Holshouser Residence Hall Renovation | UNCC | Tony Schallert | 12-09461-02A | 2014-03-17 | FD | 2014-02-06 | 2015-04-15 | Residence Hall | 400 | 99713 | 12 | Holshouser Residence Hall Renovation | 90.1-2007 | 12163 | 121.9801 | 9302 | 93.2877 | 23.52% | 2861 | 0 |  |  |  |  | Holshouser Residence Hall Renovation | 169440 | 1.6993 | 126115 | 1.2648 | 25.57% | 43325 |  |  |  |  | Holshouser Residence Hall Renovation | 3663471 | 9158.6775 | 36.7402 | 2570153 | 6425.3825 | 25.7755 | 29.84% | 1093318 |  |  |  |  | Holshouser Residence Hall Renovation | 15172636 | 152.1631 | 14796933 | 1251550 | 11880 |  | 95000 | 11.1387 | CN | 90.1-2007 | 375703
Rizzo Conference Center Phase III (Privately Funded) | UNC-CH | Chris Martin | 11-08953-01A | 2012-09-04 | CD | In construction (Privately Funded) | 2015-04-15 | Hotel/Classrooms/Conference | 66 | 97014 | 5 | Rizzo Conference Center Phase III (Privately Funded) | 90.1-2004 | 6933 | 71.4639 | 4473 | 46.1067 | 35.48% | 2460 | 0 |  |  |  |  | Rizzo Conference Center Phase III (Privately Funded) | 14092 | 0.14526 | 10313 | 0.1063 | 26.82% | 3779 |  |  |  |  | Rizzo Conference Center Phase III (Privately Funded) | 2116678 | 32070.8788 | 21.8183 | 1698607 | 25736.4697 | 17.5089 | 19.75% | 418071 |  |  |  |  | Rizzo Conference Center Phase III (Privately Funded) | 25040939 | 258.1168 |  | No Contract (Privately Funded) |  |  | No Contract (Privately Funded) |  |  | 90.1-2004
Belk Residence Hall Renovation | ASU | Jerry Marshall | 10-09113-02A | 2014-02-21 | FD-2 | 2014-05-05 | 2015-06-23 | Residence Hall | 176 | 32839 | 5 | Belk Residence Hall Renovation | 90.1-2007 | 3330 | 101.4038 | 2305 | 70.1909 | 30.78% | 1025 | 0 |  |  |  |  | Belk Residence Hall Renovation | 87029 | 2.6502 | 60703 | 1.8485 | 30.25% | 26326 |  |  |  |  | Belk Residence Hall Renovation | 1209992 | 6874.9545 | 36.8462 | 755467 | 4292.4261 | 23.0052 | 37.56% | 454525 |  |  |  |  | Belk Residence Hall Renovation | 7222300 | 219.9306 | 6512106 | 806400 | 50600 |  | 125000 | 33.6471 | CN | 90.1-2007
Phase XIII Residence Hall | UNCC | Tony Schallert | 12-09496-03A | 2013-10-11 | DD-2 | 2014-01-02 | 2015-06-25 | Residence Hall | 412 | 143986 | 6 | Phase XIII Residence Hall | 90.1-2007 | 7705 | 53.5121 | 5840 | 40.5595 | 24.21% | 1865 | 0 |  |  |  |  | Phase XIII Residence Hall | 102473 | 0.71169 | 56750 | 0.39414 | 44.62% | 45723 |  |  |  |  | Phase XIII Residence Hall | 4730466 | 11481.7136 | 32.8537 | 2731460 | 6629.7573 | 18.9703 | 42.26% | 1999006 |  |  |  |  | Phase XIII Residence Hall | 30113256 | 209.1402 | 26520850 | 2312090 | 13945 |  | 200000 | 83.2481 | Optima | 90.1-2007
Belk Gymnasium Renovation (Student Recreation Facility) | UNCC | Tony Schallert | 12-09471-03A | 2013-10-18 | DD | 2014-05-05 | 2015-07-06 | Gym, Pool, Offices | NA | 105000 | 3 | Belk Gymnasium Renovation (Student Recreation Facility) | 90.1-2010 | 5893 | 56.1238 | 5553 | 52.8857 | 5.77% | 340 | 0 |  |  |  |  | Belk Gymnasium Renovation (Student Recreation Facility) | 96234 | 0.91651 | 84246 | 0.80234 | 12.46% | 11988 |  |  |  |  | Belk Gymnasium Renovation (Student Recreation Facility) | 2939272 | NA | 27.9931 | 1888963 | NA | 17.9901 | 35.73% | 1050309 |  |  |  |  | Belk Gymnasium Renovation (Student Recreation Facility) | 14388687 | 137.0351 | 13744319 | 1224800 | 0 |  | 136650 | 65.15 | M&L | 90.1-2010
S & BS Building Renovation | UNCW |  | 07-09975-02A | 2014-07-02 | CD | 2014-05-30 | 2015-07-30 | Offices, classrooms, labs | NA | 43554 | 2 | S & BS Building Renovation | 90.1-2010 | 5934.9 | 136.2653 | 5079 | 116.6139 | 14.42% | 855.9 | [5 empty] | S & BS Building Renovation | 110349 | 2.5336 | 91957 | 2.1113 | 16.67% | 18392 |  |  |  |  | S & BS Building Renovation | 1075870 | NA | 24.702 | 760602 | NA | 17.4634 | 29.3% | 315268 |  |  |  |  | S & BS Building Renovation | 9820475 | 225.4781 | 5837018 | 859450 |  | 17250 | 98204.75 | 222.8638 | MCBH | 90.1-2010
Oak Residence Hall Renovation | UNCC | Tony Schallert | 12-09648-03A | 2014-01-06 | CD-2 | 2014-05-19 | 2015-08-01 | Residence Hall | 248 | 52844 | 4 | Oak Residence Hall Renovation | 90.1-2007 | 4104 | 77.6626 | 2776 | 52.532 | 32.36% | 1328 | 0 |  |  |  |  | Oak Residence Hall Renovation | 78156 | 1.479 | 52863 | 1.0004 | 32.36% | 25293 |  |  |  |  | Oak Residence Hall Renovation | 3786332 | 15267.4677 | 71.6511 | 2951199 | 11899.996 | 55.8474 | 22.06% | 835133 |  |  |  |  | Oak Residence Hall Renovation | 7187260 | 136.009 | 5929373 | 591176 | 0 |  | 77500 | 52.7967 | Peterson | 90.1-2007
Student Recreation Center | UNCG | Douglas Cato | 09-07928-02A | 2014-03-17 | CD | 2014-03-06 | 2016-07-14 | Gym/Pool | NA | 213000 | 3 | Student Recreation Center | 90.1-2007 | 20211 | 94.8873 | 15288 | 71.7746 | 24.36% | 4923 | 0 |  |  |  |  | Student Recreation Center | 275822 | 1.2949 | 188166 | 0.88341 | 31.78% | 87656 |  |  |  |  | Student Recreation Center | 2060500 | NA | 9.6737 | 1524900 | NA | 7.1592 | 25.99% | 535600 |  |  |  |  | Student Recreation Center (cost includes CUP?) | 69872746 | 328.0411 | 63588816 | 6427000 | 67200 |  | 344800 | 76.3887 | M&L | 90.1-2007
Winkler Residence Hall Renovation Demolished 06/01/14 | ASU | Jerry Marshall | 10-08894-03A | 2012-09-14 | CD | Demolished 06/01/14 | Demolished 06/01/14 | Residence Hall | 192 | 78450 | 12 | Winkler Residence Hall Renovation Demolished 06/01/14 | 90.1-2004 | 6070 | 77.3741 | 3601 | 45.9018 | 40.68% | 2469 | 0 |  |  |  |  | Winkler Residence Hall Renovation Demolished 06/01/14 | 143502 | 1.8292 | 87933 | 1.1209 | 38.72% | 55569 |  |  |  |  | Winkler Residence Hall Renovation Demolished 06/01/14 | 2528379 | 13168.6406 | 32.2292 | 1493037 | 7776.2344 | 19.0317 | 40.95% | 1035342 |  |  |  |  | Winkler Residence Hall Renovation Demolished 06/01/14 | 11873469 | 151.3508 |  | 1313285 | 103000 |  | 92600 | 217.1907 |  | 90.1-2004
Bio-tech & Med Sim Center NOT SB 668 | Edgecombe CC |  | 05-06644-02A | 2014-04-09 | DD | Design Build / NOT SB 668 | Design Build / NOT SB 668 | Office/Classroom/Labs | NA | 44978 | 3 | Bio-tech & Med Sim Center NOT SB 668 | 90.1-2007 | 6871 | 152.7636 | 4929 | 109.5869 | 28.26% | 1942 | 0 |  |  |  |  | Bio-tech & Med Sim Center NOT SB 668 | 134054 | 2.9804 | 98221 | 2.1838 | 26.73% | 35833 |  |  |  |  | Bio-tech & Med Sim Center NOT SB 668 |  | NA | 0 |  | NA | 0 |  | 0 |  |  |  |  | Bio-tech & Med Sim Center NOT SB 668 | 4825393 | 107.2834 | 4180000 | 932460 | 308832 |  | 28700 | 27.4307 |  | 90.1-2007
Burson Building Renovation | UNCC | Tony Schallert | 13-10798-01A | 2014-09-12 | AP | No Contract | 2016-10-10 | Chemistry/Physics Teaching Labs classrooms offices | NA | 99552 | 2 | Burson Building Renovation | [12 empty] | Burson Building Renovation | [10 empty] | Burson Building Renovation | [12 empty] | Burson Building Renovation | 11500000 | 115.5175 |  |  |  |  | 31000 |  | M&L
New Student Center | NCA&T |  | 03-08608-02A | 2014-05-09 | CD | 2014-02-20 | 2017-08-01 | Offices/Theater/Conference/Food Service/Book Store | NA | 182275 | 4 | New Student Center | 90.1-2007 | 31691 | 173.8637 | 23425 | 128.5146 | 26.08% | 8266 | 0 |  |  |  |  | New Student Center | 529117 | 2.9029 | 366504 | 2.0107 | 30.73% | 162613 |  |  |  |  | New Student Center | 5763776 | NA | 31.6213 | 4434106 | NA | 24.3265 | 23.07% | 1329670 |  |  |  |  | New Student Center | 71022605 | 389.6453 | 64958142 | 7250000 | 166000 |  | 594000 | 41.9675 | RMF | 90.1-2007
Advanced + Emerging Technologies Center NOT SB 668 | CFCC | Ken Pearce | 11-08585-02A | 2013-07-19 | DD | No Contract | No Contract | Classrooms, labs, offices | NA | 94236 | 2 | Advanced + Emerging Technologies Center NOT SB 668 | 90.1-2007 | 6944 | 73.6873 | 6610 | 70.143 | 4.81% | 334 | 0 |  |  |  |  | Advanced + Emerging Technologies Center NOT SB 668 | 249013 | 2.6424 | 222050 | 2.3563 | 10.83% | 26963 |  |  |  |  | Advanced + Emerging Technologies Center NOT SB 668 | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. |  |  |  |  | Advanced + Emerging Technologies Center NOT SB 668 | 21563001 | 228.8191 | 3432421 | 2079762 | 0 |  | 0 |  |  | 90.1-2007
Heavy Equipment + Transport Technology Center NOT SB 668 | CFCC | Ken Pearce | 11-08585-02A | 2013-07-19 | DD | No Contract | No Contract | Equipment repair, offices, classrooms | NA | 32221 | 2 | Heavy Equipment + Transport Technology Center NOT SB 668 | 90.1-2007 | [6 empty] | 0 |  |  |  |  | Heavy Equipment + Transport Technology Center NOT SB 668 | 28938 | 0.89811 | 22854 | 0.70929 | 21.02% | 6084 |  |  |  |  | Heavy Equipment + Transport Technology Center NOT SB 668 | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. | Not used. |  |  |  |  | Heavy Equipment + Transport Technology Center NOT SB 668 | 6833178 | 212.0722 | 2041899 | Included w/A+ETC | 0 |  | NOT SB 668 |  |  | 90.1-2007
Science and Office Bldg | WSSU | Dick Kabis | 07-07236-01A | 2013-04-01 | CD | Approved to bid 11/04/2013 | No Contract | Classroom/Lab/Offices | NA | 123275 | 6 | Science and Office Bldg | 90.1-2004 | 23068 | 187.1263 | 15903 | 129.0043 | 31.06% | 7165 | 0 |  |  |  |  | Science and Office Bldg | 425425 | 3.451 | 296267 | 2.4033 | 30.36% | 129158 |  |  |  |  | Science and Office Bldg | 1377837 | NA | 11.1769 | 878485 | NA | 7.1262 | 36.24% | 499352 |  |  |  |  | Science and Office Bldg | 42881459 | 347.852 | 39331912 | 4603210 | 138000 |  | 455967 | 32.081 | AEI | 90.1-2004
Main Campus Student Union | ECU | Les Hewlett hewlettl14@ecu.edu | 11-09263-02A | 2014-05-16 | SD | No Contract | No Contract | Offices/Theater/Conference/ Food Service/ Book Store | NA | 219070 | 4 | Main Campus Student Union | 90.1-2007 | 13361 | 60.9896 | 9943 | 45.3873 | 25.58% | 3418 | [5 empty] | Main Campus Student Union | 249185 | 1.1375 | 204787 | 0.9348 | 17.82% | 44398 |  |  |  |  | Main Campus Student Union | [12 empty] | Main Campus Student Union | 73076027 | 333.5739 | 70925238 | [5 empty] | AEI | 90.1-2007
Mary Ellen Jones Renovation | UNC |  | 11-09861-02A | 2014-06-06 | DD | No Contract | No Contract | Labs/Offices | NA | 207610 | 11 | Mary Ellen Jones Renovation | 90.1-2007 | 26345.5 | 126.899 | 22268.5 | 107.2612 | 15.48% | 4077 | [5 empty] | Mary Ellen Jones Renovation | 1001430 | 4.8236 | 788087 | 3.796 | 21.3% | 213343 |  |  |  |  | Mary Ellen Jones Renovation | 663675 | NA | 3.1967 | 445591 | NA | 2.1463 | 32.86% | 218084 |  |  |  |  | Mary Ellen Jones Renovation | 52755217 | 254.1073 | 47940800 | 5184529 |  | 10370 | 730000 | 26.0369 | Newcomb & Boyd | 90.1-2007
Collaborative Science Building | UNC |  | 11-09030-02A | 2013-11-01 | DD | No Contract | No Contract | Labs/Offices | NA | 274810 | 9 | Collaborative Science Building | 90.1-2007 | 15342 | 55.8277 | 11509 | 41.8798 | 24.98% | 3833 | 0 |  |  |  |  | Collaborative Science Building | 293091 | 1.0665 | 229379 | 0.83468 | 21.74% | 63712 |  |  |  |  | Collaborative Science Building | 1871354 | NA | 6.8096 | 1339798 | NA | 4.8754 | 28.4% | 531556 |  |  |  |  | Collaborative Science Building | 72817169 | 264.9728 | 78341076 | 7995000 | 223000 | 65350 | 500000 | -74.3276 | Atelier Ten | 90.1-2007
Holding Hall Renovation | Wake TCC |  | 06-06753-02A | 2013-11-18 | CD | No Contract | No Contract | Offices/Classrooms | NA | 47729 | 1 | Holding Hall Renovation | 90.1-2007 | 2614 | 54.7675 | 1818 | 38.0901 | 30.45% | 796 | [5 empty] | Holding Hall Renovation | 52390 | 1.0977 | 33542 | 0.70276 | 35.98% | 18848 |  |  |  |  | Holding Hall Renovation | 1075022 | NA | 22.5235 | 817762 | NA | 17.1334 | 23.93% | 257260 |  |  |  |  | Holding Hall Renovation | 3636045 | 76.181 | 3327846 | 449750 | 41200 |  |  | 18.5377 | Dewberry | 90.1-2007
Reynolds Coliseum Renovation | NCSU | Shanna Harwell <smharwel@ncsu.edu> | 12-09912-01B | 2014-05-27 | DD | No Contract | No Contract | Basketball Arena, locker rooms, offices | NA | 165584 | 3 | Reynolds Coliseum Renovation | 90.1-2007 | 29645 | 179.033 | 21778 | 131.5224 | 26.54% | 7867 | [5 empty] | Reynolds Coliseum Renovation | 531737 | 3.2113 | 421010 | 2.5426 | 20.82% | 110727 |  |  |  |  | Reynolds Coliseum Renovation | 395678 | NA | 2.3896 | 296302 | NA | 1.7894 | 25.12% | 99376 |  |  |  |  | Reynolds Coliseum Renovation | 23537423 | 142.1479 | 23537423 | 3170473 | 35000 | 60000 | 58725 | 1.3883 | BNK | 90.1-2007
Sanford Residence Hall Renovation | UNCC | Tony Schallert | 12-09978-03A | 2014-07-09 | DD | No Contract | No Contract | Residence Hall | 440 | 99436 | 12 | Sanford Residence Hall Renovation | 90.1-2010 | 5384 | 54.1454 | 4674 | 47.0051 | 13.19% | 710 | [5 empty] | Sanford Residence Hall Renovation | 58913 | 0.59247 | 50839 | 0.51127 | 13.7% | 8074 |  |  |  |  | Sanford Residence Hall Renovation | 4280271 | 9727.8886 | 43.0455 | 2887348 | 6562.1545 | 29.0373 | 32.54% | 1392923 |  |  |  |  | Sanford Residence Hall Renovation | 15688400 | 157.7738 | 15615290 | 1287470 |  | 4100 | 100000 | 21.9482 | M&L | 90.1-2010 | 73110
Student Center Health Sciences Campus | ECU | Les Hewlett hewlettl14@ecu.edu | 11-10217-02A | 2014-05-30 | DD | No Contract | No Contract | Offices/Gym/ Food Service/ Book Store | NA | 75843 | 4 | Student Center Health Sciences Campus | 90.1-2004 | 6819 | 89.9094 | 5027 | 66.2817 | 26.28% | 1792 | [5 empty] | Student Center Health Sciences Campus | 96722 | 1.2753 | 73792 | 0.97296 | 23.71% | 22930 |  |  |  |  | Student Center Health Sciences Campus | 1871360 | NA | 24.6741 | 1215180 | NA | 16.0223 | 35.06% | 656180 |  |  |  |  | Student Center Health Sciences Campus | 25507078.25 | 336.3142 | 21220000 | 2903738 | 154488 |  | 300000 | 206.7844 | RDK | 90.1-2004
Student Housing Phase III | UNC |  | 12-09765-02A | 2014-08-18 | SD | No Contract | No Contract | Residence Hall and Offices | 275 | 109249 | 7 | Student Housing Phase III | 90.1-2010 | 9552 | 87.4333 | 8694 | 79.5797 | 8.982% | 858 | [5 empty] | Student Housing Phase III | 229389 | 2.0997 | 203080 | 1.8589 | 11.47% | 26309 |  |  |  |  | Student Housing Phase III | 926079 | 3367.56 | 8.4768 | 589878 | 2145.0109 | 5.3994 | 36.3% | 336201 |  |  |  |  | Student Housing Phase III | 24351716 | 222.901 | 24137876 | 1961668 | 53300 | 31970 | 250000 | 20.8716 | CN | 90.1-2010
Western Crime Lab | NCDoJ |  | 12-09454-02A | 2014-07-09 | CD | No Contract | No Contract | Labs/Offices | NA | 35357 | 2 | Western Crime Lab | 90.1-2007 | 7819 | 221.1443 | 5719 | 161.7501 | 26.86% | 2100 | 0 |  |  |  |  | Western Crime Lab | 205920 | 5.824 | 148867 | 4.2104 | 27.71% | 57053 |  |  |  |  | Western Crime Lab | 90384 | NA | 2.5563 | 69048 | NA | 1.9529 | 23.61% | 21336 |  |  |  |  | Western Crime Lab | 14101085 | 398.8202 | 13630000 | 1440000 |  |  | 120000 | 10.3603 | M&C | 90.1-2007
Division 2 Equipment Shop | DOT |  | 12-09859-03A | 2014-04-04 | SD | No Contract | No Contract | Repair garage/storage/offices | NA | 36700 | 1 | Division 2 Equipment Shop |  | 1102.38 | 30.0376 | [9 empty] | Division 2 Equipment Shop | 63506 | 1.7304 | 44454.2 | 1.2113 | 30% | 19051.8 |  |  |  |  | Division 2 Equipment Shop | [12 empty] | Division 2 Equipment Shop | 6528314 | 177.8832 | 6201898.3 | 539733 | 12290 | 8000 | 37090 | 20.1449 | Dibble and Pledger
Phase XIV Residence Hall | UNCC | Tony Schallert | 12-10117-03A | 2014-04-08 | DD | No Contract | No Contract | Residence Hall | 419 | 157219 | 6 | Phase XIV Residence Hall | 90.1-2007 | 8498 | 54.052 | 7032 | 44.7274 | 17.25% | 1466 | [5 empty] | Phase XIV Residence Hall | 149191 | 0.94894 | 140621 | 0.89443 | 5.744% | 8570 |  |  |  |  | Phase XIV Residence Hall | 4009898 | 9570.1623 | 25.5052 | 2294948 | 5477.2029 | 14.5971 | 42.77% | 1714950 |  |  |  |  | Phase XIV Residence Hall | 37955586 | 241.4186 | 34937000 | 3018220 |  | 27500 | 164340 | 374.6121 | Optima | 90.1-2004
Elm Residence Hall Renovation | UNCC | Tony Schallert | 12-09940-03A | 2014-06-23 | DD | No Contract | No Contract | Residence Hall | 95 | 29845 | 3 | Elm Residence Hall Renovation | 90.1-2007 | 2122 | 71.1007 | 1669 | 55.9223 | 21.35% | 453 | [5 empty] | Elm Residence Hall Renovation | 34775 | 1.1652 | 26751 | 0.89633 | 23.07% | 8024 |  |  |  |  | Elm Residence Hall Renovation | 1069151 | 11254.2211 | 35.8235 | 696432 | 7330.8632 | 23.335 | 34.86% | 372719 |  |  |  |  | Elm Residence Hall Renovation | 5366082.96 | 179.7984 | 5158196.28 | 448389 |  | 3312 | 23400 | 29.2371 | Peterson | 90.1-2007
Maple Residence Hall Renovation | UNCC | Tony Schallert | 12-09940-03A | 2014-06-23 | DD | No Contract | No Contract | Residence Hall | 64 | 23270 | 3 | Maple Residence Hall Renovation | 90.1-2007 | 1704 | 73.2273 | 1196 | 51.3966 | 29.81% | 508 | [5 empty] | Maple Residence Hall Renovation | 28673 | 1.2322 | 19427 | 0.83485 | 32.25% | 9246 |  |  |  |  | Maple Residence Hall Renovation | 710168 | 11096.375 | 30.5186 | 462765 | 7230.7031 | 19.8868 | 34.84% | 247403 |  |  |  |  | Maple Residence Hall Renovation | 4173620.08 | 179.3563 | 4011930.44 | 348747 |  | 2576 | 18200 | 19.7345 | Peterson | 90.1-2007
Pine Residence Hall Renovation | UNCC | Tony Schallert | 12-09940-03A | 2014-06-23 | DD | No Contract | No Contract | Residence Hall | 95 | 29799 | 3 | Pine Residence Hall Renovation | 90.1-2007 | 2122 | 71.2104 | 1669 | 56.0086 | 21.35% | 453 | [5 empty] | Pine Residence Hall Renovation | 34775 | 1.167 | 26751 | 0.89771 | 23.07% | 8024 |  |  |  |  | Pine Residence Hall Renovation | 1069151 | 11254.2211 | 35.8788 | 696432 | 7330.8632 | 23.371 | 34.86% | 372719 |  |  |  |  | Pine Residence Hall Renovation | 5366082.96 | 180.0759 | 5158196.28 | 448389 |  | 3312 | 23400 | 29.2371 | Peterson | 90.1-2007
Allied Health & Workforce (Courtesy review only of DD phase) | ABTCC |  | 12-09487-01A | 2012-11-13 | DD | No Contract | No Contract | Office/Classroom/Lab/Assembly | NA | 185810 | 6 | Allied Health & Workforce | 90.1-2004 | 10582 | 56.9506 | 3675 | 19.7783 | 65.27% | 6907 | 0 |  |  |  |  | Allied Health & Workforce | 267259 | 1.4383 | 93214 | 0.50166 | 65.12% | 174045 |  |  |  |  | Allied Health & Workforce | 115375 | NA | 0.62093 | 50944 | NA | 0.27417 | 55.84% | 64431 |  |  |  |  | Allied Health & Workforce | 45400738 | 244.3396 | 42736000 | no contract |  |  |  | 15.3106 |  | 90.1-2004
Building 600 NOT SB 668 | RCCC |  | 11-08937-02A | 2013-01-25 | DD | No Contract | No Contract | Classroom, offices | NA | 69250 | 2 | Building 600 NOT SB 668 | 90.1-2004 | 4413 | 63.7256 | 2774 | 40.0578 | 37.14% | 1639 | 0 |  |  |  |  | Building 600 NOT SB 668 | 82649 | 1.1935 | 58907 | 0.85064 | 28.73% | 23742 |  |  |  |  | Building 600 NOT SB 668 | 60744 | NA | 0.87717 | 45643 | NA | 0.6591 | 24.86% | 15101 |  |  |  |  | Building 600 NOT SB 668 | 10191099 | 147.1639 | 8586550 | Included w/ Bldgs 300 and 500. | 0 |  | 0 | 67.5827 |  | 90.1-2004
New Residence Hall - Freshman Living/Learning | WSSU | Dick Kabis | 13-10372-03A | 2014-07-31 | DD | No Contract | No Contract | Residence Hall | 290 | 71021 | 6 | New Residence Hall - Freshman Living/Learning | 90.1-2010 | 3150 | 44.3531 | 2905 | 40.9034 | 7.778% | 245 | [5 empty] | New Residence Hall - Freshman Living/Learning | 73009 | 1.028 | 68936 | 0.97064 | 5.579% | 4073 |  |  |  |  | New Residence Hall - Freshman Living/Learning | 2516360 | 8677.1034 | 35.4312 | 1717995 | 5924.1207 | 24.19 | 31.73% | 798365 |  |  |  |  | New Residence Hall - Freshman Living/Learning | 16840890 | 237.1255 | 14317971 | 1735188 | 75000 | 11000 | 176132 | 683.7837 | RMF | 90.1-2010
Bus & Industry Training Bldg | Catawba Valley CC |  | 07-07389-01A | 2012-08-28 | AP | No Contract | No Contract | Classrooms/Ofices/Lab&Shop/conf training/etc | NA | 56300 | 1 | Bus & Industry Training Bldg | 90.1-2004 | 5351 | 95.0444 | 3925 | 69.7158 | 26.65% | 1426 | 0 |  |  |  |  | Bus & Industry Training Bldg | 77860 | 1.3829 | 56493 | 1.0034 | 27.44% | 21367 |  |  |  |  | Bus & Industry Training Bldg | 35250 | NA | 0.62611 | 23345 | NA | 0.41465 | 33.77% | 11905 |  |  |  |  | Bus & Industry Training Bldg | 14858000 | 263.9076 |  | 1282000 | 45000 |  | 45670 |  |  | 90.1-2004
Highway Patrol Training Facility | DOA |  | 10-08389-02A | 2012-06-28 | CD | Project on Hold | Project on Hold | Office/Classroom/Training | NA | 34386 | 2 | Highway Patrol Training Facility | 90.1-2004 | 2484 | 72.2387 | 1436 | 41.7612 | 42.19% | 1048 | 0 |  |  |  |  | Highway Patrol Training Facility | 59882 | 1.7415 | 41042 | 1.1936 | 31.46% | 18840 |  |  |  |  | Highway Patrol Training Facility | 667359 | NA | 19.4079 | 310095 | NA | 9.0181 | 53.53% | 357264 |  |  |  |  | Highway Patrol Training Facility | 6245727 | 181.6358 | 5604454 | is for multiple buildings | is for multiple buildings |  | 84000 |  |  | 90.1-2004
Basic Skills Building | Robeson CC |  | 07-07572-01A | 2010-12-22 | AP/SD | Project on Hold | Project on Hold | Office/Classroom | NA | 34271 | 2 | Basic Skills Building | 90.1-2004 | 2178 | 63.5523 | 1492 | 43.5354 | 31.5% | 686 | 0 |  |  |  |  | Basic Skills Building | 51338 | 1.498 | 36026 | 1.0512 | 29.83% | 15312 |  |  |  |  | Basic Skills Building |  | NA | 0 |  | NA | 0 |  | 0 |  |  |  |  | Basic Skills Building | [9 empty] | 90.1-2004
School of Aviation | ECSU | Elizabeth Linney | 07-07166-02A | 2011-01-24 | CD | Project on Hold | Project on Hold | Office/Classroom/Hangar | NA | 44000 | 1 | School of Aviation | 90.1-2004 | 1913 | 43.4773 | 1115 | 25.3409 | 41.71% | 798 | 0 |  |  |  |  | School of Aviation | 118819 | 2.7004 | 67443 | 1.5328 | 43.24% | 51376 |  |  |  |  | School of Aviation | 179563 | NA | 4.081 | 121788 | NA | 2.7679 | 32.18% | 57775 |  |  |  |  | School of Aviation | [9 empty] | 90.1-2004
Multipurpose Bldg | South Piedmont CC |  | 07-07352-03A | 2010-07-23 | CD | Approved to bid 05/15/2011 | Project on Hold | Office/Classroom/Labs | NA | 75000 | 3 | Multipurpose Bldg | 90.1-2004 | 5827 | 77.6933 | 3550 | 47.3333 | 39.08% | 2277 | 0 |  |  |  |  | Multipurpose Bldg | 135642 | 1.8086 | 87360 | 1.1648 | 35.6% | 48282 |  |  |  |  | Multipurpose Bldg | 587500 | NA | 7.8333 | 398125 | NA | 5.3083 | 32.23% | 189375 |  |  |  |  | Multipurpose Bldg | [9 empty] | 90.1-2004
Locomotive and Railcar Maint. Facility | DOT |  | 10-08634-03A | 2011-10-20 | SD | Project on Hold | Project on Hold | Offices & Railcar | NA | 68400 | 1 | Locomotive and Railcar Maint. Facility | 90.1-2004 | 23291 | 340.5117 | 8015 | 117.1784 | 65.59% | 15276 | 0 |  |  |  |  | Locomotive and Railcar Maint. Facility | 210152 | 3.0724 | 107570 | 1.5727 | 48.81% | 102582 |  |  |  |  | Locomotive and Railcar Maint. Facility | [12 empty] | Locomotive and Railcar Maint. Facility | [9 empty] | 90.1-2004
Discovery Center Project - Reynolds East | NCSSM |  | 07-07313-04A | 2010-05-10 | CD | Final Not Approved 05/23/2011 | Project on Hold | Residence Hall / Classroom | 31 | 26000 | 4 | Discovery Center Project - Reynolds East | 90.1-2004 | 1846 | 71 | 1121 | 43.1154 | 39.27% | 725 | 0 |  |  |  |  | Discovery Center Project - Reynolds East | 30466 | 1.1718 | 19282 | 0.74162 | 36.71% | 11184 |  |  |  |  | Discovery Center Project - Reynolds East | 475929 | 15352.5484 | 18.305 | 337075 | 10873.3871 | 12.9644 | 29.18% | 138854 |  |  |  |  | Discovery Center Project - Reynolds East | [9 empty] | 90.1-2004
Note on BA4: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on AL5: Leonard Thagard: limited kitchen use and limited bathroom use. Number is extremely low.
Note on AO5: Leonard Thagard: limited kitchen and bathroom use. Number is low.
Note on BA5: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on P6: Leonard Thagard: highest baseline EUI to date for all state buildings
Note on R6: Leonard Thagard: highest proposed EUI for state buildings to date
Note on BA6: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on BA7: Leonard Thagard: Calculated from original amount construction contract less increase noted in LCCA for envelope, plumb, chillers and lights.
Note on V8: Leonard Thagard: does not include steam consumption
Note on BA8: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on BC8: Leonard Thagard: SB 668 at $99800 and LEED at $73700
Note on BA10: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on K11: Leonard Thagard: size is for addition only
Note on O11: Leonard Thagard: energy use is for addition only
Note on V11: Leonard Thagard: metered energy use is for addition and existing building
Note on W11: Leonard Thagard: Metered EUI is for entire building, existing plus addition
Note on AH11: Leonard Thagard: $/Yr/SF is for the entire building at 66,128 gross square feet.
Note on AV11: Leonard Thagard: Used total building square footage at 66,128GSF.
Note on BA11: Leonard Thagard: Calculated from construction contract less alternates in designer's estimate.
Note on AY14: Leonard Thagard: Includes RUP?
Note on BA14: Leonard Thagard: Does not include RUP?
Note on BC14: Leonard Thagard: LEED fees of 180,000 plus design amend #1 for SB 668 for 41,084
Note on J17: Leonard Thagard: One model performed and applied to seven bldgs
Note on K17: Leonard Thagard: One model performed and applied to seven bldgs.
Note on O17: Leonard Thagard: One model performed and applied to seven bldgs
Note on AY17: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BB17: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BC17: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BE17: Leonard Thagard: Cx fee divided by 7 buildings.
Note on J18: Leonard Thagard: One model performed and applied to seven bldgs
Note on K18: Leonard Thagard: One model performed and applied to seven bldgs.
Note on O18: Leonard Thagard: One model performed and applied to seven bldgs
Note on AY18: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BB18: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BC18: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BE18: Leonard Thagard: Cx fee divided by 7 buildings.
Note on J19: Leonard Thagard: One model performed and applied to seven bldgs
Note on K19: Leonard Thagard: One model performed and applied to seven bldgs.
Note on O19: Leonard Thagard: One model performed and applied to seven bldgs
Note on AY19: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BB19: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BC19: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BE19: Leonard Thagard: Cx fee divided by 7 buildings.
Note on J20: Leonard Thagard: One model performed and applied to seven bldgs
Note on K20: Leonard Thagard: One model performed and applied to seven bldgs.
Note on O20: Leonard Thagard: One model performed and applied to seven bldgs
Note on AY20: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BB20: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BC20: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BE20: Leonard Thagard: Cx fee divided by 7 buildings.
Note on J21: Leonard Thagard: One model performed and applied to seven bldgs
Note on K21: Leonard Thagard: One model performed and applied to seven bldgs.
Note on O21: Leonard Thagard: One model performed and applied to seven bldgs
Note on AY21: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BB21: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BC21: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BE21: Leonard Thagard: Cx fee divided by 7 buildings.
Note on J22: Leonard Thagard: One model performed and applied to seven bldgs
Note on K22: Leonard Thagard: One model performed and applied to seven bldgs.
Note on O22: Leonard Thagard: One model performed and applied to seven bldgs
Note on AY22: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BB22: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BC22: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BE22: Leonard Thagard: Cx fee divided by 7 buildings.
Note on J23: Leonard Thagard: One model performed and applied to seven bldgs
Note on K23: Leonard Thagard: One model performed and applied to seven bldgs.
Note on O23: Leonard Thagard: One model performed and applied to seven bldgs
Note on AY23: Leonard Thagard: Original Amount Construction Contract divided by 7 buildings.
Note on BB23: Leonard Thagard: Original Total Design Fee divided by 7 buildings.
Note on BC23: Leonard Thagard: LEED or SB 668 fee divided by 7 buildings.
Note on BE23: Leonard Thagard: Cx fee divided by 7 buildings.
Note on BC25: Leonard Thagard: LEED services added as design amendment. Add to OTDF.
Note on V26: Leonard Thagard: energy data provided by Optima Engineering
Note on BB28: Leonard Thagard: Combined design fee for original building design and revised building design.
Note on BC29: Leonard Thagard: SB 668 at 17520 and LEED at 139300
Note on AY33: Leonard Thagard: CMR bid packages, NCSU utility assessment, parking deck assessment, etc. make bid amount difficult to accurately calculate.
Note on AY34: Leonard Thagard: Amount is for entire football complex.
Note on AZ34: Leonard Thagard: Error in calculation due to entire football complex in one bid package. Building was not broken out.
Note on BB34: Leonard Thagard: Fee includes design for complete football stadium complex.
Note on W37: Leonard Thagard: EUI for addition plus existing building.
Note on AH37: Leonard Thagard: $/GSF is for addition plus existing building.
Note on AV37: Leonard Thagard: Gallons/GSF is for addition plus the existing building.
Note on AY37: Leonard Thagard: Best guess from multiple bid packages. Will revisit later.
Note on BB37: Leonard Thagard: 27% of full design fee
Note on AY38: Leonard Thagard: 73 percent of bid package total for Plemmons and Summitt
Note on BB38: Leonard Thagard: 73 percent of full design fee.
Note on BA39: Leonard Thagard: Note in LCCA report: "*Initial Cost estimated to be 85% of Construction Budget."
Note on H40: Leonard Thagard: BO
Note on AY45: Leonard Thagard: Early site package plus building package.
Note on BA45: Leonard Thagard: Clark Nexsen analysis indicated baseline building cost more to build than the proposed building. Analysis not used here.
Note on V46: Leonard Thagard: Does not include natural gas consumption.
Note on AT46: Leonard Thagard: Water use is not realistic.
Note on AY47: Leonard Thagard: Early site plus site and building bid packages.
Note on V48: Leonard Thagard: Meter data is incomplete. No steam data and no domestic hot water data.
Note on V49: Leonard Thagard: Meter does not include natural gas for cooking appliances.
Note on H53: Leonard Thagard: Best guess.
Note on AY53: Leonard Thagard: Designer's LCCA estimate.
Note on BA53: Leonard Thagard: Designer's LCCA estimate.
Note on H54: Leonard Thagard: BO per Jerry Rogers' handwritten notes in file.
Note on BA54: Leonard Thagard: LCCA cost estimate for proposed building was $46,642,869 while baseline was $46,128,762 for a difference of 514,107 which was deducted from the bid amount to arrive at the baseline building estimate.
Note on BC54: Leonard Thagard: LEED certification 110000 and article 15-1 fee 229250
Note on AY60: Leonard Thagard: Early site plus building package.
Note on BC64: Leonard Thagard: Green Globes.
Note on AY66: Leonard Thagard: CMR bid packages and CO's through CO#10.
Note on BA66: Leonard Thagard: CD estimates for baseline and proposed buildings exceed CMR bids through CO #10. Baseline estimate is CMR contract amount through CO #10 less designer's delta between baseline and proposed buildings.
Note on H71: Leonard Thagard: Bad soil discovered. Project delayed. Completion day not given. Recovery schedule completion date noted. Project is behind schedule. There was no recovery schedule or standard schedule for review.
Note on H72: Leonard Thagard: The completion date is September 2014 according to interscope.
Note on AR74: Leonard Thagard: includes kitchen load and cooling tower make up at 3,600,000 gall/yr.
Note on AY75: Leonard Thagard: Captures most but not all bid packages.
Note on BB75: Leonard Thagard: includes swing space, promotion support, bridge over RR tracks, etc.
Note on K76: Leonard Thagard: Listed now as two buildings East at 102,127 GSF and West at 105,950 GSF.
Note on G79: Leonard Thagard: Private funding. No state contract.
Note on H79: Leonard Thagard: Interscope indicates 45% complete as of 7/25/14. 04/15/15 completion is LWT's best guess.
Note on S81: Leonard Thagard: 27% improvement without plug and process loads.
Note on BC81: Leonard Thagard: Green Globes
Note on K82: Leonard Thagard: 131,341 includes pool deck and pool lobby in GSF. M&L estimate at 105,000 GSF.
Note on O82: Leonard Thagard: Includes plug and process loads. Pool equipment and HVAC are considered process loads.
Note on S82: Leonard Thagard: 6% less energy than A90.1-2010.
Note on BF82: Leonard Thagard: Not correct since base is A90.1-2010 instead of A90.1-2004. Also window and roof replacement not analyzed based on LCCA.
Note on K83: Leonard Thagard: GSF does not include tempered un-occupied attic space of ~22,000 SF.
Note on AY83: Leonard Thagard: Designer's proposed building estimate is $5,957,771. Early demo is not included. Contract may include CUP and distribution piping. Ear
Note on BA83: Leonard Thagard: does not include early demo, CEP, CEP distribution, etc.
Note on BE83: Leonard Thagard: LTs guess
Note on AM84: Leonard Thagard: Includes cooling tower make up and large laundry load.
Note on K85: Leonard Thagard: GSF includes alternates for additional space and per email from Rebecca dated 12.19.13.
Note on O85: Leonard Thagard: Includes process loads.
Note on Q85: Leonard Thagard: Inlcudes process loads.
Note on AY87: Leonard Thagard: SB 668 bldg estimate from PDC. BCC DB GMP is $9,751,745
Note on BA87: Leonard Thagard: Proposed bldg estimate from PDC. BCC DB GMP is $9,751,745
Note on BC87: Leonard Thagard: PDC estimate from HB 628 study.
Note on BE87: Leonard Thagard: PDC estimate for Cx.
Note on O89: Leonard Thagard: Includes process load
Note on Q89: Leonard Thagard: Includes process load.
Note on S89: Leonard Thagard: Savings are 46% with process load removed.
Note on AA89: Leonard Thagard: Includes process load.
Note on AC89: Leonard Thagard: Includes process load.
Note on AL89: Leonard Thagard: Includes cooling tower consumption.
Note on AO89: Leonard Thagard: Includes cooling tower consumption that is reduced due to smaller cooling load.
Note on AY89: Leonard Thagard: Cost includes demo, temp space, early site. Soup to nuts project cost.
Note on BA89: Leonard Thagard: Baseline whole building estimate from LCCA.
Note on BB89: Leonard Thagard: Includes fee for swing space and others.
Note on K90: Leonard Thagard: Base bid GSF. Alt Bid adds 4019 GSF.
Note on O90: Leonard Thagard: No updates for the DD submission.
Note on Q90: Leonard Thagard: No updates for the DD submission.
Note on O91: Leonard Thagard: No data provided with SD or DD submission.
Note on Q91: Leonard Thagard: No data provided with SD or DD submission.
Note on BB92: Leonard Thagard: complicated fee structure due to multiple increases in scope and square footage of project.
Note on BC92: Leonard Thagard: complex due to multiple increases in scope and square footage
Note on AY93: Leonard Thagard: Includes all site costs of $10,183,960.
Note on K94: Leonard Thagard: 158,450 is modeled according to summary sheet. 207,610 is gross square footage according to building code summary..
Note on O94: Leonard Thagard: Plug and process has not been included.
Note on Q94: Leonard Thagard: Plug and process has not been included.
Note on AB94: Leonard Thagard: Highest $/GSF to date.
Note on AD94: Leonard Thagard: Highest $/GSF to date.
Note on BE94: Leonard Thagard: $730,000 Cx reserve. Current Cx contract is $36,940.
Note on BE95: Leonard Thagard: Cx reserve. Design only Cx is for $44,680.
Note on L97: Leonard Thagard: base=57,963 1st=70,579 mez=37,042 Need to verify GSF.
Note on O98: Leonard Thagard: Includes plug and process
Note on AY100: Leonard Thagard: from page 51 of the SD project manual as Total Construction Costs.
Note on BA100: Leonard Thagard: from page 90 of the energy model lcca report.
Note on BB100: Leonard Thagard: contract not signed as of 09.02.14
Note on BC100: Leonard Thagard: from design contract: $43,200 for model and $10,100 for LEED
Note on BE100: Leonard Thagard: Cx reserve of $250,000
Note on BE101: Leonard Thagard: Current contract is for $22,000. $120,000 is commissioning reserve.
Note on AC102: Leonard Thagard: assume 30% savings over baseline
Note on AD102: Leonard Thagard: Highest $/GSF to date.
Note on BA102: Leonard Thagard: assume 95% of proposed building construction estimate
Note on S103: Leonard Thagard: 25% improvement w/o plug load
Note on Z103: Leonard Thagard: energy dollars include plug and process loads
Note on AY103: Leonard Thagard: Total CM DD estimate. Designer's DD estimate is $36,334,998.
Note on BA103: Leonard Thagard: baseline estimate from energy model report. Proposed estimate si $36,334,998 compared to CM estimate of
Note on A107: Leonard Thagard: Courtsey review only of energy model and LCCA per Greg Driver & Joe Bace discussion (SCO Director & AB Tech Fac/Oper Director)
Note on R107: Leonard Thagard: second lowest proposed EUI, second only to a warehouse/storage facility.
Note on S107: Leonard Thagard: Highest percentage savings to date.
Note on E110: Leonard Thagard: No updates to report as of 11.20.13. AP approved, design contract approved, no SD submission.

## 13.14 Meter Data
2013/2014 Meter Data Summary
1 | ASU - Cone Residence Hall Renovation | [16 empty] | ASU - Cone Residence Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 96643.12 | 114833.84 | 95351.84 | 74287.04 | 71859.28 | 63800.56 | 84077.36 | 66297.76 | 75581.2 | 80548.4 | 73478.08 | 82502.96 |  |  | 979261.44 | kwhs | 3342.2193 | MMbtu
| Steam (lbs) |  |  | 95933 | 132637.8 | 192700.2 | 214389.4 | 207715.8 | 381229.4 | 204379 | 255265.2 | 206881.6 | 81751.6 | 45881 | 58394 |  |  | 2077158 | lbs | 2077.158 | MMbtu | 5419.3773 | MMbtu
| Water (gallons) |  |  | 128000 | 190000 | 224300 | 173473 | 80000 | 185000 | 190346 | 140346 | 186283 | 77895 | 33085.173 | 78085 |  |  | 1686813.173 | gallons | 1686813.173 | gallons
| Elecricity Cost ($) |  |  | 8598.2021 | 10227.8989 | 8508.3279 | 6649.7124 | 6446.9613 | 5908.2048 | 7624.8998 | 5899.6245 | 6712.9535 | 7134.1322 | 6494.8624 | 7323.4779 |  |  | 87529.2577 |  | 87529.2577
| Steam Costs ($) |  |  | 2014.8 | 2785.68 | 4047.12 | 4502.64 | 4362.48 | 8006.64 | 4292.4 | 5361.12 | 4344.96 | 1716.96 | 963.6 | 1226.4 |  |  | 43624.8 |  | 43624.8
131154.0577
2 | UNCC - Prospector Hall Renovation Phase II | [16 empty] | UNCC - Prospector Hall Renovation Phase II
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 63690 | 96100 | 52663 | 52331 | 33231 | 38321 | 43278 | 49566 | 62030 | 69156 | 80988 | 46669 |  |  |  | 688023 | kwhs | 2348.2225 | MMbtu
| Nat Gas (Therms) |  | 1239 | 1174 | 2619 | 2610 | 3129 | 3244 | 4291 | 4676 | 3776 | 3140 | 1973 | 1643 |  |  |  | 33514 | therms | 3350.5998 | MMbtu | 5698.8223 | MMbtu
| Water Usage (CF) |  | 7650 | 51000 | 19210 | 18520 | 14660 | 14145 | 15295 | 15220 | 14250 | 14880 | 7480 | 12940 |  |  |  | 205250 | CF | 1535270 | gallons
| Elecricity Cost ($) |  | 4256.4121 | 6377.5562 | 3556.6848 | 3171.2637 | 1908.1012 | 2236.8602 | 2480.047 | 2889.8895 | 3675.1047 | 3931.4626 | 4675.4304 | 3027.0495 |  |  |  | 42185.862 |  | 42185.862
| Nat Gas Costs ($) |  | 1127.6177 | 1064.8769 | 2370.4083 | 2363.1818 | 2919.3327 | 2999.3232 | 4019.7124 | 4315.7191 | 3231.4581 | 2576.389 | 1748.7577 | 1610.2013 |  |  |  | 30346.978 |  | 30346.978
72532.8399
3 | UNCC - Miltimore Residence Hall | [16 empty] | UNCC - Miltimore Residence Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 217457 | 160490 | 203429 | 166251 | 138132 | 124889 | 139000 | 133870 | 139130 | 146224 | 153776 | 65996 |  |  |  | 1788644 | kwhs | 6104.642 | MMbtu
| Nat Gas (Therms) |  | 3277 | 3078 | 3630 | 4223 | 4887 | 5896 | 8070 | 8390 | 6911 | 4287 | 3143 | 3451 |  |  |  | 59243 | therms | 5922.8855 | MMbtu | 12027.5275 | MMbtu
| Water Usage (CF) |  | 23765 | 60876 | 74436 | 50221 | 55522 | 41439 | 76667 | 19317 | 60140 | 54212 | 42411 | 47588 |  |  |  | 606594 | CF | 4537323.12 | gallons
| Elecricity Cost ($) |  | 14532.6835 | 10650.7179 | 13738.9218 | 10074.8268 | 7931.4447 | 7289.9776 | 7965.3988 | 7805.1387 | 8243.065 | 8312.7161 | 8877.4755 | 4280.6393 |  |  |  | 109703.0057 |  | 109703.0057
| Nat Gas Costs ($) |  | 2982.4078 | 2791.9003 | 3285.4457 | 3823.6463 | 4559.533 | 5451.2976 | 7559.7946 | 7743.5592 | 5914.3556 | 3517.5094 | 2785.7807 | 3382.1088 |  |  |  | 53797.339 |  | 53797.339
163500.3447
4 | NCCU - Nursing Building | [16 empty] | NCCU - Nursing Building
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | * | [15 empty] | 0 | kwhs | 0 | MMbtu
| Steam (lbs) | * | [15 empty] | 0 | lbs |  | MMbtu
| Natural Gas (Therms) |  | 43 | 41 | 47 | 45 | 51 | 48 | 50 | 44 | 45 | 50 | 44 | 46 |  |  |  | 554 | therms | 55.3868 | MMbtu
| Water (CF) |  | 50613 | 32576 | 14693 | 8110 | 2418 | 2393 | 1963 | 2199 | 2114 | 5877 | 12506 | 15532 |  |  |  | 150994 | CF | 1129435.12 | gallons
| Elecricity Cost ($) | * | [15 empty] | 0 |  | 0
| Steam Costs ($) | * | [15 empty] | 0 |  | 0
| Natural Gas ( $) |  | 57.69 | 55.53 | 58.99 | 56.83 | 62.08 | 59.46 | 61.21 | 55.96 | 56.8 | 60.88 | 55.67 | 57.4 |  |  |  | 698.5 |  | 698.5
|  | * No data. Meters not operational. | [17 empty] | 698.5
5 | NCCU - Chidley Residence Hall | [16 empty] | NCCU - Chidley Residence Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 176060 | 174415 | 174280 | 168764 | 120336 | 89358 | 83521 | 92352 | 97382 | 128712 | 104508 | 67634 |  |  |  | 1477322 | kwhs | 5042.1 | MMbtu
| Steam (lbs) | * | [15 empty] | 0 | lbs |  | MMbtu
| Natural Gas (Therms) |  | 280 | 299 | 34 | 0 | 0 | 0 | 0 | 817 | 1425 | 1191 | 1572 | 215 |  |  |  | 5833 | therms | 583.1607 | MMbtu | 5625.2607 | Mmbtu
| Water (CF) |  | 16447 | 26360 | 52340 | 57520 | 62064 | 44528 | 12184 | 41108 | 44390 | 28911 | 52833 | 18204 |  |  |  | 456889 | CF | 3417529.72 | gallons
| Elecricity Cost ($) |  | 7381.1394 | 7312.1745 | 7306.5147 | 7075.2619 | 5044.9665 | 3746.2448 | 3501.5344 | 3871.7652 | 4082.643 | 5396.1219 | 4381.3934 | 2835.4878 |  |  |  | 61935.2475 |  | 61935.2475
| Steam Costs ($) | * | [15 empty] | 0 |  | 0
| Natural Gas ( $) |  | 291.38 | 309.81 | 50.7 | 17.5 | 17.5 | 17.5 | 17.5 | 735.92 | 1237.4 | 1044.99 | 1373.96 | 213.95 |  |  |  | 5328.11 |  | 5328.11
|  | * No data. Meters not operational. | [17 empty] | 67263.3575
6 | UNC-CH - Loudermilk | [16 empty] | UNC-CH - Loudermilk
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 142751 | 191399 | 157749 | 168745 | 149433 | 140210 | 148789 | 168547 | 150998 | 145846 | 158623 | 145460 |  | 1868550 | kwhs | 6377.3611 | MMbtu
| Steam Usage (mlbs) |  |  |  | 726 | 476 | 435 | 605 | 850 | 760 | 702 | 656 | 359 | 458 | 580 | 734 |  | 7341 | mlbs | 8765.154 | MMbtu
| Chilled water (ton-hrs) |  |  |  | 167254 | 113689 | 57995 | 11238 | 14795 | 1337 | 2008 | 2309 | 18183 | 91876 | 155036 | 166476 |  | 802196 | ton-hrs | 9626.352 | MMbtu
| Natural Gas (therms) |  |  |  | 151 | 316 | 335 | 385 | 416 | 305 | 372 | 281 | 379 | 289 | 176 | 130 |  | 3535 | therms | 353.4156 | MMbtu | 25122.2828 | Mmbtu
| Water Usage (kgallons) |  |  |  | 64 | 71 | 108 | 91 | 28 | 67 | 65 | 94 | 122 | 32 | 210 | 137 |  | 1089 | kgallons | 1089000 | gallons
| Electricity Cost ($) |  |  |  | 9107.51 | 11560.5 | 9480.71 | 9095.36 | 8323.42 | 8454.66 | 8793.43 | 8882.43 | 8923.98 | 8459.07 | 9850.49 | 9833.1 |  | 110764.66 |  | 110764.66
| Steam Cost ($) |  |  |  | 8154.58 | 5346.53 | 4886.01 | 6795.48 | 9547.37 | 8536.47 | 7885 | 7368.32 | 4032.36 | 5144.35 | 6515.78 | 8245.83 |  | 82458.08 |  | 82458.08
| Chilled Water ($) |  |  |  | 16290.54 | 11073.31 | 5648.71 | 1094.58 | 1441.03 | 130.22 | 195.58 | 224.9 | 1771.02 | 8948.72 | 14418.35 | 15482.27 |  | 76719.23 |  | 76719.23
| Natural Gas ($) |  |  |  | 158.1 | 307.18 | 324.45 | 369.91 | 398.09 | 297.18 | 358.09 | 273.51 | 361.96 | 280.73 | 178.27 | 136.25 |  | 3443.72 |  | 3443.72
269941.97
7 | DoAg&CS - Davis Arena | [16 empty] | DoAg&CS - Davis Arena
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 36600 | 43800 | 61400 | 37700 | 75700 | 28400 | 37900 | 36200 | 45900 | 42000 | 41400 | 50300 |  |  |  | 537300 | kwhs | 1833.8049 | MMbtu
| Nat Gas (Therms) |  | 110 | 155 | 142 | 347 | 1226 | 4592 | 5878 | 7314 | 5593 | 2972 | 1035 | 276 |  |  |  | 29640 | therms | 2963.2923 | MMbtu | 4797.0972 | Mmbtu
| Water Usage (gallons) |  | 12716 | 29172 | 71060 | 105468 | 34408 | 11968 | 17204 | 15708 | 23936 | 15708 | 48620 | 82280 |  |  |  | 468248 | gallons | 468248 | gallons
| Elecricity Cost ($) |  | 4034.18 | 4478.51 | 5764.87 | 3969.19 | 7040.4 | 3284.26 | 3914 | 3792.91 | 4483.8 | 4348.46 | 4211.4 | 4943.1 |  |  |  | 54265.08 |  | 54265.08
| Nat Gas Costs ($) |  | 125.47 | 169.65 | 155.9 | 338.38 | 1073.25 | 3850 | 4856.35 | 5952.64 | 4638.77 | 2517.46 | 3464.35 | 269 |  |  |  | 27411.22 |  | 27411.22
81676.3
8 | NCSU - Student Health Center Addition and Renovation | [16 empty] | NCSU - Student Health Center Addition and Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electric (kWh) |  |  |  | 64384.3453 | 67020.2609 | 64748.8092 | 61389.5423 | 63016.6942 | 61018.7101 | 68301.2237 | 66171.7788 | 66079.4689 | 63531.1419 | 67398.9993 | 74291.6667 |  | 787352.6411 | kwhs | 2687.2346 | MMbtu
| Chilled Water (Dtherms) |  |  |  | 783.6435 | 475.6293 | 131.8786 | 121.7749 | 114.291 | 106.2765 | 165.1844 | 313.4366 | 604.7734 | 845.3457 | 958.5018 | 937.0703 |  | 5557.8062 | dthrms | 5557.8062 | MMbtu
| Steam (1,000 lbs) |  |  |  | 366.45 | 436.5833 | 504.869 | 640.318 | 599.6652 | 438.3448 | 329.4253 | 375.6322 | 331.5977 | 298.7356 | 290 | 192 |  | 4803.6212 | 1000 lbs | 4803.6212 | MMbtu | 13048.6619 | Mmbtu
| Water (CCF) |  |  |  | 58.523 | 71.1527 | 82.3383 | 36.5903 | 33.1318 | 31.7874 | 45.3888 | 44.8612 | 39.3007 | 30.8218 | 36.0646 | 47.6347 |  | 557.5951 | CCF | 417081.1667 | gallons
| Electric Cost ($) |  |  |  | 5601.438 | 5830.7627 | 5633.1464 | 5340.8902 | 5482.4524 | 5308.6278 | 5942.2065 | 5756.9448 | 5748.9138 | 5527.2093 | 5863.7129 | 6463.375 |  | 68499.6798 |  | 68499.6798
| Chilled Water Cost ($) |  |  |  | 10743.7521 | 6520.8778 | 1808.0563 | 1669.5345 | 1566.9292 | 1457.051 | 2264.6782 | 4297.2151 | 8291.4438 | 11589.6902 | 13802.4263 | 13493.8128 |  | 77505.4673 |  | 77505.4673
| Steam Cost ($) |  |  |  | 5284.209 | 6295.5317 | 7280.2117 | 9233.3852 | 8647.1719 | 6320.9324 | 4750.3126 | 5416.6161 | 4781.6389 | 4307.7678 | 4022.3 | 2663.04 |  | 69003.1173 |  | 69003.1173
215008.2644
9 | ECSU - Gilchrist Ed & Psych Bldg | [16 empty] | ECSU - Gilchrist Ed & Psych Bldg
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity Usage (KWhs) |  | 57984 | 55872 | 54912 | 47040 | 52224 | 53760 | 45312 | 61824 | 48768 | 40704 | 37632 | 48000 |  |  |  | 604032 | kwhs | 2061.5612 | MMbtu
| Water Usage (gallons) |  | 4032.55 | 6507.99 | 6506.21 | 6886 | 3459.8 | 1843.55 | 1631.21 | 3347.66 | 2224.45 | 5903.93 | 4066.09 | 4406.22 |  |  |  | 50815.66 | gallons | 50815.66 | gallons
| Elecricity Cost ($) |  | 7149.86 | 6834.85 | 7081.17 | 5824.79 | 6651.71 | 6224.35 | 5518.37 | 6829.41 | 5946.53 | 5304.53 | 4903.43 | 6276.31 |  |  |  | 74545.31 |  | 74545.31
10 | DoAg&CS - SENC Ag Center | [16 empty] | DoAg&CS - SENC Ag Center
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 2160 | 3000 | 3880 | 4120 | 2640 | 2560 | 2440 | 2120 | 2360 | 3120 | 2080 | 3840 |  |  |  | 34320 | kwhs | 117.1342 | MMbtu
| Nat Gas (Therms) |  | 27 | 23 | 28 | 247 | 420 | 706 | 1706 | 844 | 414 | 85 | 28 | 27 |  |  |  | 4555 | therms | 455.3912 | MMbtu | 572.5254 | Mmbtu
| Water Usage (gallons) |  | 34980 | 69680 | 57720 | 86280 | 18990 | 28600 | 38130 | N/A | 36090 | 43300 | 75980 | 29880 |  |  |  | 519630 | gallons | 519630 | gallons
| Elecricity Cost ($) |  | 628.28 | 700.93 | 929.19 | 802.74 | 1005.66 | 654.97 | 715.15 | 633.25 | 0 | 0 | 252.79 | 876.54 |  |  |  | 7199.5 |  | 7199.5
| Nat Gas Costs ($) |  | 46.59 | 42.94 | 47.5 | 261.43 | 408.94 | 676.07 | 1620.61 | 790.77 | 364.27 | 92.09 | 47.23 | 48.21 |  |  |  | 4446.65 |  | 4446.65
11646.15
11 | UNCC - EPIC | [16 empty] | UNCC - EPIC
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 360773 | 376949 | 339208 | 475978 | 334420 | 456727 | 399272 | 284263 | 314420 | 413293 | 410392 | 391747 |  |  |  | 4557442 | kwhs | 15554.5495 | MMbtu
| Nat Gas (Therms) |  | 499 | 480 | 514 | 501 | 4215 | 4822 | 6505 | 4875 | 4806 | 2638 | 452 | 165 |  |  |  | 30472 | therms | 3046.4725 | MMbtu
| Chilled water (BTU*10^6) |  | 2730 | 2466 | 2118 | 1481 | 1018 | 728 | 486 | 530 | 613 | 1247 | 1912 | 2337 |  |  |  | 17666 | MMbtu | 17666 | MMbtu
| Hot Water (BTU*10^6) |  | 418 | 526 | 551 | 613 | 955 | 735 | 925 | 588 | 602 | 410 | 184 | 168 |  |  |  | 6675 | MMbtu | 6675 | MMbtu | 42942.022 | MMbtu
| Water Usage (CF) |  | 6260 | 6901 | 11570 | 8030 | 14562 | 12049 | 18954 | 14132 | 17648 | 9747 | 5630 | 8555 |  |  |  | 134038 | CF | 1002604.24 | gallons
| Elecricity Cost ($) |  | 24110.5129 | 25015.7484 | 22908.9863 | 28844.3132 | 19202.1671 | 26659.9109 | 22880.293 | 16573.6322 | 18628.5092 | 23495.3726 | 23691.8954 | 25409.5342 |  |  |  | 277420.8756 |  | 277420.8756
| Nat Gas Costs ($) |  | 564.2193 | 473.0477 | 480.0909 | 468.3496 | 4041.7167 | 4628.9637 | 6263.0235 | 4577.6693 | 4222.6035 | 2212.2263 | 410.6048 | 176.88 |  |  |  | 28519.3952 |  | 28519.3952
| Chilled Water |  | 12858.3 | 11614.86 | 9975.78 | 6975.51 | 4794.78 | 3428.88 | 2289.06 | 2496.3 | 2887.23 | 5873.37 | 9005.52 | 11007.27 |  |  |  | 83206.86 |  | 83206.86
| Hot Water |  | 3122.46 | 3929.22 | 4115.97 | 4579.11 | 7133.85 | 5490.45 | 6909.75 | 4392.36 | 4496.94 | 3062.7 | 1374.48 | 1254.96 |  |  |  | 49862.25 |  | 49862.25
439009.3809
12 | DOA - VA - VA Home Swananoa | [16 empty] | DOA - VA - VA Home Swananoa
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 152296 | 149628 | 156506 | 161390 | 165600 | 159984 | 154587 | 140548 | 156153 | 169544 | 174724 | 171911 |  | 1912871 | kwhs | 6528.6287 | MMbtu
| Nat Gas (Therms) |  |  |  | 1213 | 1541 | 1649 | 2164 | 2889 | 1316 | 1988 | 2180 | 1850 | 1648 | 1898 | 1719 |  | 22055 | therms | 2204.9734 | MMbtu | 8733.6021 | Mmbtu
| Water Usage (CF) |  |  |  | 3809 | 4051 | 4539 | 4647 | 5009 | 5463 | 5791 | 6173 | 6567 | 6978 | 5886 | 7680 |  | 66593 | CF | 498115.64 | gallons
| Elecricity Cost ($) |  |  |  | 12775.39 | 12473.39 | 12326.65 | 13270.41 | 13817.56 | 13187.61 | 12639.42 | 11636.7 | 12726.58 | 13809.79 | 14353.83 | 14122.68 |  | 157140.01 |  | 157140.01
| Nat Gas Costs ($) |  |  |  | 1079.77 | 1278.27 | 1326.43 | 1846.92 | 2444.9 | 1147.49 | 1701.75 | 1883.57 | 1540.93 | 1474.33 | 1688.33 | 1533.74 |  | 18946.43 |  | 18946.43
176086.44
13 | Pitt CC - Russell Classroom Building | [16 empty] | Pitt CC - Russell Classroom Building
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Gas Usage (CCF) | [16 empty] | 0 | CCF | 0 | MMbtu
| Water (gallons) CCF? | [16 empty] | 0 | CCF | 0 | gallons
| Elecricity Cost ($) | [16 empty] | 0 |  | 0
| Gas Cost ($) | [16 empty] | 0 |  | 0
0
14 | UNCG - Bailey Residence Hall Renovation | [16 empty] | UNCG - Bailey Residence Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 25053 | 25134 | 28239 | 20460 | 25563 | 24454 | 22098 | 25793 | 20663 | 15650 | 15399 | 25182 |  | 273688 | kwhs | 934.0971 | MMbtu
| Steam Usage (lbs) |  |  |  | 11480 | 25760 | 123940 | 175720 | 246650 | 178290 | 97990 | 25440 | 6630 | 4130 | 3810 | 9290 |  | 909130 | lbs | 909.13 | MMbtu
| Chilled water (ton-hrs) |  |  |  | 19492 | 18522 | 11913 | 10588 | 7195 | 8456 | 8389 | 14529 | 28608 | 22546 | 21501 | 28341 |  | 200080 | ton-hrs | 2400.96 | MMbtu | 4244.1871 | Mmbtu
| Water (gallons) |  |  |  | 52600 | 52900 | 59100 | 15700 | 43700 | 51400 | 39400 | 52700 | 13700 | 1000 | 600 | 47500 |  | 430300 | gallons | 430300 | gallons
| Electricity Cost ($) |  |  |  | 1782.02 | 1601.38 | 1702.92 | 1277.51 | 1564.76 | 1465.44 | 1379.16 | 1530.04 | 1261.91 | 1061.54 | 1044.52 | 1708.09 |  | 17379.29 |  | 17379.29
| Steam Cost ($) |  |  |  | 89.69 | 201.27 | 968.4 | 1372.99 | 1927.2 | 1393.09 | 765.65 | 198.76 | 51.8 | 32.27 | 29.77 | 72.58 |  | 7103.47 |  | 7103.47
| Chilled Water ($) |  |  | * | [13 empty] | 0 |  | 0
|  |  |  | * | No chilled water meter data. | [14 empty] | 24482.76
15 | UNCG - Coit Residence Hall Renovation | [16 empty] | UNCG - Coit Residence Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 23834 | 24071 | 28259 | 19016 | 18684 | 17980 | 22050 | 24756 | 20501 | 15721 | 15058 | 22964 |  | 252894 | kwhs | 863.1272 | MMbtu
| Steam Usage (lbs) |  |  |  | 18790 | 35540 | 67950 | 35990 | 65960 | 49660 | 16350 | 15230 | 7320 | 3870 | 3580 | 7620 |  | 327860 | lbs | 327.86 | MMbtu
| Chilled water (ton-hrs) |  |  |  | 17804 | 15818 | 13265 | 10015 | 6558 | 6932 | 10604 | 13436 | 17467 | 22527 | 20569 | 23987 |  | 178982 | ton-hrs | 2147.784 | MMbtu | 3338.7712 | Mmbtu
| Water (gallons) |  |  |  | 50200 | 46800 | 48900 | 12400 | 95100 | 44700 | 33800 | 44800 | 11300 | 1000 | 1000 | 32800 |  | 422800 | gallons | 422800 | gallons
| Electricity Cost ($) |  |  |  | 1695.31 | 1533.65 | 1704.13 | 1187.34 | 1143.68 | 1077.47 | 1376.16 | 1468.52 | 1252.02 | 1066.36 | 1021.38 | 1557.65 |  | 16083.67 |  | 16083.67
| Steam Cost ($) |  |  |  | 148.23 | 277.71 | 530.95 | 281.23 | 515.4 | 388.04 | 127.75 | 118.99 | 57.19 | 30.24 | 27.97 | 59.53 |  | 2563.23 |  | 2563.23
| Chilled Water ($) |  |  | * | [13 empty] | 0 |  | 0
|  |  |  | * | No chilled water meter data. | [14 empty] | 18646.9
16 | UNCG - Cotten Residence Hall Renovation | [16 empty] | UNCG - Cotten Residence Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 25488 | 25792 | 29122 | 20458 | 25362 | 24858 | 22332 | 24797 | 22117 | 16522 | 16664 | 24495 |  | 278007 | kwhs | 948.8379 | MMbtu
| Steam Usage (lbs) |  |  |  | 18660 | 42650 | 178400 | 222330 | 307240 | 214670 | 187860 | 5500 | 1200 | 800 | 7670 | 17550 |  | 1204530 | lbs | 1204.53 | MMbtu
| Chilled water (ton-hrs) |  |  |  | 15106 | 12124 | 9249 | 6692 | 4295 | 6190 | 6354 | 11830 | 13283 | 15463 | 15205 | 20417 |  | 136208 | ton-hrs | 1634.496 | MMbtu | 3787.8639 | Mmbtu
| Water (gallons) |  |  |  | 57400 | 53500 | 58100 | 18100 | 48000 | 52700 | 42600 | 56500 | 15100 | 1100 | 2000 | 38200 |  | 443300 | gallons | 443300 | gallons
| Electricity Cost ($) |  |  |  | 1812.96 | 1643.3 | 1756.17 | 1277.38 | 1552.46 | 1489.65 | 1393.76 | 1470.95 | 1350.71 | 1120.69 | 1130.32 | 1661.49 |  | 17659.84 |  | 17659.84
| Steam Cost ($) |  |  |  | 145.8 | 333.26 | 1393.98 | 1737.26 | 2400.74 | 1677.41 | 1467.92 | 42.98 | 9.38 | 6.25 | 59.92 | 137.11 |  | 9412.01 |  | 9412.01
| Chilled Water ($) |  |  | * | [13 empty] | 0 |  | 0
|  |  |  | * | No chilled water meter data. | [14 empty] | 27071.85
17 | UNCG - Gray Residence Hall Renovation | [16 empty] | UNCG - Gray Residence Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 25748 | 25583 | 28483 | 20273 | 24384 | 24093 | 21685 | 25360 | 22439 | 17547 | 17041 | 24553 |  | 277189 | kwhs | 946.0461 | MMbtu
| Steam Usage (lbs) |  |  |  | 19220 | 74170 | 101070 | 164580 | 79260 | 27740 | 21140 | 17150 | 6640 | 3240 | 3420 | 8350 |  | 525980 | lbs | 525.98 | MMbtu
| Chilled water (ton-hrs) |  |  |  | 15498 | 4827 | 1746 | 2355 | 1761 | 1185 | 1361 | 4590 | 10241 | 14216 | 13854 | 18369 |  | 90003 | ton-hrs | 1080.036 | MMbtu | 2552.0621 | Mmbtu
| Water (gallons) |  |  |  | 56300 | 54600 | 60100 | 15500 | 39800 | 45400 | 36400 | 46400 | 11400 | 300 | 2500 | 39200 |  | 407900 | gallons | 407900 | gallons
| Electricity Cost ($) |  |  |  | 1831.46 | 1629.99 | 1717.64 | 1265.83 | 1492.59 | 1443.8 | 1353.38 | 1504.35 | 1370.38 | 1190.22 | 1155.89 | 1665.43 |  | 17620.96 |  | 17620.96
| Steam Cost ($) |  |  |  | 150.18 | 579.56 | 789.75 | 1286.02 | 619.33 | 216.75 | 165.18 | 134 | 51.88 | 25.32 | 26.72 | 65.24 |  | 4109.93 |  | 4109.93
| Chilled Water ($) |  |  | * | [13 empty] | 0 |  | 0
|  |  |  | * | No chilled water meter data. | [14 empty] | 21730.89
18 | UNCG - Hinshaw Residence Hall Renovation | [16 empty] | UNCG - Hinshaw Residence Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 28712 | 29511 | 33257 | 24327 | 30170 | 27805 | 25465 | 29541 | 25832 | 21021 | 20853 | 31432 |  | 327926 | kwhs | 1119.2114 | MMbtu
| Steam Usage (lbs) |  |  |  | 16160 | 19220 | 74170 | 101070 | 164580 | 93920 | 79260 | 21760 | 18500 | 7260 | 7050 | 16160 |  | 619110 | lbs | 619.11 | MMbtu
| Chilled water (ton-hrs) |  |  |  | 20812 | 13519 | 8387 | 7243 | 4389 | 5121 | 5517 | 10705 | 14355 | 17665 | 17243 | 24184 |  | 149140 | ton-hrs | 1789.68 | MMbtu | 3528.0014 | Mmbtu
| Water (gallons) |  |  |  | 45900 | 43000 | 45600 | 11900 | 42900 | 44900 | 38400 | 48000 | 14900 | 2000 | 2500 | 46000 |  | 386000 | gallons | 386000 | gallons
| Electricity Cost ($) |  |  |  | 2042.29 | 1880.26 | 2005.53 | 1518.96 | 1846.76 | 16666.25 | 1589.3 | 1752.37 | 1577.59 | 1425.86 | 1414.46 | 2132.3 |  | 35851.93 |  | 35851.93
| Steam Cost ($) |  |  |  | 126.27 | 150.18 | 579.56 | 789.75 | 1286.02 | 733.88 | 619.33 | 170.02 | 144.55 | 56.73 | 55.08 | 126.25 |  | 4837.62 |  | 4837.62
| Chilled Water ($) |  |  | * | [13 empty] | 0 |  | 0
|  |  |  | * | No chilled water meter data. | [14 empty] | 40689.55
19 | UNCG - Jamison Residence Hall Renovation | [16 empty] | UNCG - Jamison Residence Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 25616 | 25462 | 28596 | 20973 | 26326 | 25140 | 22531 | 26409 | 21608 | 17290 | 16370 | 25698 |  | 282019 | kwhs | 962.5308 | MMbtu
| Steam Usage (lbs) |  |  |  | 14010 | 19540 | 26860 | 30120 | 152230 | 106610 | 54940 | 9057 | 7490 | 4430 | 4310 | 7090 |  | 436687 | lbs | 436.687 | MMbtu
| Chilled water (ton-hrs) |  |  |  | 73070 | 63360 | 43080 | 37670 | 36410 | 41780 | 37230 | 50260 | 59920 | 76220 | 81520 | 90670 |  | 691190 | ton-hrs | 8294.28 | MMbtu | 9693.4978 | Mmbtu
| Water (gallons) |  |  |  | 47100 | 44600 | 46200 | 12500 | 41300 | 46600 | 36500 | 51000 | 15100 | 5000 | 1830 | 43600 |  | 391330 | gallons | 391330 | gallons
| Electricity Cost ($) |  |  |  | 1822.07 | 1622.28 | 1724.45 | 1309.54 | 1611.46 | 1506.55 | 1406.18 | 1566.58 | 1319.63 | 1172.78 | 1110.37 | 1743.09 |  | 17914.98 |  | 17914.98
| Steam Cost ($) |  |  |  | 109.46 | 152.68 | 209.88 | 235.35 | 1189.51 | 833.04 | 110.12 | 70.76 | 58.52 | 34.61 | 33.67 | 55.39 |  | 3092.99 |  | 3092.99
| Chilled Water ($) | [16 empty] | 0 |  | 0
21007.97
20 | UNCG - Shaw Residence Hall Renovation | [16 empty] | UNCG - Shaw Residence Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 47115 | 47333 | 52848 | 39962 | 49214 | 46143 | 41387 | 48781 | 42948 | 33373 | 32432 | 44245 |  | 525781 | kwhs | 1794.4906 | MMbtu
| Steam Usage (lbs) |  |  |  | 53240 | 164380 | 704150 | 751020 | 1089140 | 817570 | 691630 | 207770 | 139600 | 14660 | 5440 | 12360 |  | 4650960 | lbs | 4650.96 | MMbtu
| Chilled water (ton-hrs) |  |  |  | 39687 | 36569 | 33365 | 30866 | 21826 | 19329 | 25175 | 31822 | 38534 | 42917 | 41963 | 55574 |  | 417627 | ton-hrs | 5011.524 | MMbtu | 11456.9746 | Mmbtu
| Water (gallons) |  |  |  | 83400 | 80700 | 84800 | 24500 | 72900 | 86300 | 66100 | 90000 | 24300 | 800 | 3600 | 66600 |  | 684000 | gallons | 684000 | gallons
| Electricity Cost ($) |  |  |  | 3351.29 | 3015.76 | 3186.94 | 2495.19 | 3012.48 | 2765.18 | 2583.01 | 2893.68 | 2622.89 | 2263.7 | 2199.86 | 3001.13 |  | 33391.11 |  | 33391.11
| Steam Cost ($) |  |  |  | 416.02 | 1284.49 | 5502.16 | 5868.4 | 8510.04 | 6388.41 | 5404.33 | 1623.49 | 1090.82 | 114.55 | 42.5 | 96.56 |  | 36341.77 |  | 36341.77
| Chilled Water ($) | [16 empty] | 0 |  | 0
69732.88
21 | WCU - Harrill Residence Hall Renovation | [16 empty] | WCU - Harrill Residence Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 74080 | 88168 | 94347 | 79716 | 75594 | 66617 | 85340 | 76631 | 72908 | 70976 | 59228 | 60285 |  |  |  | 903890 | kwhs | 3084.9766 | MMbtu
| Water (gallons) |  | 20180 | 111900 | 206350 | 166780 | 170630 | 81220 | 141630 | 141240 | 52920 | 73766 | 60030 | 9290 |  |  |  | 1235936 | gallons | 1235936 | gallons
| Elecricity Cost ($) |  | 5158.04 | 6351.6 | 6775.34 | 4737.52 | 4513.57 | 4111.27 | 5047.43 | 4655.49 | 4283.78 | 4205.75 | 3551.78 | 4406.35 |  |  |  | 57797.92 |  | 57797.92
22 | UNCP Health Science Builidng | [16 empty] | UNCP Health Science Builidng
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 132276 | 137730 | 134465 | 124059 | 117931 | 93622 | 110748 | 109838 | 79601 | 106369 | 52332 | 111294 |  |  |  | 1310265 | kwhs | 4471.9344 | MMbtu
| Nat Gas (Therms) |  | 1577 | 1398 | 1304 | 1202 | 2179 | 2368 | 4126 | 4009 | 2298 | 2457 | 1910 | 1177 |  |  |  | 26005 | therms | 2599.8791 | MMbtu | 7071.8136 | MMBtu
| Water (gallons) |  | 147700 | 141500 | 131000 | 67100 | 31250 | 18300 | 9750 | 10120 | 26800 | 50000 | 94225 | 120500 |  |  |  | 848245 | gallons | 848245 | gallons
| Electricity Cost ($) |  | 10682.6098 | 11123.0748 | 10859.3934 | 10019.0048 | 9524.1076 | 7560.9127 | 8944.0085 | 8870.5169 | 6428.5768 | 8590.3604 | 4226.3323 | 8988.1034 |  |  |  | 105817.0014 |  | 105817.0014
| Nat Gas Costs ($) |  | 907.4058 | 804.4092 | 750.3216 | 691.6308 | 1253.7966 | 1362.5472 | 2374.1004 | 2306.7786 | 1322.2692 | 1413.7578 | 1099.014 | 677.2458 |  |  |  | 14963.277 |  | 14963.277
120780.2784
23 | FSU - Renaissance Residence Hall | [16 empty] | FSU - Renaissance Residence Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Elecricity Cost ($) | [16 empty] | 0 |  | 0
24 | UNCA - Overlook Residence Hall | [16 empty] | UNCA - Overlook Residence Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Elecricity Cost ($) | [16 empty] | 0 |  | 0
25 | ECSU - Viking Tower Residence Hall | [16 empty] | ECSU - Viking Tower Residence Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity Usage (KWhs) |  | 48053 | 56310 | 63175 | 64734 | 55026 | 46456 | 48327 | 49101 | 51656 | 57063 | 47757 | 43244 |  |  |  | 630902 | kwhs | 2153.2685 | MMbtu
| Water (gallons) |  | 48861 | 112674 | 264394 | 244725 | 139753 | 139753 | 150199 | 166150 | 151077 | 211623 | 73612 | 41488 |  |  |  | 1744309 | gallons | 1744309 | gallons
| Elecricity Cost ($) |  | 4867.72 | 5951.96 | 6608.09 | 6868.25 | 5915.33 | 4915.04 | 5166.14 | 5263.58 | 5501.36 | 5991.59 | 4995.37 | 4631.39 |  |  |  | 66675.82 |  | 66675.82
26 | UNCW Teaching Lab | [16 empty] | UNCW Teaching Lab
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 109141 | 89326 | 85857 | 137600 | 65888 | 108352 | 120241 | 103751 | 101400 | 96239 | 74474 | 93475 |  |  |  | 1185744 | kwhs | 4046.9443 | MMbtu
| Heating Hot Water Usage (MMbtu) |  |  |  | 98480 | 192448.7 | 256470.9875 | 246075.9 | 413569.8875 | 367402.9125 | 327137.85 | 239755.8875 | 206739.5 | 180217.2875 |  |  |  | 2528298.9125 | MMbtu | 2528.2989 | MMbtu
| Chilled water (ton-hrs) |  |  |  | 80296 | 95195 | 43466 | 36570 | 19051 | 23850 | 23687 | 76208 | 114941.3521 | 160071.7198 |  |  |  | 673336.0719 | ton-hrs | 8080.0329 | MMbtu | 14655.276 | MMbtu
| Water Usage (gallons) |  | 27827 | 106428 | 31150 | 316096 | 388811 | 416254 | -962866 | 68544 | 69405 | 71453 | 45725 | 48096 |  |  |  | 626923 | gallons | 626923 | gallons
| Electricity Cost ($) |  | 8731.28 | 7565.91 | 6859.97 | 10182.4 | 4645.1 | 8039.72 | 8501.04 | 7843.58 | 7361.64 | 6794.47 | 5183.39 | 7599.52 |  |  |  | 89308.02 |  | 89308.02
| Heating Hot Water ($) |  | 1828.29 | 1455 | 1208 | 2422 | 1567 | 3248 | 2711 | 3327 | 2821 | 1789 | 1578 | 1927 |  |  |  | 25881.29 |  | 25881.29
| Chilled Water ($) |  | 16088 | 14362 | 8271 | 7801 | 1814 | 3336 | 2530 | 2243 | 2486 | 5389 | 5703 | 12696 |  |  |  | 82719 |  | 82719
197908.31
27 | UNCA - Rhoades Hall Renovation | [16 empty] | UNCA - Rhoades Hall Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Elecricity Cost ($) | [16 empty] | 0 |  | 0
28 | ECU - Ross Hall | [16 empty] | ECU - Ross Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 188476.34 | 187630.31 | 177812.54 | 176182.44 | 184912.54 | 167556.58 | 187339.86 | 186005.46 | 201417.79 | 186189 | 190007 | 191943 |  | 2225472.86 | kwhs | 7595.5389 | MMbtu
| Chilled water (ton-hrs) | [16 empty] | 0 | ton-hrs | 0 | MMbtu
| Water Usage (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) |  |  |  | 17716.776 | 17637.2491 | 16714.3788 | 16561.1494 | 17381.7788 | 15750.3185 | 17609.9468 | 17484.5132 | 18933.2723 | 17501.766 | 17860.658 | 18042.642 |  | 209194.4488 |  | 209194.4488
| Chilled Water ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
209194.4488
29 | Gaston College - Lena Sue Beam Renovation | [16 empty] | Gaston College - Lena Sue Beam Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Heating Hot Water (?) | [16 empty] | 0 | lbs | 0 | MMbtu
| Chilled water (ton-hrs) | [16 empty] | 0 | ton-hrs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Electricity Cost ($) | [16 empty] | 0 |  | 0
| Heating Hot Water Cost ($) | [16 empty] | 0 |  | 0
| Chilled Water ($) | [16 empty] | 0 |  | 0
0
30 | NCSU - Hunt Library | [16 empty] | NCSU - Hunt Library
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electric (kWh) |  |  |  | 365680.8245 | 375253.554 | 367059.5389 | 350414.1822 | 349761.6153 | 329313.9403 | 325871.9224 | 341362.9913 | 347227.0203 | 347058.96 | 352408.0811 | 352410.8887 |  | 4203823.5187 | kwh | 14347.6497 | MMbtu
| Chilled Water (Dtherms) |  |  |  | 385.3984 | 768.36 | 928.36 | 802.45 | 905.56 | 790.99 | 663.48 | 268.4 | 7223.208 | 6896.752 | 6485.24 | 6501.92 |  | 32620.1184 | dthrms | 32620.1184 | MMbtu
| Steam (1,000 lbs) |  |  |  | NA | NA | 5385 | 1274 | 1539 | 1287 | 1275 | 1023 | 1024 | 985 | 343.2969 | 345.3047 |  | 14480.6016 | 1000 lbs | 14480.6016 | MMbtu | 61448.3697 | MMbtu
| Water (CF) |  |  |  | 145.9627 | 164.3336 | 157.079 | 112.4944 | 112.1846 | 126.3049 | 164.661 | 175.0607 | 120.1814 | 575 | 341 | 301 |  | 2495.2624 | CCF | 1866456.3085 | gallons
| Electric Cost ($) |  |  |  | 31814.2317 | 32647.0592 | 31934.1799 | 30486.0338 | 30429.2605 | 28650.3128 | 28350.8572 | 29698.5802 | 30208.7508 | 30194.1295 | 30659.5031 | 30659.7473 |  | 365732.6461 |  | 365732.6461
| Chilled Water Cost ($) |  |  |  | 5283.8125 | 10534.2156 | 12727.8156 | 11001.5895 | 12415.2276 | 10844.4729 | 9096.3108 | 3679.764 | 99030.1817 | 94554.4699 | 93387.456 | 93627.648 |  | 456182.9641 |  | 456182.9641
| Steam Cost ($) |  |  |  | NA | NA | 77651.7 | 18371.08 | 22192.38 | 18558.54 | 18385.5 | 14751.66 | 14766.08 | 14203.7 | 4761.5277 | 4789.376 |  | 208431.5437 |  | 208431.5437
1030347.1539
31 | UNCC - Rose Football Center | [16 empty] | UNCC - Rose Football Center
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 161849 | 167621 | 182746 | 175264 | 165377 | 138223 | 119830 | 116370 | 194940 | 100670 | 146090 | 143280 |  |  |  | 1812260 | kwhs | 6185.2434 | MMbtu
| Nat Gas (Therms) |  | 1562 | 1694 | 2077 | 2277 | 3889 | 3340 | 4159 | 3475 | 3298 | 2174 | 1014 | 1031 |  |  |  | 29990 | therms | 2998.284 | MMbtu | 9183.5274 | Mmbtu
| Water Usage (CF) |  | 5490 | 15661 | 14440 | 14072 | 9708 | 2193 | 5277 | 5689 | 12523 | 7430 | 5461 | 5332 |  |  |  | 103276 | CF | 772504.48 | gallons
| Elecricity Cost ($) |  | 10816.3926 | 11123.9578 | 12342.0604 | 10621.0155 | 9495.834 | 8068.3053 | 6866.8615 | 6784.821 | 11549.652 | 5723.008 | 8433.7633 | 9293.4421 |  |  |  | 111119.1135 |  | 111119.1135
| Nat Gas Costs ($) |  | 1421.581 | 1536.5429 | 1890.94 | 2070.68 | 3632.33 | 3098.56 | 3905.05 | 3217.44 | 2833.32 | 1794.83 | 905.17 | 940.95 |  |  |  | 27247.394 |  | 27247.394
138366.5075
32 | DOA - VA - VA Home Kinston | [16 empty] | DOA - VA - VA Home Kinston
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 161600 | 141600 | 143400 | 149400 | 154400 | 156800 | 156600 | 130000 | 173200 | 135800 | 186000 | 170800 |  |  | 1859600 | kwhs | 6346.8148 | MMbtu
| Nat Gas (Therms) |  |  | 723 | 739 | 865 | 963 | 922 | 1343 | 902 | 1093 | 1216 | 1071 | 1119 | 1251 |  |  | 12207 | therms | 1220.4086 | MMbtu | 7567.2234
| Water Usage (gallons) |  |  | 159550 | 81300 | 71600 | 112300 | 137480 | 124050 | 143200 | 136010 | 116500 | 141800 | 161100 | 182600 |  |  | 1567490 | gallons | 1567490 | gallons
| Elecricity Cost ($) |  |  | 13344.33 | 12036.47 | 12116.49 | 12380.97 | 12747.97 | 12650.83 | 12896.19 | 12896.19 | 13921.29 | 11155.12 | 15036.73 | 14221.17 |  |  | 155403.75 |  | 155403.75
| Nat Gas Costs ($) |  |  | 674.14 | 688.52 | 801.75 | 917.8 | 872.94 | 1277.49 | 903.14 | 1878.26 | 1015.77 | 951.11 | 1019.18 | 1166.66 |  |  | 12166.76 |  | 12166.76
167570.51
33 | Randolph CC - Klaussner Building Renovation | [16 empty] | Randolph CC - Klaussner Building Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 64600 | 53900 | 64100 | 54700 | 49500 | 41600 | 31300 | 36600 | 44300 | 60400 | 61700 | 76000 |  |  |  | 638700 | kwhs | 2179.8831 | MMbtu
| Nat Gas (Therms) |  | 239 | 273 | 152 | 702 | 843 | 1057 | 1141 | 1560 | 1110 | 732 | 311 | 259 |  |  |  | 8379 | therms | 837.6999 | MMbtu | 3017.583 | MMbtu
| Water Usage (CF) |  | 87 | 119 | 118 | 146 | 109 | 82 | 110 | 187 | 157 | 199 | 110 | 137 |  |  |  | 1561 | CF | 11676.28 | gallons
| Elecricity Cost ($) |  | 6072.72 | 5451.8 | 6198.78 | 5171.75 | 4786.28 | 4357.81 | 3356.24 | 3689.73 | 4238.76 | 5700.57 | 5808.78 | 6324.94 |  |  |  | 61158.16 |  | 61158.16
| Nat Gas Costs ($) |  | 239.19 | 269.74 | 160.42 | 693.36 | 796.87 | 1002.42 | 1090.66 | 1429.94 | 934.98 | 627.68 | 300.88 | 260.2 |  |  |  | 7806.34 |  | 7806.34
68964.5
34 | ASU - Plemmons Student Union Addition | [16 empty] | ASU - Plemmons Student Union Addition
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 181802.96 | 239736.72 | 193410.72 | 167832.32 | 158616.24 | 151638.48 | 173009.88 | 145604.08 | 167482.6 | 163268.2 | 150024.64 | 154229.68 |  |  | 2046656.52 | kwhs | 6985.2387 | MMbtu
| Steam (lbs) |  |  | 731593.4 | 461312.6 | 842542 | 674867.8 | 809174 | 1115325.4 | 682375.6 | 902604.4 | 724919.8 | 504691 | 397913.4 | 470488.8 |  |  | 8317808.2 | lbs | 8317.8082 | MMbtu | 15303.0469 | MMbtu
| Water (gallons) |  |  | 333000 | 427000 | 475900 | 456359 | 390001 | 507000 | 540918 | 183918 | 228589 | 211785 | 332555.459 | 156555 |  |  | 4243580.459 | gallons | 4243580.459 | gallons
| Elecricity Cost ($) |  |  | 16105.9043 | 21296.4452 | 17214.78 | 14999.8414 | 14213.2466 | 14023.0962 | 15671.5612 | 12939.7978 | 14853.0983 | 14424.6939 | 13218.7814 | 13631.797 |  |  | 182593.0434 |  | 182593.0434
| Steam Costs ($) |  |  | 15365.04 | 9688.56 | 17695.2 | 14173.68 | 16994.4 | 23424.24 | 14331.36 | 18956.64 | 15224.88 | 10599.6 | 8357.04 | 9881.28 |  |  | 174691.92 |  | 174691.92
357284.9634
35 | ASU - Summit Residence Hall and Appalachian Hall | [16 empty] | ASU - Summit Residence Hall and Appalachian Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  | 107513.92 | 140709.44 | 116877.44 | 96720.64 | 88444.48 | 70200.96 | 106069.76 | 76516.16 | 90139.2 | 97414.4 | 90465.28 | 92359.36 |  |  | 1173431.04 | kwhs | 4004.9201 | MMbtu
| Steam (lbs) |  |  | 437120.8 | 359540.2 | 462981 | 530551.2 | 387068.8 | 846713 | 451302.2 | 542230 | 358706 | 216892 | 246923.2 | 286964.8 |  |  | 5126993.2 | lbs | 5126.9932 | MMbtu | 9131.9133 | MMbtu
| Water (gallons) |  |  | 139528 | 218280 | 274768 | 222064 | 95872 | 182328 | 224152 | 172792 | 245264 | 117648 | 78184.368 | 95304 |  |  | 2066184.368 | gallons | 2066184.368 | gallons
| Elecricity Cost ($) |  |  | 9500.1636 | 12473.9959 | 10394.3221 | 8649.9062 | 7939.7522 | 6503.649 | 9620.539 | 6814.5477 | 8000.3182 | 8603.7338 | 7962.9562 | 8147.895 |  |  | 104611.7789 |  | 104611.7789
| Steam Costs ($) |  |  | 10688.82 | 8791.75 | 11321.17 | 12973.44 | 9464.91 | 19687.45 | 11035.59 | 13259.03 | 8771.36 | 5303.61 | 6037.95 | 7017.09 |  |  | 124352.17 |  | 124352.17
228963.9489
36 | UNCW - MARBIONC | [16 empty] | UNCW - MARBIONC
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | * | * | 271000 | 257600 | 248800 | 232400 | 217000 | 188400 | 237000 | 238000 | 322800 | 334000 |  |  |  | 2547000 | kwhs | 8692.911 | MMbtu
| Nat Gas (MCF) |  | * | 705 | 423.4 | 510.3 | 755.6 | 1098.6 | 1300.4 | 1061.6 | 383.5 | 713 | 697.4 | 642.9 |  |  |  | 8291.7 | MCF | 8515.5759 | MMbtu | 17208.4869 | MMbtu
| Water Usage (CF) |  | * | * | * | * | * | * | * | * | * | * | * | * |  |  |  | 0 | CF | 0 | gallons
| Elecricity Cost ($) |  | * | * | 23490.26 | 21781.91 | 21124.71 | 19507.65 | 18410.8 | 16373.78 | 19835.29 | 19906.51 | 26005.39 | 25641.94 |  |  |  | 212078.24 |  | 212078.24
| Nat Gas Costs ($) |  | * | 6474.16 | 3897.67 | 4973.81 | 7089.77 | 10403.16 | 12397.04 | 9757.84 | 7047.09 | 6044.15 | 6028.34 | 5710.61 |  |  |  | 79823.64 |  | 79823.64 |  |  | MCF=1000CF
|  |  | * | No meter data available. | [15 empty] | 291901.88 |  |  | 1 cubic foot = 1,025 Btu
37 | DOA - NC State Bar HQ | [16 empty] | DOA - NC State Bar HQ
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  |  | 69200 | 82600 | 78200 | 73400 | 81800 | 69800 | 74800 | 76400 | 65400 | 62600 | 75400 | 72000 | 881600 | kwhs | 3008.9008 | MMbtu
| Water Usage (CCF) |  |  |  |  | 20 | 21 | 17 | 13 | 20 | 19 | 18 | 19 | 16 | 27 | 23 | 22 | 235 | CCF | 175780 | gallons
| Elecricity Cost ($) |  |  |  |  | 5997.1 | 7048.17 | 6695.62 | 6475.23 | 7165.66 | 6044.77 | 6288.27 | 6432.95 | 5628.77 | 5526.73 | 6463.28 | 6206.95 | 75973.5 |  | 75973.5
75973.5
38 | FSU - Science and Technology Building | [16 empty] | FSU - Science and Technology Building
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Elecricity Cost ($) | [16 empty] | 0 |  | 0
39 | UNCW - Student Rec Facility Addition | [16 empty] | UNCW - Student Rec Facility Addition
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 196000 | 157000 | 143000 | 211000 | 76000 | 129000 | 132000 | 125000 | 134000 | 146000 | 126000 | 169000 |  |  |  | 1744000 | kwhs | 5952.272 | MMbtu
| Nat Gas (MCF) |  | 22 | 20 | 26 | 35 | 11 | 14 | 26 | 32 | 25 | 34 | 14 | 21 |  |  |  | 280 | MCF | 287.56 | MMbtu
| Heating Hot Water Usage (MMbtu) |  | 328600 | 319000 | 251800 | 339700 | 596800 | 877900 | 10008000 | 593200 | 644700 | 327800 | 293200 | 315801 |  |  |  | 14896501 | MMbtu | 14896.501 | MMbtu
| Chilled water (ton-hrs) |  | 166225 | 167925 | 129275 | 102217 | 47075 | 42608 | 25117 | 20575 | 44867 | 74842 | 112958 | 149900 |  |  |  | 1083584 | ton-hrs | 13003.008 | MMbtu | 34139.341 | MMbtu
| Water Usage (gallons) |  | 25000 | 76000 | 134400 | 193700 | 48500 | 95000 | 69300 | 127800 | 203000 | 38400 | 73600 | 82800 |  |  |  | 1167500 | gallons | 1167500 | gallons
| Elecricity Cost ($) |  | 15680 | 13297.9 | 11425.7 | 15614 | 5358 | 9571.8 | 9332.4 | 9450 | 9728.4 | 10307.6 | 8769.6 | 13739.7 |  |  |  | 132275.1 |  | 132275.1
| Nat Gas Costs ($) |  | 118.58 | 102.8 | 135.46 | 176.05 | 60.06 | 79.8 | 159.64 | 239.36 | 158.25 | 198.9 | 86.1 | 124.74 |  |  |  | 1639.74 |  | 1639.74 |  |  | MCF=1000CF
| Heating Hot Water ($) |  | 1828 | 1544 | 1208 | 2422 | 1567 | 3248 | 2711 | 3327 | 2821 | 1789 | 1578 | 1924 |  |  |  | 25967 |  | 25967
| Chilled Water ($) |  | 16008 | 14362 | 8271 | 7801 | 1814 | 3336 | 2530 | 2243 | 2486 | 5389 | 5703 | 12696 |  |  |  | 82639 |  | 82639
[20 empty] | 242520.84 |  |  | 1 cubic foot = 1,025 Btu
40 | WSSU - Reaves Student Activities Center | [16 empty] | WSSU - Reaves Student Activities Center
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 144457.0593 | 125807.8897 | 113819.1379 | 103014.4603 | 121367.6113 | 106566.6831 | 120479.5556 | 123587.7505 | 138388.6787 | 154373.6812 | 152005.5326 | 164734.3309 |  | 1568602.371 | kwhs | 5353.6399 | MMbtu
| Steam (Nat Gas in therms) |  |  |  | 4849.2352 | 5621.7063 | 8284.6067 | 9198.3225 | 10961.5066 | 9524.727 | 10187.2855 | 7054.9861 | 4238.3414 | 4485.9155 | 4407.3351 | 4609.7442 |  | 83423.7123 | therms | 8340.3794 | MMbtu
| Nat Gas (Therms) |  |  |  | 307 | 340 | 412 | 2094 | 1802 | 1176 | 903 | 1012 | 881 | 324 | 283 | 678 |  | 10212 | therms | 1020.9562 | MMbtu | 14714.9755 | Mmbtu
| Water (gallons) |  |  |  | 24850.221 | 91479.0345 | 66987.8775 | 22404.0975 | 93760.587 | 93184.5885 | 62185.3965 | 95832.6855 | 22493.8635 | 21850.5405 | 9747.0915 | 74617.9875 |  | 679393.971 | gallons | 679393.971 | gallons
| Elecricity Cost ($) |  |  |  | 10554.2845 | 7913.7332 | 7299.0547 | 6490.4562 | 7579.7297 | 7021.3441 | 7629.1442 | 7864.7182 | 9521.0548 | 11935.943 | 11603.9277 | 12774.3448 |  | 108187.735 |  | 108187.735
| Steam Costs ($ Natural Gas) |  |  |  | 2460.0488 | 2782.3234 | 4471.4077 | 5180.1537 | 6460.6775 | 6728.5291 | 6080.235 | 4188.1283 | 2661.0513 | 2609.6057 | 2469.0235 | 2305.1888 |  | 48396.3727 |  | 48396.3727
| Nat Gas Costs ($) |  |  |  | 290.5169 | 321.7451 | 389.8793 | 1958.65 | 1710.31 | 1089.45 | 765.71 | 854.38 | 807.61 | 319.6 | 282.14 | 601.01 |  | 9391.0012 |  | 9391.0012
165975.109
41 | UNCC - Belk Residence Hall | [16 empty] | UNCC - Belk Residence Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 163324 | 175940 | 215472 | 177599 | 155770 | 138580 | 148199 | 131000 | 153381 | 161007 | 160801 | 37260 |  |  |  | 1818333 | kwhs | 6205.9705 | MMbtu
| Nat Gas (Therms) |  | 2134 | 2912 | 3806 | 3609 | 4632 | 5855 | 6585 | 5964 | 5972 | 3972 | 1376 | 268 |  |  |  | 47085 | therms | 4707.3758 | MMbtu | 10913.3464 | Mmbtu
| Water (CF) |  | 14673.7968 | 64347.5936 | 97355.615 | 40498.6631 | 42875.6684 | 54553.4759 | 59014.7059 | 62072.1925 | 74533.4225 | 62820.8556 | 21835.5615 | 6530.7487 |  |  |  | 601112.2995 | CF | 4496320 | gallons
| Elecricity Cost ($) |  | 10914.9671 | 11676.0378 | 14552.2661 | 10762.5167 | 8944.2066 | 8089.144 | 8492.5478 | 7637.8066 | 9087.397 | 9153.1177 | 9283.0281 | 2416.7619 |  |  |  | 111009.7975 |  | 111009.7975
| Nat Gas Costs ($) |  | 1942.16 | 2641.33 | 3444.74 | 3267.71 | 4321.62 | 5413.39 | 6168.68 | 5504.48 | 5110.77 | 3259.05 | 1219.61 | 262.65 |  |  |  | 42556.19 |  | 42556.19
153565.9875
42 | NCSU - Cherry Building Renovation | [16 empty] | NCSU - Cherry Building Renovation
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 12120 | 13440 | 20280 | 24960 | 26520 | 26160 | 15240 | 15120 | 14280 | 11280 | 14219.29 | 13560 |  | 207179.29 | kwhs | 707.1029 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 707.1029 | Mmbtu
| Water (CCF) |  |  |  | 2 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 11 | CCF | 8228 | gallons
| Elecricity Cost ($) |  |  |  | 945.06 | 1123.35 | 1527.15 | 1714.14 | 1839.47 | 1873.1 | 1184.81 | 1193.87 | 1052.54 | 1080.61 | 736.23 | 1071.77 |  | 15342.1 |  | 15342.1
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
15342.1
43 | UNCC - Hunt Residence Hall | [16 empty] | UNCC - Hunt Residence Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  | 62719 | 135317 | 83282 | 75172 | 106109 | 86868 | 82705 | 91894 | 91196 | 96122 | 77072 | 63855 |  |  |  | 1052311 | kwhs | 3591.5374 | MMbtu
| Elec (KWhs) RUP |  | 68260 | 100193 | 42411 | 47279 | 32134 | 34367 | 30431 | 29943 | 32510 | 41846 | 60551 | 81591 |  |  |  | 601516 | kwhs | 2052.9741 | MMbtu
| Nat Gas (Therms) |  | 100 | 281 | 690 | 675 | 783 | 617 | 821 | 1211 | 907 | 1007 | 613 | 125 |  |  |  | 7830 | therms | 782.8131 | MMbtu
| Nat Gas RUP |  | 4395 | 2624 | 3702 | 3797 | 5182 | 6851 | 8615 | 7688 | 6823 | 5657 | 5944 | 7918 |  |  |  | 69196 | therms | 6917.9479 | MMbtu | 13345.2725 | Mmbtu
| Water (CF) |  | 1999 | 25635 | 50734 | 35367 | 39687 | 16640 | 38589 | 35870 | 30818 | 26888 | 22548 | 2485 |  |  |  | 327260 | CF | 2447904.8 | gallons
| Water RUP |  | 11841 | 11101 | 19915 | 3684 | 6915 | 1799 | 1980 | 2209 | 2775 | 11714 | 17125 | 24294 |  |  |  | 115352 | CF | 862832.96 | gallons | 3310737.76 | gallons
| Elecricity Cost ($) |  | 4191.52 | 8980.1433 | 5624.5908 | 4555.4305 | 6092.706 | 5070.6289 | 4739.4123 | 5357.7756 | 5403.109 | 5464.4579 | 4449.36 | 4141.7696 |  |  |  | 64070.904 |  | 64070.904
| Elec RUP |  | 4561.8259 | 6649.183 | 2864.2987 | 2865.112 | 1845.1123 | 2006.0587 | 1743.8493 | 1745.7927 | 1926.1269 | 2378.9112 | 3495.6041 | 5292.1638 |  |  |  | 37374.0386 |  | 37374.0386
| Nat Gas Costs ($) |  | 113.07 | 276.93 | 644.48 | 631.01 | 750.81 | 592.3 | 790.46 | 1137.14 | 796.9 | 844.47 | 556.86 | 134 |  |  |  | 7268.43 |  | 7268.43
| Nat Gas RUP |  | 3974.06 | 2382.51 | 3351.28 | 3436.65 | 4831.87 | 6330.11 | 8062.81 | 7088.6 | 5835.57 | 4631.26 | 5187.41 | 7063.42 |  |  |  | 62175.55 |  | 62175.55
108713.3726
44 | NCSU - Wolf Ridge 6 | [16 empty] | NCSU - Wolf Ridge 6
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 42479.1701 | 41397.0032 | 37326.004 | 34498.9929 | 36833.0078 | 38876.0071 | 38966.98 | 38203.0029 | 36464.0198 | 37791 | 37184 | 38392 |  | 458411.1878 | kwhs | 1564.5574 | MMbtu
| Steam (lbs) |  |  |  | 69.8354 | 102.9491 | 203.1206 | 277.7183 | 376.1128 | 265.0368 | 261.3553 | 91.1047 | 47.6145 | 43.78 | 50.9 | 25.23 |  | 1814.7573 | lbs | 1.8148 | MMbtu
| Chilled Water (Dtherms) |  |  |  | 235.0539 | 103.2827 | 74.8926 | 8.2824 | 14 | 18 | 26 | 84 | 161 | 305 | 332 | 286 |  | 1647.5115 | dtherms | 19.7701 | MMbtu | 1586.1423 | Mmbtu
| Water (CCF) |  |  |  | 187 | 159 | 125 | 178 | 116 | 125 | 79 | 88 | 53 | 68 | 54 | 62 |  | 1294 | CCF | 967912 | gallons
| Electricity Cost ($) |  |  |  | 3695.6878 | 3601.5393 | 3247.3624 | 3001.4124 | 3204.4717 | 3382.2126 | 3390.1273 | 3323.6613 | 3172.3697 | 3287.817 | 3235.008 | 3340.104 |  | 39881.7733 |  | 39881.7733
| Steam Costs ($) |  |  |  | NA | NA | NA | NA | 5423.5465 | 3821.8309 | 3768.743 | 1313.7296 | NA | 631.3076 | 705.983 | 349.9401 |  | 16015.0807 |  | 16015.0807
| Chilled Water ($) |  |  |  | 3222.5889 | 1416.006 | 1026.7769 | 113.5511 | 191.94 | 246.78 | 356.46 | 1151.64 | 2207.31 | 4181.55 | 4780.8 | 4118.4 |  | 19791.214 |  | 19791.214
75688.0681
45 | NCSU - Wolf Ridge 1 | [16 empty] | NCSU - Wolf Ridge 1
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 151838.6459 | 151949.9969 | 135144.989 | 130012.9547 | 137597.1069 | 144941.0095 | 144964.9353 | 139818.0542 | 135489.9902 | 131695.9229 | 131431.0303 | 136429.0771 |  | 1671313.713 | kwhs | 5704.1937 | MMbtu
| Steam (lbs) |  |  |  | 146.6543 | 216.1931 | 426.5532 | 583.2083 | 1383.7269 | 1169.2073 | 639.135 | 321.8167 | 211.4602 | 157 | 169 | 175 |  | 5598.955 | lbs | 5.599 | MMbtu
| Chilled water (Dtherms) |  |  |  | 650.1258 | 416.5971 | 263.3448 | 122 | 96 | 102 | 157 | 341 | 668 | 978 | 1035 | 976 |  | 5805.0677 | dtherms | 69.6608 | MMbtu | 5779.4535 | Mmbtu
| Water (CCF) |  |  |  | 190 | 215 | 255 | 170 | 185 | 255 | 195 | 215 | 90 | 110 | 105 | 190 |  | 2175 | CCF | 1626900 | gallons
| Electricity Cost ($) |  |  |  | 13209.9622 | 13219.6497 | 11757.614 | 11311.1271 | 11970.9483 | 12609.8678 | 12611.9494 | 12164.1707 | 11787.6292 | 11457.5453 | 11434.4996 | 11869.3297 |  | 145404.293 |  | 145404.293
| Steam Costs ($) |  |  |  | 2114.7549 | 3117.5045 | 6150.8967 | 8409.8644 | 19953.3414 | 16859.9695 | 9216.3266 | 4640.5971 | 3049.2559 | 2263.94 | 2344.03 | 2427.25 |  | 78432.9761 |  | 78432.9761
| Chilled Water ($) |  |  |  | 8913.2248 | 5711.5456 | 3610.4575 | 1672.62 | 1316.16 | 1398.42 | 2152.47 | 4675.11 | 9158.28 | 13408.38 | 14904 | 14054.4 |  | 72061.8431 |  | 72061.8431
295899.1122
46 | UNCG - Spartan Village 1 | [16 empty] | UNCG - Spartan Village 1
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 18000 | 86700 | 102600 | 109500 | 1113400 | 84000 | 70500 | 64333 | 47264 | 43754 | 44155 | 51376 |  | 1835582 | kwhs | 6264.8414 | MMbtu
| Nat Gas (Therms) |  |  |  | 564 | 531 | 642 | 616 | 421 | 865 | 660 | 711 | 665 | 98 | 109 | 122 |  | 6004 | therms | 600.2567 | MMbtu | 6865.098 | Mmbtu
| Water (gallons) |  |  |  | 175032 | 228888 | 210188 | 229636 | 73304 | 187748 | 222156 | 201960 | 246840 | 12716 | 1496 | 33660 |  | 1823624 | gallons | 1823624 | gallons
| Elecricity Cost ($) |  |  |  | 1741.78 | 6531.34 | 7798.48 | 8591.68 | 8739.82 | 6881.85 | 6905.76 | 5660.98 | 4615.49 | 4401.47 | 4446.56 | 4890.97 |  | 71206.18 |  | 71206.18
| Nat Gas Costs ($) |  |  |  | 531.25 | 501.6 | 626.82 | 590.24 | 415.76 | 1245.33 | 188.72 | 607.86 | 584.78 | 110.3 | 123.14 | 135.02 |  | 5660.82 |  | 5660.82
76867
47 | UNCG - Spartan Village 3 | [16 empty] | UNCG - Spartan Village 3
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 92700 | 61800 | 42300 | 61500 | 78900 | 63600 | 50100 | 39000 | 27035 | 26613 | 27287 | 32916 |  | 603751 | kwhs | 2060.6022 | MMbtu
| Nat Gas (Therms) |  |  |  | 312 | 299 | 375 | 331 | 259 | 482 | 329 | 364 | 318 | 378 | 346 | 195 |  | 3988 | therms | 398.7048 | MMbtu | 2459.3069 | Mmbtu
| Water (gallons) |  |  |  | 139128 | 178772 | 166056 | 158576 | 37400 | 155584 | 168300 | 142120 | 143616 | 748 | 1496 | 14212 |  | 1306008 | gallons | 1306008 | gallons
| Elecricity Cost ($) |  |  |  | 6668.52 | 4453.19 | 3480.48 | 4810.01 | 6102.75 | 5018.61 | 4548.76 | 3405.03 | 2672.6 | 2646.87 | 2700.47 | 3046.58 |  | 49553.87 |  | 49553.87
| Nat Gas Costs ($) |  |  |  | 304.79 | 293.11 | 376.29 | 328.45 | 265.16 | 472.82 | 312.15 | 325.25 | 292.37 | 360.44 | 339.7 | 201.73 |  | 3872.26 |  | 3872.26
53426.13
48 | UNCG - Spartan Village 4 | [16 empty] | UNCG - Spartan Village 4
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  |  | 4380 | 46500 | 54900 | 68700 | 57300 | 48000 | 46395 | 34365 | 29364 | 31741 | 39247 |  | 460892 | kwhs | 1573.0244 | MMbtu
| Nat Gas (Therms) |  |  |  | 475 | 461 | 554 | 531 | 373 | 812 | 494 | 617 | 546 | 88 | 126 | 119 |  | 5196 | therms | 519.4759 | MMbtu | 2092.5003 | Mmbtu
| Water (gallons) |  |  |  | 139128 | 178772 | 166056 | 158576 | 37400 | 155584 | 168300 | 142120 | 143616 | 748 | 1496 | 14212 |  | 1306008 | gallons | 1306008 | gallons
| Elecricity Cost ($) |  |  |  |  | 4056.36 | 4231.61 | 4800.03 | 5553.53 | 4831.13 | 4896.78 | 4151.6 | 3414.67 | 3080.44 | 3260.39 | 3731.22 |  | 46007.76 |  | 46007.76
| Nat Gas Costs ($) |  |  |  | 451.27 | 438.69 | 544.25 | 512.17 | 371.14 | 779.07 | 456.45 | 533.64 | 484.5 | 101.29 | 138.67 | 132.27 |  | 4943.41 |  | 4943.41
50951.17
49 | WSSU - Martin-Schexnider Residence Hall | [16 empty] | WSSU - Martin-Schexnider Residence Hall
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) |  |  |  | 83895.2233 | 73064.4875 | 66101.8716 | 59826.9215 | 70485.7408 | 61889.9188 | 69969.9915 | 71775.1142 | 80370.9362 | 89654.424 | 88279.0925 | 95671.4995 |  | 910985.2214 | kwhs | 3109.1926 | MMbtu
| Nat Gas (Therms) |  |  |  | 2816.2533 | 3264.8755 | 4811.3878 | 5342.0395 | 6366.0305 | 5531.603 | 5916.392 | 4097.2704 | 2461.4692 | 2605.2509 | 2559.6144 | 2677.1659 |  | 48449.3524 | therms | 4843.7785 | MMbtu | 7952.971 | Mmbtu
| Water (gallons) |  |  |  | 16838.6055 | 7278.5265 | 3523.3155 | 2842.59 | 156132.996 | 178754.028 | 118296.627 | 210561.114 | 17145.306 | 161758.332 | 193146.51 | 309356.0775 |  | 1375634.028 | gallons | 1375634.028 | gallons
| Elecricity Cost ($) |  |  |  | 6129.5312 | 4595.9984 | 4239.0163 | 3769.4127 | 4402.0217 | 4077.7324 | 4430.7198 | 4567.5324 | 5529.4703 | 6931.9464 | 6739.1245 | 7418.8587 |  | 62831.3647 |  | 62831.3647
| Nat Gas Costs ($) |  |  |  | 1428.7038 | 1615.8687 | 2596.8253 | 3008.4383 | 3752.1183 | 3907.6765 | 3531.1717 | 2432.3073 | 1545.4384 | 1515.5608 | 1433.9159 | 1338.7669 |  | 28106.7918 |  | 28106.7918
62831.3647
50 | Cape Fear Community College - Union Station | [16 empty] | Cape Fear Community College - Union Station
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [16 empty] | 0 | kwhs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu
| Water (CF) | [16 empty] | 0 | CF | 0 | gallons
| Elecricity Cost ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
0
51 | ECU - Smith-Williams Center | [16 empty] | ECU - Smith-Williams Center
| Utility | Jun-13 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-14 | Total | Units | Total | Units
| Electricity (KWhs) | [6 empty] | 49565 | 35870 | 26238 | 36303 | 32906 | 35271 | 33773 | 44401 | 25329 |  | 319656 | kwhs | 1090.9859 | MMbtu
| Steam (lbs) | [16 empty] | 0 | lbs | 0 | MMbtu
| Nat Gas (Therms) | [16 empty] | 0 | therms | 0 | MMbtu | 1090.9859 | MMbtu
| Water (gallons) | [16 empty] | 0 | gallons | 0 | gallons
| Elecricity Cost ($) | [6 empty] | 4659.11 | 3371.78 | 2466.372 | 3412.482 | 3093.164 | 3315.474 | 3174.662 | 4173.694 | 2380.926 |  | 30047.664 |  | 30047.664
| Steam Costs ($) | [16 empty] | 0 |  | 0
| Nat Gas Costs ($) | [16 empty] | 0 |  | 0
30047.664

## 13.14 Raw Meter
1 | ASU - Cone Residence Hall Renovation
App State - Plemmons, Cone, Summit Utility Data
ELECTRICITY
Bldg. # | Building Name | time axis 2010-07-01 to 2014-07-01
204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 227800 | 214280 | 225000 | 221480 | 190120 | 186400 | 149800 | 169880 | 176080 | 194280 | 202520 | 204080 | 185200 | 182360 | 221240 | 184480 | 192240 | 159400 | 93960 | 150160 | 161304.8 | 184936.24 | 200038.48 | 212508.96 | 164809.92 | 171163.76 | 191234.64 | 181865.2 | 160043.52 | 158691.04 | 162637.92 | 156600.48 | 163100.8 | 182870.4 | 170412.48 | 195797.84 | 172848.4 | 181802.96 | 239736.72 | 193410.72 | 167832.32 | 158616.24 | 151638.48 | 173009.88 | 145604.08 | 167482.6 | 163268.2 | 150024.64 | 154229.68
315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 30920 | 42883 | 87000 | 89330 | 74095 | 65520 | 51680 | 65760 | 67200 | 67922 | 67325 | 54118 | 61002 | 47297 | 97209 | 82790 | 74640 | 78640 | 59040 | 75280 | 68445.6 | 81539.28 | 78760.56 | 70425.12 | 83354.24 | 95440.72 | 106644.08 | 90944.4 | 79893.44 | 75534.88 | 61110.24 | 77534.56 | 66657.6 | 76348.8 | 74618.56 | 100114.48 | 92674.8 | 96643.12 | 114833.84 | 95351.84 | 74287.04 | 71859.28 | 63800.56 | 84077.36 | 66297.76 | 75581.2 | 80548.4 | 73478.08 | 82502.96
452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2649.6 | 3444.48 | 4680.96 | 12305.92 | 75868.84 | 94233.52 | 103495.28 | 93234.4 | 90349.04 | 82741.08 | 67491.84 | 96344.96 | 85841.6 | 96620.8 | 94928.96 | 110927.68 | 86316.8 | 107513.92 | 140709.44 | 116877.44 | 96720.64 | 88444.48 | 70200.96 | 106069.76 | 76516.16 | 90139.2 | 97414.4 | 90465.28 | 92359.36
204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 15780.47 | 14844.63 | 15586.66 | 15343 | 13172.29 | 12914.8 | 11564.69 | 14007.85 | 14518.63 | 16018.03 | 16696.88 | 16825.4 | 15269.98 | 15036 | 18239.12 | 15210.66 | 15849.97 | 13144.46 | 7847.46 | 13989.73 | 14719.5 | 17232.4816 | 18638.2484 | 19799.0325 | 15359.0554 | 15950.5038 | 17818.7533 | 16946.6228 | 14915.3845 | 14789.4924 | 12597.1118 | 14489.8107 | 15087.0346 | 16885.8919 | 15705.2025 | 17941.6669 | 15826.806 | 16105.9043 | 21296.4452 | 17214.78 | 14999.8414 | 14213.2466 | 14023.0962 | 15671.5612 | 12939.7978 | 14853.0983 | 14424.6939 | 13218.7814 | 13631.797
315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 2171.15 | 3005.4 | 6059.14 | 6220.42 | 5153.51 | 4559.95 | 4010.19 | 5442.32 | 5560.96 | 5620.45 | 5571.26 | 4483.21 | 5050.33 | 3921.26 | 8033.24 | 6845.34 | 6173.9 | 6503.44 | 4947.92 | 7032.02 | 6267.55 | 7604.4363 | 7345.7837 | 6569.8954 | 7773.3804 | 8898.4197 | 9941.2685 | 8479.8905 | 7451.2315 | 7045.5273 | 4741.0025 | 7186.1608 | 6173.8085 | 7059.0927 | 6888.4709 | 9205.3588 | 8520.2409 | 8598.2021 | 10227.8989 | 8508.3279 | 6649.7124 | 6446.9613 | 5908.2048 | 7624.8998 | 5899.6245 | 6712.9535 | 7134.1322 | 6494.8624 | 7323.4779
452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07 | 392.9622 | 890.9878 | 1979.8021 | 7087.7942 | 8797.3266 | 9659.2982 | 8704.2166 | 8435.684 | 7727.5203 | 5244.5257 | 8933.1385 | 7953.5968 | 8926.5754 | 8747.6766 | 10137.8643 | 7867.493 | 9500.1636 | 12473.9959 | 10394.3221 | 8649.9062 | 7939.7522 | 6503.649 | 9620.539 | 6814.5477 | 8000.3182 | 8603.7338 | 7962.9562 | 8147.895
STEAM
Bldg. # | Building Name | time axis 2010-07-01 to 2014-07-01
204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 519706.6 | 395410.8 | 316161.8 | 308654 | 493012.2 | 947651.2 | 982687.6 | 474659.8 | 401250.2 | 322001.2 | 351198.2 | 274451.8 | 37539 | 404587 | 459644.2 | 527214.4 | 569758.6 | 608966 | 654847 | 620644.8 | 524711.8 | 1393948.2 | 601458.2 | 583105.8 | 642334 | 733261.8 | 677370.4 | 742438 | 886754.6 | 978516.6 | 1117828 | 953490.6 | 797495.2 | 533888 | 681541.4 | 413763.2 | 726588.2 | 731593.4 | 461312.6 | 842542 | 674867.8 | 809174 | 1115325.4 | 682375.6 | 902604.4 | 724919.8 | 504691 | 397913.4 | 470488.8
315 | Cone Residence Hall Steam Use in Lbs. | 41710 | 62565 | 100104 | 153492.8 | 163503.2 | 216892 | 296141 | 200208 | 166840 | 135140.4 | 94264.6 | 101772.4 | 79249 | 165171.6 | 141814 | 164337.4 | 206881.6 | 207048.44 | 208216.32 | 242752.2 | 211052.6 | 160166.4 | 82585.8 | 59228.2 | 65901.8 | 85922.6 | 171011 | 170176.8 | 208550 | 219394.6 | 291970 | 254848.1 | 229405 | 171011 | 145985 | 52554.6 | 59228.2 | 95933 | 132637.8 | 192700.2 | 214389.4 | 207715.8 | 381229.4 | 204379 | 255265.2 | 206881.6 | 81751.6 | 45881 | 58394
452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210652.184 | 60696.392 | 83545.13 | 170660.636 | 189229.928 | 343473.508 | 382747.644 | 356320.188 | 498426.158 | 606463.4 | 623147.4 | 367048 | 385400.4 | 272783.4 | 340353.6 | 437120.8 | 359540.2 | 462981 | 530551.2 | 387068.8 | 846713 | 451302.2 | 542230 | 358706 | 216892 | 246923.2 | 286964.8
204 & 445 | Plemmons Student Union Total Steam Cost | 22867.09 | 17398.08 | 13911.12 | 13580.78 | 21692.54 | 41696.65 | 43238.25 | 20885.04 | 17655.01 | 14168.05 | 15452.72 | 5764.08 | 788.4 | 8497.2 | 9653.52 | 11072.64 | 11966.16 | 12789.6 | 13753.2 | 13034.88 | 11020.08 | 29275.92 | 12631.92 | 12246.48 | 13490.4 | 15400.08 | 14226.24 | 15592.8 | 18623.76 | 20550.96 | 23476.8 | 20025.36 | 16749.12 | 11212.8 | 14313.84 | 8689.92 | 15259.92 | 15365.04 | 9688.56 | 17695.2 | 14173.68 | 16994.4 | 23424.24 | 14331.36 | 18956.64 | 15224.88 | 10599.6 | 8357.04 | 9881.28
315 | Cone Residence Hall Steam Costs | 1835.24 | 2752.86 | 4404.58 | 6753.68 | 7194.14 | 9543.25 | 13030.2 | 8809.15 | 7340.96 | 5946.18 | 4147.64 | 2137.44 | 1664.4 | 3468.96 | 2978.4 | 3451.44 | 4344.96 | 4348.46 | 4372.99 | 5098.32 | 4432.56 | 3363.84 | 1734.48 | 1243.92 | 1384.08 | 1804.56 | 3591.6 | 3574.08 | 4380 | 4607.76 | 6132 | 5352.36 | 4818 | 3591.6 | 3066 | 1103.76 | 1243.92 | 2014.8 | 2785.68 | 4047.12 | 4502.64 | 4362.48 | 8006.64 | 4292.4 | 5361.12 | 4344.96 | 1716.96 | 963.6 | 1226.4
452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4424.15 | 1274.76 | 1754.66 | 3584.31 | 3974.24 | 7213.61 | 8038.46 | 7483.56 | 10467.99 | 14829.71 | 15237.68 | 8975.34 | 9424.1 | 6670.31 | 8322.59 | 10688.82 | 8791.75 | 11321.17 | 12973.44 | 9464.91 | 19687.45 | 11035.59 | 13259.03 | 8771.36 | 5303.61 | 6037.95 | 7017.09
WATER & SEWER
Bldg. # | Building Name | time axis 2010-07-01 to 2014-07-01
204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 227000 | 183000 | 225000 | 344000 | 215000 | 164000 | 101000 | 391000 | 303000 | 172000 | 150000 | 200400 | 209000 | 258000 | 385000 | 387000 | 287000 | 151000 | 196000 | 287000 | 294000 | 310000 | 145000 | 210000 | 278000 | 501000 | 459000 | 439000 | 368000 | 227000 | 500000 | 275000 | 181000 | 279000 | 200000 | 219000 | 244000 | 333000 | 427000 | 475900 | 456359 | 390001 | 507000 | 540918 | 183918 | 228589 | 211785 | 332555.459 | 156555
315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 20000 | 83000 | 139000 | 174000 | 119000 | 108000 | 53000 | 231000 | 190000 | 54000 | 27000 | 6000 | 12000 | 81000 | 174000 | 147000 | 146000 | 93000 | 112000 | 196000 | 164000 | 158000 | 65000 | 18000 | 27000 | 114000 | 166000 | 176000 | 172000 | 77000 | 129000 | 170000 | 133000 | 167000 | 113000 | 86000 | 150000 | 128000 | 190000 | 224300 | 173473 | 80000 | 185000 | 190346 | 140346 | 186283 | 77895 | 33085.173 | 78085
452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5992 | 32528 | 100152 | 205440 | 208008 | 197736 | 89880 | 160072 | 212288 | 172056 | 219136 | 77896 | 11128 | 11128 | 139528 | 218280 | 274768 | 222064 | 95872 | 182328 | 224152 | 172792 | 245264 | 117648 | 78184.368 | 95304
204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 2093.02 | 1370.77 | 1567.19 | 2355.2 | 1751.58 | 1112.4 | 702.32 | 2027.61 | 1806.48 | 1939.76 | 1447.95 | 1348.36 | 1842.05 | 1678.25 | 2296 | 3225.7 | 3158.8 | 2030.4 | 1351.5 | 1658.65 | 2290.3 | 3059.25 | 2194.5 | 2112 | 1325.3 | 2441.1 | 4465.2 | 3722.6 | 3126.7 | 2551.7 | 2913.5 | 2847 | 2453.7 | 2472.6 | 3117.5 | 2551.5 | 3401.1 | 3105.9 | 3993.7 | 4651.87 | 5036.2027 | 5584.5 | 5330.1 | 6721.467 | 3878.967 | 2495.034 | 2707.638 | 4023.6185 | 2575.653
315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 91.64 | 273.77 | 1081.38 | 1295.16 | 1062.99 | 859.46 | 529.02 | 1387.37 | 1148.25 | 1097.17 | 662.24 | 199.4 | 114.9 | 301.5 | 861.15 | 1559.7 | 1444.65 | 1232.2 | 1012.75 | 1203.2 | 1681.8 | 1794.6 | 1224.5 | 535.15 | 221.45 | 602.15 | 1095.55 | 1536.15 | 1584.55 | 1415.95 | 969.05 | 1568.75 | 1608.35 | 1646.05 | 1822.75 | 1223.75 | 1805.75 | 1544.15 | 1671.75 | 2134.24 | 2191.1569 | 1597.75 | 1582.75 | 2376.999 | 2081.999 | 1987.448 | 1603.436 | 599.4195 | 440.441
452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.74 | 100.84 | 2320.58 | 6556.74 | 603.22 | 573.43 | 413.45 | 592.27 | 955.3 | 722.64 | 1604.7 | 1894.11 | 568.17 | 194.27 | 770.52 | 1875.28 | 2525.21 | 2638.7704 | 1900.79 | 1666.76 | 2584.974 | 2497.664 | 2537.948 | 2148.846 | 1009.822 | 633.346
2 | UNCC - Prospector Hall Renovation Phase II | bar: 2011-11-01 to 2011-12-01; 2012-03-01; 2012-06-01
Prospector Hall Renovation |  | 2010-08-01: 06-07223-01A
|  |  | Jul 13 | Aug 13 | Sep 13 | Oct 13 | Nov 13 | Dec 13 | Jan 14 | Feb 14 | Mar 14 | Apr 14 | May 14 | Jun 14
Consumption
Electric (KWH) |  | 2010-08-01: 63690; 2010-09-01: 96100; 2010-10-01: 52663; 2010-11-01: 52331; 2010-12-01: 33231; 2011-01-01: 38321; 2011-02-01: 43278; 2011-03-01: 49566; 2011-04-01: 62030; 2011-05-01: 69156; 2011-06-01: 80988; 2011-07-01: 46669
Nat Gas (Therms) |  | 2010-08-01: 1239; 2010-09-01: 1174; 2010-10-01: 2619; 2010-11-01: 2610; 2010-12-01: 3129; 2011-01-01: 3244; 2011-02-01: 4291; 2011-03-01: 4676; 2011-04-01: 3776; 2011-05-01: 3140; 2011-06-01: 1973; 2011-07-01: 1643
Water (CF) |  | 2010-08-01: 7650; 2010-09-01: 51000; 2010-10-01: 19210; 2010-11-01: 18520; 2010-12-01: 14660; 2011-01-01: 14145; 2011-02-01: 15295; 2011-03-01: 15220; 2011-04-01: 14250; 2011-05-01: 14880; 2011-06-01: 7480; 2011-07-01: 12940
Costs $
Electric |  | 2010-08-01: 4256.4121; 2010-09-01: 6377.5562; 2010-10-01: 3556.6848; 2010-11-01: 3171.2637; 2010-12-01: 1908.1012; 2011-01-01: 2236.8602; 2011-02-01: 2480.047; 2011-03-01: 2889.8895; 2011-04-01: 3675.1047; 2011-05-01: 3931.4626; 2011-06-01: 4675.4304; 2011-07-01: 3027.0495
Nat Gas |  | 2010-08-01: 1127.6177; 2010-09-01: 1064.8769; 2010-10-01: 2370.4083; 2010-11-01: 2363.1818; 2010-12-01: 2919.3327; 2011-01-01: 2999.3232; 2011-02-01: 4019.7124; 2011-03-01: 4315.7191; 2011-04-01: 3231.4581; 2011-05-01: 2576.389; 2011-06-01: 1748.7577; 2011-07-01: 1610.2013
Water |  | 2010-08-01: 655.2138; 2010-09-01: 3873.6273; 2010-10-01: 1427.3188; 2010-11-01: 1443.0697; 2010-12-01: 1161.1631; 2011-01-01: 1229.1503; 2011-02-01: 1053.8383; 2011-03-01: 1262.4953; 2011-04-01: 983.0615; 2011-05-01: 1081.669; 2011-06-01: 556.5457; 2011-07-01: 982.2983
Metered data is whole building data - not just the partial renovation
Metered data includes process loads
Chill water to building not metered
3 | UNCC - Miltimore Residence Hall | bar: 2011-11-01 to 2011-12-01; 2012-03-01
Miltimore Residence Hall |  | 2010-08-01: 05-06656-01A
|  |  | Jul 13 | Aug 13 | Sep 13 | Oct 13 | Nov 13 | Dec 13 | Jan 14 | Feb 14 | Mar 14 | Apr 14 | May 14 | Jun 14
Consumption
Electric (KWH) |  | 2010-08-01: 217457; 2010-09-01: 160490; 2010-10-01: 203429; 2010-11-01: 166251; 2010-12-01: 138132; 2011-01-01: 124889; 2011-02-01: 139000; 2011-03-01: 133870; 2011-04-01: 139130; 2011-05-01: 146224; 2011-06-01: 153776; 2011-07-01: 65996
Nat Gas (Therms) |  | 2010-08-01: 3277; 2010-09-01: 3078; 2010-10-01: 3630; 2010-11-01: 4223; 2010-12-01: 4887; 2011-01-01: 5896; 2011-02-01: 8070; 2011-03-01: 8390; 2011-04-01: 6911; 2011-05-01: 4287; 2011-06-01: 3143; 2011-07-01: 3451
Water (CF) |  | 2010-08-01: 23765; 2010-09-01: 60876; 2010-10-01: 74436; 2010-11-01: 50221; 2010-12-01: 55522; 2011-01-01: 41439; 2011-02-01: 76667; 2011-03-01: 19317; 2011-04-01: 60140; 2011-05-01: 54212; 2011-06-01: 42411; 2011-07-01: 47588
Costs $
Electric |  | 2010-08-01: 14532.6835; 2010-09-01: 10650.7179; 2010-10-01: 13738.9218; 2010-11-01: 10074.8268; 2010-12-01: 7931.4447; 2011-01-01: 7289.9776; 2011-02-01: 7965.3988; 2011-03-01: 7805.1387; 2011-04-01: 8243.065; 2011-05-01: 8312.7161; 2011-06-01: 8877.4755; 2011-07-01: 4280.6393
Nat Gas |  | 2010-08-01: 2982.4078; 2010-09-01: 2791.9003; 2010-10-01: 3285.4457; 2010-11-01: 3823.6463; 2010-12-01: 4559.533; 2011-01-01: 5451.2976; 2011-02-01: 7559.7946; 2011-03-01: 7743.5592; 2011-04-01: 5914.3556; 2011-05-01: 3517.5094; 2011-06-01: 2785.7807; 2011-07-01: 3382.1088
Water |  | 2010-08-01: 2035.4451; 2010-09-01: 4623.7439; 2010-10-01: 5530.6559; 2010-11-01: 3913.1966; 2010-12-01: 4397.6873; 2011-01-01: 3600.902; 2011-02-01: 5282.4206; 2011-03-01: 1602.3404; 2011-04-01: 4148.8645; 2011-05-01: 3940.8227; 2011-06-01: 3155.5693; 2011-07-01: 3612.4891
4 | NCCU - Nursing Building | bar: 2011-11-01 to 2012-03-01
Utility Data for Nursing Building - FY 13-14 |  | 2010-07-01: 2014-07-13; 2010-08-01: 2014-08-13; 2010-09-01: 2014-09-13; 2010-10-01: 2014-10-13; 2010-11-01: 2014-11-13; 2010-12-01: 2014-12-13; 2011-01-01: 2014-01-14; 2011-02-01: 2014-02-14; 2011-03-01: 2014-03-14; 2011-04-01: 2014-04-14; 2011-05-01: 2014-05-14; 2011-06-01: 2014-06-14; 2011-07-01: Totals
Electricity | kWh | 2011-09-01: See note 2 below.
Cost / kWh | bar: 2010-07-01 to 2011-06-01
Total Usage Cost
Natural Gas | Therms | 2010-07-01: 43; 2010-08-01: 41; 2010-09-01: 47; 2010-10-01: 45; 2010-11-01: 51; 2010-12-01: 48; 2011-01-01: 50; 2011-02-01: 44; 2011-03-01: 45; 2011-04-01: 50; 2011-05-01: 44; 2011-06-01: 46; 2011-07-01: 554
| Cost (Paid to Utility) | 2010-07-01: 57.69; 2010-08-01: 55.53; 2010-09-01: 58.99; 2010-10-01: 56.83; 2010-11-01: 62.08; 2010-12-01: 59.46; 2011-01-01: 61.21; 2011-02-01: 55.96; 2011-03-01: 56.8; 2011-04-01: 60.88; 2011-05-01: 55.67; 2011-06-01: 57.4; 2011-07-01: 698.5
Water | CF-Low Flow (CF) | 2010-07-01: 8965; 2010-08-01: 11252; 2010-09-01: 9299; 2010-10-01: 4271; 2010-11-01: 1233; 2010-12-01: 703; 2011-01-01: 989; 2011-02-01: 1108; 2011-03-01: 1034; 2011-04-01: 3253; 2011-05-01: 8040; 2011-06-01: 10286; 2011-07-01: 60433
| CF-High Flow (CF) | 2010-07-01: 41648; 2010-08-01: 21324; 2010-09-01: 5394; 2010-10-01: 3839; 2010-11-01: 1185; 2010-12-01: 1690; 2011-01-01: 974; 2011-02-01: 1091; 2011-03-01: 1080; 2011-04-01: 2624; 2011-05-01: 4466; 2011-06-01: 5246; 2011-07-01: 90561
| Total CF | 2010-07-01: 50613; 2010-08-01: 32576; 2010-09-01: 14693; 2010-10-01: 8110; 2010-11-01: 2418; 2010-12-01: 2393; 2011-01-01: 1963; 2011-02-01: 2199; 2011-03-01: 2114; 2011-04-01: 5877; 2011-05-01: 12506; 2011-06-01: 15532; 2011-07-01: 150994
| Cost (Paid to Utility) | 2010-07-01: 3559.72; 2010-08-01: 2363.87; 2010-09-01: 1178.23; 2010-10-01: 741.78; 2010-11-01: 364.4; 2010-12-01: 362.74; 2011-01-01: 334.22; 2011-02-01: 349.87; 2011-03-01: 344.24; 2011-04-01: 593.73; 2011-05-01: 1033.23; 2011-06-01: 1233.85; 2011-07-01: 12459.88
Note 1: Due to problems with the electrical submeters installed in the Nursing Building (since corrected), usage date for Nursing was not available for FY 13-14.
Note 2: Steam meter was incorrectly installed by contractor, and was repaired in Augst of 2014.
5 | NCCU - Chidley Residence Hall | bar: 2011-11-01 to 2012-03-01
Utility Data for Chidley North - FY 13-14 |  | 2010-07-01: 2014-07-13; 2010-08-01: 2014-08-13; 2010-09-01: 2014-09-13; 2010-10-01: 2014-10-13; 2010-11-01: 2014-11-13; 2010-12-01: 2014-12-13; 2011-01-01: 2014-01-14; 2011-02-01: 2014-02-14; 2011-03-01: 2014-03-14; 2011-04-01: 2014-04-14; 2011-05-01: 2014-05-14; 2011-06-01: 2014-06-14; 2011-07-01: Totals
Electricity | kWh | 2010-07-01: 176060; 2010-08-01: 174415; 2010-09-01: 174280; 2010-10-01: 168764; 2010-11-01: 120336; 2010-12-01: 89358; 2011-01-01: 83521; 2011-02-01: 92352; 2011-03-01: 97382; 2011-04-01: 128712; 2011-05-01: 104508; 2011-06-01: 67634; 2011-07-01: 1477322
| Cost / kWh | 2010-07-01: 0.041924; 2010-08-01: 0.041924; 2010-09-01: 0.041924; 2010-10-01: 0.041924; 2010-11-01: 0.041924; 2010-12-01: 0.041924; 2011-01-01: 0.041924; 2011-02-01: 0.041924; 2011-03-01: 0.041924; 2011-04-01: 0.041924; 2011-05-01: 0.041924; 2011-06-01: 0.041924
| Total Usage Cost | 2010-07-01: 7381.1394; 2010-08-01: 7312.1745; 2010-09-01: 7306.5147; 2010-10-01: 7075.2619; 2010-11-01: 5044.9665; 2010-12-01: 3746.2448; 2011-01-01: 3501.5344; 2011-02-01: 3871.7652; 2011-03-01: 4082.643; 2011-04-01: 5396.1219; 2011-05-01: 4381.3934; 2011-06-01: 2835.4878; 2011-07-01: 61935.2475
Natural Gas | Therms | 2010-07-01: 280; 2010-08-01: 299; 2010-09-01: 34; 2010-10-01: 0; 2010-11-01: 0; 2010-12-01: 0; 2011-01-01: 0; 2011-02-01: 817; 2011-03-01: 1425; 2011-04-01: 1191; 2011-05-01: 1572; 2011-06-01: 215; 2011-07-01: 5833
| Cost (Paid to Utility) | 2010-07-01: 291.38; 2010-08-01: 309.81; 2010-09-01: 50.7; 2010-10-01: 17.5; 2010-11-01: 17.5; 2010-12-01: 17.5; 2011-01-01: 17.5; 2011-02-01: 735.92; 2011-03-01: 1237.4; 2011-04-01: 1044.99; 2011-05-01: 1373.96; 2011-06-01: 213.95; 2011-07-01: 5328.11
Water | CF-Low Flow (CF) | 2010-07-01: 186; 2010-08-01: 516; 2010-09-01: 10743; 2010-10-01: 15307; 2010-11-01: 15381; 2010-12-01: 8038; 2011-01-01: 1784; 2011-02-01: 7544; 2011-03-01: 7656; 2011-04-01: 4777; 2011-05-01: 9592; 2011-06-01: 534; 2011-07-01: 82058
| CF-High Flow (CF) | 2010-07-01: 16261; 2010-08-01: 25844; 2010-09-01: 41597; 2010-10-01: 42213; 2010-11-01: 46683; 2010-12-01: 36490; 2011-01-01: 10400; 2011-02-01: 33564; 2011-03-01: 36734; 2011-04-01: 24134; 2011-05-01: 43241; 2011-06-01: 17670; 2011-07-01: 374831
| Total CF | 2010-07-01: 16447; 2010-08-01: 26360; 2010-09-01: 52340; 2010-10-01: 57520; 2010-11-01: 62064; 2010-12-01: 44528; 2011-01-01: 12184; 2011-02-01: 41108; 2011-03-01: 44390; 2011-04-01: 28911; 2011-05-01: 52833; 2011-06-01: 18204; 2011-07-01: 456889
| Cost (Paid to Utility) | 2010-07-01: 1276; 2010-08-01: 1951.75; 2010-09-01: 3674.22; 2010-10-01: 4017.66; 2010-11-01: 4318.92; 2010-12-01: 3156.29; 2011-01-01: 1011.88; 2011-02-01: 2929.54; 2011-03-01: 3147.14; 2011-04-01: 2120.88; 2011-05-01: 3706.91; 2011-06-01: 1411.01
Note 1: Accurate steam data is still not being captured at Chidley. Meters have been repaired per the manufacturer, but the flow rate is so low at this time that data is not being captured as of 8/26/2014.
6 | UNC-CH - Loudermilk | bar: 2011-11-01; 2012-02-01
Loudermilk Center of Excellence (375)
Energy and Water Usage (Acct. #01012081)
Annual Summary of Performance
id | Period | 2010-07-01: name; 2010-08-01: total btu; 2010-09-01: Electric (Btu); 2010-10-01: ng (Btu); 2010-11-01: steam (Btu); 2010-12-01: chw (Btu); 2011-01-01: mgal water; 2011-02-01: gsf; 2011-03-01: mgal non-potable water; 2011-04-01: Site EUI
Actual Performance | Sept 13 - Aug 14 | 2010-07-01: UNC Chapel Hill; 2010-08-01: 18231239352; 2010-09-01: 6375492600; 2010-10-01: 353500000; 2010-11-01: 8765154000; 2010-12-01: 2737092752; 2011-01-01: 1089; 2011-02-01: 195165; 2011-03-01: 0; 2011-04-01: 93414.4921
Modeled Performance | NA | 2010-07-01: UNC Chapel Hill; 2010-08-01: 7001059000; 2010-09-01: 3177664000; 2010-10-01: 99432000; 2010-11-01: 1747534000; 2010-12-01: 1976429000; 2011-01-01: NA; 2011-02-01: 170000; 2011-03-01: NA; 2011-04-01: 41182.7
Monthly Detail of Performance
UTILITY | 2013-09-01 | 2010-07-01: 2013-10-01; 2010-08-01: 2013-11-01; 2010-09-01: 2013-12-01; 2010-10-01: 2014-01-01; 2010-11-01: 2014-02-01; 2010-12-01: 2014-03-01; 2011-01-01: 2014-04-01; 2011-02-01: 2014-05-01; 2011-03-01: 2014-06-01; 2011-04-01: 2014-07-01; 2011-05-01: 2014-08-01
Consumption:
ELECTRIC (kWhs) | 142751 | 2010-07-01: 191399; 2010-08-01: 157749; 2010-09-01: 168745; 2010-10-01: 149433; 2010-11-01: 140210; 2010-12-01: 148789; 2011-01-01: 168547; 2011-02-01: 150998; 2011-03-01: 145846; 2011-04-01: 158623; 2011-05-01: 145460
STEAM (MLBS) | 726 | 2010-07-01: 476; 2010-08-01: 435; 2010-09-01: 605; 2010-10-01: 850; 2010-11-01: 760; 2010-12-01: 702; 2011-01-01: 656; 2011-02-01: 359; 2011-03-01: 458; 2011-04-01: 580; 2011-05-01: 734
CHILLED WATER (Ton-Hrs.) | 167254 | 2010-07-01: 113689; 2010-08-01: 57995; 2010-09-01: 11238; 2010-10-01: 14795; 2010-11-01: 1337; 2010-12-01: 2008; 2011-01-01: 2309; 2011-02-01: 18183; 2011-03-01: 91876; 2011-04-01: 155036; 2011-05-01: 166476; 2011-06-01: 802196
NATURAL GAS (Therms) | 151 | 2010-07-01: 316; 2010-08-01: 335; 2010-09-01: 385; 2010-10-01: 416; 2010-11-01: 305; 2010-12-01: 372; 2011-01-01: 281; 2011-02-01: 379; 2011-03-01: 289; 2011-04-01: 176; 2011-05-01: 130
WATER (kGal) | 64 | 2010-07-01: 71; 2010-08-01: 108; 2010-09-01: 91; 2010-10-01: 28; 2010-11-01: 67; 2010-12-01: 65; 2011-01-01: 94; 2011-02-01: 122; 2011-03-01: 32; 2011-04-01: 210; 2011-05-01: 137
SEWER (kGal) | 63 | 2010-07-01: 69; 2010-08-01: 108; 2010-09-01: 91; 2010-10-01: 27; 2010-11-01: 67; 2010-12-01: 65; 2011-01-01: 94; 2011-02-01: 121; 2011-03-01: 32; 2011-04-01: 208; 2011-05-01: 132
STORMWATER (ksf) | 121 | 2010-07-01: 121; 2010-08-01: 121; 2010-09-01: 121; 2010-10-01: 121; 2010-11-01: 121; 2010-12-01: 121; 2011-01-01: 121; 2011-02-01: 121; 2011-03-01: 121; 2011-04-01: 121; 2011-05-01: 121
Costs:
ELECTRIC ($) | 9107.51 | 2010-07-01: 11560.5; 2010-08-01: 9480.71; 2010-09-01: 9095.36; 2010-10-01: 8323.42; 2010-11-01: 8454.66; 2010-12-01: 8793.43; 2011-01-01: 8882.43; 2011-02-01: 8923.98; 2011-03-01: 8459.07; 2011-04-01: 9850.49; 2011-05-01: 9833.1
STEAM ($) | 8154.58 | 2010-07-01: 5346.53; 2010-08-01: 4886.01; 2010-09-01: 6795.48; 2010-10-01: 9547.37; 2010-11-01: 8536.47; 2010-12-01: 7885; 2011-01-01: 7368.32; 2011-02-01: 4032.36; 2011-03-01: 5144.35; 2011-04-01: 6515.78; 2011-05-01: 8245.83
CHILLED WATER ($) | 16290.54 | 2010-07-01: 11073.31; 2010-08-01: 5648.71; 2010-09-01: 1094.58; 2010-10-01: 1441.03; 2010-11-01: 130.22; 2010-12-01: 195.58; 2011-01-01: 224.9; 2011-02-01: 1771.02; 2011-03-01: 8948.72; 2011-04-01: 14418.35; 2011-05-01: 15482.27
NATURAL GAS ($) | 158.1 | 2010-07-01: 307.18; 2010-08-01: 324.45; 2010-09-01: 369.91; 2010-10-01: 398.09; 2010-11-01: 297.18; 2010-12-01: 358.09; 2011-01-01: 273.51; 2011-02-01: 361.96; 2011-03-01: 280.73; 2011-04-01: 178.27; 2011-05-01: 136.25
WATER ($) | 547.27 | 2010-07-01: 602.72; 2010-08-01: 487.4; 2010-09-01: 413.11; 2010-10-01: 137.79; 2010-11-01: 308.23; 2010-12-01: 299.49; 2011-01-01: 426.22; 2011-02-01: 550.4; 2011-03-01: 281.36; 2011-04-01: 1760.53; 2011-05-01: 1153.88
SEWER ($) | 441 | 2010-07-01: 481.8; 2010-08-01: 747; 2010-09-01: 631.4; 2010-10-01: 196.2; 2010-11-01: 468.2; 2010-12-01: 454.6; 2011-01-01: 651.8; 2011-02-01: 835.4; 2011-03-01: 230.2; 2011-04-01: 1427; 2011-05-01: 910.2
STORMWATER ($) | 262.57 | 2010-07-01: 262.57; 2010-08-01: 262.57; 2010-09-01: 262.57; 2010-10-01: 262.57; 2010-11-01: 262.57; 2010-12-01: 262.57; 2011-01-01: 262.57; 2011-02-01: 262.57; 2011-03-01: 262.57; 2011-04-01: 307.8; 2011-05-01: 307.8
7 | DoAg&CS - Davis Arena | bar: 2011-11-01 to 2011-12-01; 2012-03-01; 2012-06-01
NC Department of Agriculture & Consumer Services - Western Ag Center - Davis Events Center
| Utility | 2010-07-01: 2011-07-01; 2010-08-01: 2011-08-01; 2010-09-01: 2011-09-01; 2010-10-01: 2011-10-01; 2010-11-01: 2011-11-01; 2010-12-01: 2011-12-01; 2011-01-01: 2012-01-01; 2011-02-01: 2012-02-01; 2011-03-01: 2012-03-01; 2011-04-01: 2012-04-01; 2011-05-01: 2012-05-01; 2011-06-01: 2012-06-01; 2011-07-01: Annual Total
| Electricity Usage (KWhs) | 2010-09-01: 66200; 2010-10-01: 64100; 2010-11-01: 31200; 2010-12-01: 25400; 2011-01-01: 27000; 2011-02-01: 35300; 2011-03-01: 42100; 2011-04-01: 37700; 2011-05-01: 40500; 2011-06-01: 37800; 2011-07-01: 407300
| Water Usage (gallons) | 2010-09-01: 22769; 2010-10-01: 10786; 2010-11-01: 11108; 2010-12-01: 11108; 2011-01-01: 22769; 2011-02-01: 4488; 2011-03-01: 17204; 2011-04-01: 17204; 2011-05-01: 14960; 2011-06-01: 36652; 2011-07-01: 169048
| Natural Gas Therms | 2010-09-01: 12; 2010-10-01: 687; 2010-11-01: 1819; 2010-12-01: 1102; 2011-01-01: 2938; 2011-02-01: 3717; 2011-03-01: 3949; 2011-04-01: 1272; 2011-05-01: 619; 2011-06-01: 401; 2011-07-01: 16516
| Elecricity Cost ($) | 2010-09-01: 5583.22; 2010-10-01: 5585.23; 2010-11-01: 3095.65; 2010-12-01: 2707.31; 2011-01-01: 2888.23; 2011-02-01: 3481.19; 2011-03-01: 3966.99; 2011-04-01: 3652.65; 2011-05-01: 3852.68; 2011-06-01: 3756.5; 2011-07-01: 38569.65
| Water-Sewer Costs ($) | 2010-09-01: 1410.52; 2010-10-01: 668.17; 2010-11-01: 688.17; 2010-12-01: 688.17; 2011-01-01: 1410.52; 2011-02-01: 74.08; 2011-03-01: 1638.3; 2011-04-01: 1638.3; 2011-05-01: 1617.09; 2011-06-01: 1822.12; 2011-07-01: 11655.44
| Natural Gas ($) | 2010-09-01: 28.35; 2010-10-01: 624.64; 2010-11-01: 1595.37; 2010-12-01: 933.62; 2011-01-01: 2405.7; 2011-02-01: 2971.33; 2011-03-01: 2974.07; 2011-04-01: 991.77; 2011-05-01: 497.66; 2011-06-01: 334.75; 2011-07-01: 13357.26
| Utility | 2010-07-01: 2012-07-01; 2010-08-01: 2012-08-01; 2010-09-01: 2012-09-01; 2010-10-01: 2012-10-01; 2010-11-01: 2012-11-01; 2010-12-01: 2012-12-01; 2011-01-01: 2013-01-01; 2011-02-01: 2013-02-01; 2011-03-01: 2013-03-01; 2011-04-01: 2013-04-01; 2011-05-01: 2013-05-01; 2011-06-01: 2013-06-01; 2011-07-01: Annual Total
| Electricity Usage (KWhs) | 2010-07-01: 52500; 2010-08-01: 49100; 2010-09-01: 48100; 2010-10-01: 57500; 2010-11-01: 35100; 2010-12-01: 33600; 2011-01-01: 23200; 2011-02-01: 28800; 2011-03-01: 41100; 2011-04-01: 33900; 2011-05-01: 24900; 2011-06-01: 37700; 2011-07-01: 465500
| Water Usage (gallons) | 2010-07-01: 19448; 2010-08-01: 27676; 2010-09-01: 68816; 2010-10-01: 76296; 2010-11-01: 20944; 2010-12-01: 26180; 2011-01-01: 14212; 2011-02-01: 14212; 2011-03-01: 16456; 2011-04-01: 16456; 2011-05-01: 17952; 2011-06-01: 29172; 2011-07-01: 347820
| Natural Gas Therms | 2010-07-01: 176; 2010-08-01: 157; 2010-09-01: 99; 2010-10-01: 345; 2010-11-01: 895; 2010-12-01: 2042; 2011-01-01: 735; 2011-02-01: 1755; 2011-03-01: 5155; 2011-04-01: 3449; 2011-05-01: 210; 2011-06-01: 139; 2011-07-01: 15157
| Elecricity Cost ($) | 2010-07-01: 4852.01; 2010-08-01: 4785.4; 2010-09-01: 4659.1; 2010-10-01: 5576.91; 2010-11-01: 3696.78; 2010-12-01: 3591.05; 2011-01-01: 2861.87; 2011-02-01: 3259.68; 2011-03-01: 4133.47; 2011-04-01: 3621.98; 2011-05-01: 2982.63; 2011-06-01: 3217.16; 2011-07-01: 47238.04
| Water-Sewer Costs ($) | 2010-07-01: 1669.12; 2010-08-01: 1747.99; 2010-09-01: 2142.34; 2010-10-01: 2214.04; 2010-11-01: 1683.46; 2010-12-01: 1733.65; 2011-01-01: 1618.93; 2011-02-01: 1618.93; 2011-03-01: 903.2; 2011-04-01: 903.2; 2011-05-01: 917.54; 2011-06-01: 1025.09; 2011-07-01: 18177.49
| Natural Gas ($) | 2010-07-01: 157.8; 2010-08-01: 142.66; 2010-09-01: 96.42; 2010-10-01: 291.12; 2010-11-01: 713; 2010-12-01: 1580.5; 2011-01-01: 613.7; 2011-02-01: 1499.82; 2011-03-01: 4276.71; 2011-04-01: 2884.05; 2011-05-01: 210.6; 2011-06-01: 153.94; 2011-07-01: 12620.32
| Utility | 2010-07-01: 2013-07-01; 2010-08-01: 2013-08-01; 2010-09-01: 2013-09-01; 2010-10-01: 2013-10-01; 2010-11-01: 2013-11-01; 2010-12-01: 2013-12-01; 2011-01-01: 2014-01-01; 2011-02-01: 2014-02-01; 2011-03-01: 2014-03-01; 2011-04-01: 2014-04-01; 2011-05-01: 2014-05-01; 2011-06-01: 2014-06-01; 2011-07-01: Annual Total
| Electricity Usage (KWhs) | 2010-07-01: 36600; 2010-08-01: 43800; 2010-09-01: 61400; 2010-10-01: 37700; 2010-11-01: 75700; 2010-12-01: 28400; 2011-01-01: 37900; 2011-02-01: 36200; 2011-03-01: 45900; 2011-04-01: 42000; 2011-05-01: 41400; 2011-06-01: 50300; 2011-07-01: 537300
| Water Usage (gallons) | 2010-07-01: 12716; 2010-08-01: 29172; 2010-09-01: 71060; 2010-10-01: 105468; 2010-11-01: 34408; 2010-12-01: 11968; 2011-01-01: 17204; 2011-02-01: 15708; 2011-03-01: 23936; 2011-04-01: 15708; 2011-05-01: 48620; 2011-06-01: 82280; 2011-07-01: 468248
| Natural Gas Therms | 2010-07-01: 110; 2010-08-01: 155; 2010-09-01: 142; 2010-10-01: 347; 2010-11-01: 1226; 2010-12-01: 4592; 2011-01-01: 5878; 2011-02-01: 7314; 2011-03-01: 5593; 2011-04-01: 2972; 2011-05-01: 1035; 2011-06-01: 276; 2011-07-01: 29640
| Elecricity Cost ($) | 2010-07-01: 4034.18; 2010-08-01: 4478.51; 2010-09-01: 5764.87; 2010-10-01: 3969.19; 2010-11-01: 7040.4; 2010-12-01: 3284.26; 2011-01-01: 3914; 2011-02-01: 3792.91; 2011-03-01: 4483.8; 2011-04-01: 4348.46; 2011-05-01: 4211.4; 2011-06-01: 4943.1; 2011-07-01: 54265.08
| Water-Sewer Costs ($) | 2010-07-01: 877.95; 2010-08-01: 1038.55; 2010-09-01: 1769.06; 2010-10-01: 1783.15; 2010-11-01: 1089.65; 2010-12-01: 870.65; 2011-01-01: 921.75; 2011-02-01: 907.15; 2011-03-01: 987.45; 2011-04-01: 907.15; 2011-05-01: 1228.35; 2011-06-01: 1556.85; 2011-07-01: 13937.71
| Natural Gas ($) | 2010-07-01: 125.47; 2010-08-01: 169.65; 2010-09-01: 155.9; 2010-10-01: 338.38; 2010-11-01: 1073.25; 2010-12-01: 3850; 2011-01-01: 4856.35; 2011-02-01: 5952.64; 2011-03-01: 4638.77; 2011-04-01: 2517.46; 2011-05-01: 3464.35; 2011-06-01: 269; 2011-07-01: 27411.22
Notes: Davis Arena & Virginia Boone Bldg on same meter
8 | NCSU - Student Health Center Addition and Renovation | bar: 2011-10-01 to 2012-02-01
NCSU - Student Health Center Addition and Renovation
Utility | [5 empty] | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 |  | Total | Units
Electric (kWh) | [5 empty] | 64180.5431 | 64384.3453 | 67020.2609 | 64748.8092 | 61389.5423 | 63016.6942 | 61018.7101 | 68301.2237 | 66171.7788 | 66079.4689 | 63531.1419 | 67398.9993 | 74291.6667 |  | 851533.1842 | kwh
Chilled Water (Dtherms) | [5 empty] | 956.584 | 783.6435 | 475.6293 | 131.8786 | 121.7749 | 114.291 | 106.2765 | 165.1844 | 313.4366 | 604.7734 | 845.3457 | 958.5018 | 937.0703 |  | 6514.3902 | dthrms
Steam (1,000 lbs) | [5 empty] | 352.1 | 366.45 | 436.5833 | 504.869 | 640.318 | 599.6652 | 438.3448 | 329.4253 | 375.6322 | 331.5977 | 298.7356 | 290 | 192 |  | 5155.7212 | 1000 lbs
Water (CCF) | [5 empty] | 38.7056 | 58.523 | 71.1527 | 82.3383 | 36.5903 | 33.1318 | 31.7874 | 45.3888 | 44.8612 | 39.3007 | 30.8218 | 36.0646 | 47.6347 |  | 596.3007 | CCF
Electric Cost ($) | [5 empty] | 5583.7072 | 5601.438 | 5830.7627 | 5633.1464 | 5340.8902 | 5482.4524 | 5308.6278 | 5942.2065 | 5756.9448 | 5748.9138 | 5527.2093 | 5863.7129 | 6463.375 |  | 74083.387 | $
Chilled Water Cost ($) | [5 empty] | 13114.7666 | 10743.7521 | 6520.8778 | 1808.0563 | 1669.5345 | 1566.9292 | 1457.051 | 2264.6782 | 4297.2151 | 8291.4438 | 11589.6902 | 13802.4263 | 13493.8128 |  | 90620.234 | $
Steam Cost ($) | [5 empty] | 5077.282 | 5284.209 | 6295.5317 | 7280.2117 | 9233.3852 | 8647.1719 | 6320.9324 | 4750.3126 | 5416.6161 | 4781.6389 | 4307.7678 | 4022.3 | 2663.04 |  | 74080.3993 | $
Water Cost ($) | [5 empty] | 253.5216 | 383.3256 | 466.0502 | 539.3161 | 239.6663 | 217.013 | 208.2075 | 297.2965 | 293.8407 | 257.4193 | 201.883 | 283.4676 | 374.4084 |  | 4015.4158 | $
9 | ECSU - Gilchrist Ed & Psych Bldg | bar: 2014-08-01
Elizabeth City State University - Gilchrist Education & Psychology Building
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01
| Electricity Usage (KWhs) | 57984 | 55872 | 54912 | 47040 | 52224 | 53760 | 45312 | 61824 | 48768 | 40704 | 37632 | 48000
| Water Usage (gallons) | 4032.55 | 6507.99 | 6506.21 | 6886 | 3459.8 | 1843.55 | 1631.21 | 3347.66 | 2224.45 | 5903.93 | 4066.09 | 4406.22
| Elecricity Cost ($) | 7149.86 | 6834.85 | 7081.17 | 5824.79 | 6651.71 | 6224.35 | 5518.37 | 6829.41 | 5946.53 | 5304.53 | 4903.43 | 6276.31
| Water-Sewer Costs ($) | 39.52 | 63.79 | 64.41 | 68.1714 | 34.944 | 18.0668 | 16.149 | 32.8071 | 21.7996 | 57.8585 | 39.8477 | 43.181
10 | DoAg&CS - SENC Ag Center | bar: 2014-08-01
NC Department of Agriculture & Consumer Services - Southeastern Ag Center - Multi-purpose Pavilion
| Utility | 2011-07-01 | 2011-08-01 | 2011-09-01 | 2011-10-01 | 2011-11-01 | 2011-12-01 | 2012-01-01 | 2012-02-01 | 2012-03-01 | 2012-04-01 | 2012-05-01 | 2012-06-01 | Annual Total
| Electricity Usage (KWhs) |  |  |  |  | 2014-01-01: 7800; 2014-02-01: 5000; 2014-03-01: 2880; 2014-04-01: 15680
| Steam Usage (lbs) |  |  |  |  | 2014-04-01: 0
| Water Usage (gallons) |  |  |  |  | 2014-01-01: 168000; 2014-02-01: 37420; 2014-03-01: 44660; 2014-04-01: 250080
| Natural Gas Therms |  |  |  |  | 2014-01-01: 33; 2014-02-01: 30; 2014-03-01: 24; 2014-04-01: 87
| Elecricity Cost ($) |  |  |  |  | 2014-01-01: 1070.52; 2014-02-01: 786.6; 2014-03-01: 571.63; 2014-04-01: 2428.75
| Steam Costs ($) |  |  |  |  | 2014-04-01: 0
| Water-Sewer Costs ($) |  |  |  |  | 2014-01-01: 52.67; 2014-02-01: 73.84; 2014-03-01: N/A; 2014-04-01: 126.51
| Natural Gas ($) |  |  |  |  | 2014-01-01: 47.66; 2014-02-01: 45.33; 2014-03-01: 40.67; 2014-04-01: 133.66
| Utility | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | Annual Total
| Electricity Usage (KWhs) | 3360 | 2840 | 3200 | 1560 | 3360 | 2960 | 2840 | 2600 | 3800 | 2040 | 3480 | 4440 | 36480
| Steam Usage (lbs) |  |  |  |  | 2014-04-01: 0
| Water Usage (gallons) | 45320 | 40480 | 44030 | 55220 | 34670 | 28770 | 43050 | 147260 | 47580 | 10410 | 82440 | 53980 | 633210
| Natural Gas Therms | 24 | 25 | 24 | 37 | 636 | 65 | 779 | 1192 | 330 | 248 | 30 | 25 | 3415
| Elecricity Cost ($) | 620.3 | 567.57 | 604.08 | 437.78 | 620.3 | 579.74 | 567.57 | 543.24 | 736.37 | 755.2 | 857.12 | 1005.86 | 7895.13
| Steam Costs ($) |  |  |  |  | 2014-04-01: 0
| Water-Sewer Costs ($) | 51.91 | 52.67 | 54.58 | N/A | 193.64 | 158.97 | 224.89 | 629.89 | 242.41 | 319.37 | 153.26 | 238.6 | 2320.19
| Natural Gas ($) | 40.67 | 41.45 | 40.67 | 52.43 | 587.21 | 80.02 | 708.43 | 982.9 | 269.65 | 209.36 | 54.78 | 44.77 | 3112.34
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | Annual Total
| Electricity Usage (KWhs) | 2160 | 3000 | 3880 | 4120 | 2640 | 2560 | 2440 | 2120 | 2360 | 3120 | 2080 | 3840 | 34320
| Steam Usage (lbs) |  |  |  |  | 2014-04-01: 0
| Water Usage (gallons) | 34980 | 69680 | 57720 | 86280 | 18990 | 28600 | 38130 | N/A | 36090 | 43300 | 75980 | 29880 | 519630
| Natural Gas Therms | 27 | 23 | 28 | 247 | 420 | 706 | 1706 | 844 | 414 | 85 | 28 | 27 | 4555
| Elecricity Cost ($) | 628.28 | 700.93 | 929.19 | 802.74 | 1005.66 | 654.97 | 715.15 | 633.25 | 0 | 0 | 252.79 | 876.54 | 7199.5
| Steam Costs ($) |  |  |  |  | 2014-04-01: 0
| Water-Sewer Costs ($) | 497.3 | 217.65 | 557.12 | 325.85 | 228.31 | 297.28 | 235.55 | N/A | N/A | 149.45 | 232.89 | 231.36 | 2972.76
| Natural Gas ($) | 46.59 | 42.94 | 47.5 | 261.43 | 408.94 | 676.07 | 1620.61 | 790.77 | 364.27 | 92.09 | 47.23 | 48.21 | 4447
NOTES:
Pavilion, Farmers Market Building and Meeting Center all on the same water meter.
N/A - Invoice not received or credit applied from previous billing period
11 | UNCC - EPIC | bar: 2013-08-01 to 2014-04-01; 2014-07-01 to 2014-08-01
EPIC |  | 07-07078-02A
|  |  | Jul 13 | Aug 13 | Sep 13 | Oct 13 | Nov 13 | Dec 13 | Jan 14 | Feb 14 | Mar 14 | Apr 14 | May 14 | Jun 14
Consumption
Electric (KWH) |  |  | 360773 | 376949 | 339208 | 475978 | 334420 | 456727 | 399272 | 284263 | 314420 | 413293 | 410392 | 391747
Nat Gas (Therms) |  |  | 499 | 480 | 514 | 501 | 4215 | 4822 | 6505 | 4875 | 4806 | 2638 | 452 | 165
Water (CF) |  |  | 6260 | 6901 | 11570 | 8030 | 14562 | 12049 | 18954 | 14132 | 17648 | 9747 | 5630 | 8555
CHW BTUX10^6 |  |  | 2730 | 2466 | 2118 | 1481 | 1018 | 728 | 486 | 530 | 613 | 1247 | 1912 | 2337
HW BTUX10^6 |  |  | 418 | 526 | 551 | 613 | 955 | 735 | 925 | 588 | 602 | 410 | 184 | 168
Costs $
Electric |  |  | 24110.5129 | 25015.7484 | 22908.9863 | 28844.3132 | 19202.1671 | 26659.9109 | 22880.293 | 16573.6322 | 18628.5092 | 23495.3726 | 23691.8954 | 25409.5342
Nat Gas |  |  | 564.2193 | 473.0477 | 480.0909 | 468.3496 | 4041.7167 | 4628.9637 | 6263.0235 | 4577.6693 | 4222.6035 | 2212.2263 | 410.6048 | 176.88
Water |  |  | 536.1618 | 524.1549 | 859.6605 | 625.6938 | 1153.4009 | 1047.0153 | 1305.9465 | 1172.2459 | 1217.4786 | 708.5368 | 418.8973 | 649.4252
CHW |  |  | 12858.3 | 11614.86 | 9975.78 | 6975.51 | 4794.78 | 3428.88 | 2289.06 | 2496.3 | 2887.23 | 5873.37 | 9005.52 | 11007.27
HW |  |  | 3122.46 | 3929.22 | 4115.97 | 4579.11 | 7133.85 | 5490.45 | 6909.75 | 4392.36 | 4496.94 | 3062.7 | 1374.48 | 1254.96
12 | DOA - VA - VA Home Swananoa | bar: 2013-08-01 to 2014-04-01; 2014-07-01 to 2014-08-01
| NCDVA - NC State Veterans Home |  |  | Black Mountain |  | 2013-08-01: July 2013-Aug 2014
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity Usage (KWhs) | 148203 | 144096 | 152296 | 149628 | 156506 | 161390 | 165600 | 159984 | 154587 | 140548 | 156153 | 169544 | 174724 | 171911
| Steam Usage (lbs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Usage (gallons) | 3380 | 3609 | 3809 | 4051 | 4539 | 4647 | 5009 | 5463 | 5791 | 6173 | 6567 | 6978 | 5886 | 7680
| Natural Gas Usage | 1242 | 1151 | 1213 | 1541 | 1649 | 2164 | 2889 | 1316 | 1988 | 2180 | 1850 | 1648 | 1898 | 1719
| Elecricity Cost ($) | 12380.25 | 12244.87 | 12775.39 | 12473.39 | 12326.65 | 13270.41 | 13817.56 | 13187.61 | 12639.42 | 11636.7 | 12726.58 | 13809.79 | 14353.83 | 14122.68
| Steam Costs ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water-Sewer Costs ($) | 1992 | 2371.38 | 2159.68 | 2473.58 | 2552.3 | 2794.78 | 3342.28 | 4028.88 | 3094.08 | 3428.88 | 3575.88 | 3714.98 | 3199.04 | 3482.14
| Natural Gas Costs ($) | 1116.37 | 1038.91 | 1079.77 | 1278.27 | 1326.43 | 1846.92 | 2444.9 | 1147.49 | 1701.75 | 1883.57 | 1540.93 | 1474.33 | 1688.33 | 1533.74
13 | Pitt CC - Russell Classroom Building | bar: 2014-06-01 to 2014-07-01
14 | UNCG - Bailey Residence Hall Renovation | bar: 2014-08-01
| Bailey Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | 25624 | 25053 | 25134 | 28239 | 20460 | 25563 | 24454 | 22098 | 25793 | 20663 | 15650 | 15399 | 25182
| Steam Usage (lbs) | 10070 | 11480 | 25760 | 123940 | 175720 | 246650 | 178290 | 97990 | 25440 | 6630 | 4130 | 3810 | 9290
| Water Usage (gallons) | 38300 | 52600 | 52900 | 59100 | 15700 | 43700 | 51400 | 39400 | 52700 | 13700 | 1000 | 600 | 47500
| Chilled water (ton-hrs) | 26405 | 19492 | 18522 | 11913 | 10588 | 7195 | 8456 | 8389 | 14529 | 28608 | 22546 | 21501 | 28341
| Electricity Cost ($) | 1819.24 | 1782.02 | 1601.38 | 1702.92 | 1277.51 | 1564.76 | 1465.44 | 1379.16 | 1530.04 | 1261.91 | 1061.54 | 1044.52 | 1708.09
| Water Cost ($) | 271.16 | 373.28 | 375.41 | 419.41 | 111.41 | 310.12 | 364.76 | 279.61 | 373.99 | 97.22 | 7.1 | 4.26 | 337.09
| Steam Cost ($) | 78.68 | 89.69 | 201.27 | 968.4 | 1372.99 | 1927.2 | 1393.09 | 765.65 | 198.76 | 51.8 | 32.27 | 29.77 | 72.58
15 | UNCG - Coit Residence Hall Renovation
| Coit Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | 24291 | 23834 | 24071 | 28259 | 19016 | 18684 | 17980 | 22050 | 24756 | 20501 | 15721 | 15058 | 22964
| Steam Usage (lbs) | 9780 | 18790 | 35540 | 67950 | 35990 | 65960 | 49660 | 16350 | 15230 | 7320 | 3870 | 3580 | 7620
| Water Usage (gallons) | 34000 | 50200 | 46800 | 48900 | 12400 | 95100 | 44700 | 33800 | 44800 | 11300 | 1000 | 1000 | 32800
| Chilled water (ton-hrs) | 25280 | 17804 | 15818 | 13265 | 10015 | 6558 | 6932 | 10604 | 13436 | 17467 | 22527 | 20569 | 23987
| Electricity Cost ($) | 1724.6 | 1695.31 | 1533.65 | 1704.13 | 1187.34 | 1143.68 | 1077.47 | 1376.16 | 1468.52 | 1252.02 | 1066.36 | 1021.38 | 1557.65
| Water Costs ($) | 240.72 | 356.25 | 332.12 | 347.02 | 87.99 | 674.89 | 317.22 | 239.87 | 317.93 | 80.19 | 7.1 | 7.1 | 232.77
| Steam Cost ($) | 76.42 | 148.23 | 277.71 | 530.95 | 281.23 | 515.4 | 388.04 | 127.75 | 118.99 | 57.19 | 30.24 | 27.97 | 59.53
16 | UNCG - Cotten Residence Hall Renovation
| Cotten Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | 25985 | 25488 | 25792 | 29122 | 20458 | 25362 | 24858 | 22332 | 24797 | 22117 | 16522 | 16664 | 24495
| Steam Usage (lbs) | 17510 | 18660 | 42650 | 178400 | 222330 | 307240 | 214670 | 187860 | 5500 | 1200 | 800 | 7670 | 17550
| Water Usage (gallons) | 41400 | 57400 | 53500 | 58100 | 18100 | 48000 | 52700 | 42600 | 56500 | 15100 | 1100 | 2000 | 38200
| Chilled water (ton-hrs) | 20123 | 15106 | 12124 | 9249 | 6692 | 4295 | 6190 | 6354 | 11830 | 13283 | 15463 | 15205 | 20417
| Electricity Cost ($) | 1844.87 | 1812.96 | 1643.3 | 1756.17 | 1277.38 | 1552.46 | 1489.65 | 1393.76 | 1470.95 | 1350.71 | 1120.69 | 1130.32 | 1661.49
| Water Costs ($) | 293.11 | 407.35 | 379.69 | 412.31 | 128.45 | 340.64 | 373.4 | 302.32 | 400.96 | 107.16 | 7.81 | 14.19 | 271.09
| Steam Cost ($) | 136.82 | 145.8 | 333.26 | 1393.98 | 1737.26 | 2400.74 | 1677.41 | 1467.92 | 42.98 | 9.38 | 6.25 | 59.92 | 137.11
17 | UNCG - Gray Residence Hall Renovation
| Gray Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | 27005 | 25748 | 25583 | 28483 | 20273 | 24384 | 24093 | 21685 | 25360 | 22439 | 17547 | 17041 | 24553
| Steam Usage (lbs) | 10320 | 19220 | 74170 | 101070 | 164580 | 79260 | 27740 | 21140 | 17150 | 6640 | 3240 | 3420 | 8350
| Water Usage (gallons) | 36500 | 56300 | 54600 | 60100 | 15500 | 39800 | 45400 | 36400 | 46400 | 11400 | 300 | 2500 | 39200
| Chilled water (ton-hrs) | 21997 | 15498 | 4827 | 1746 | 2355 | 1761 | 1185 | 1361 | 4590 | 10241 | 14216 | 13854 | 18369
| Electricity Cost ($) | 1834.15 | 1831.46 | 1629.99 | 1717.64 | 1265.83 | 1492.59 | 1443.8 | 1353.38 | 1504.35 | 1370.38 | 1190.22 | 1155.89 | 1665.43
| Water Costs ($) | 258.42 | 399.53 | 387.47 | 426.51 | 109.99 | 282.45 | 322.19 | 258.32 | 329.28 | 80.9 | 2.13 | 17.74 | 278.19
| Steam Cost ($) | 80.64 | 150.18 | 579.56 | 789.75 | 1286.02 | 619.33 | 216.75 | 165.18 | 134 | 51.88 | 25.32 | 26.72 | 65.24
18 | UNCG - Hinshaw Residence Hall Renovation
| Hinshaw Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | 30854 | 28712 | 29511 | 33257 | 24327 | 30170 | 27805 | 25465 | 29541 | 25832 | 21021 | 20853 | 31432
| Steam Usage (lbs) | 15530 | 16160 | 19220 | 74170 | 101070 | 164580 | 93920 | 79260 | 21760 | 18500 | 7260 | 7050 | 16160
| Water Usage (gallons) | 35800 | 45900 | 43000 | 45600 | 11900 | 42900 | 44900 | 38400 | 48000 | 14900 | 2000 | 2500 | 46000
| Chilled water (ton-hrs) | 26126 | 20812 | 13519 | 8387 | 7243 | 4389 | 5121 | 5517 | 10705 | 14355 | 17665 | 17243 | 24184
| Electricity Cost ($) | 2190.56 | 2042.29 | 1880.26 | 2005.53 | 1518.96 | 1846.76 | 16666.25 | 1589.3 | 1752.37 | 1577.59 | 1425.86 | 1414.46 | 2132.3
| Water Costs ($) | 253.46 | 325.73 | 305.15 | 323.61 | 84.45 | 304.45 | 318.64 | 272.51 | 340.64 | 105.74 | 14.2 | 17.74 | 326.44
| Steam Cost ($) | 121.34 | 126.27 | 150.18 | 579.56 | 789.75 | 1286.02 | 733.88 | 619.33 | 170.02 | 144.55 | 56.73 | 55.08 | 126.25
19 | UNCG - Jamison Residence Hall Renovation
| Jamison Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | 27052 | 25616 | 25462 | 28596 | 20973 | 26326 | 25140 | 22531 | 26409 | 21608 | 17290 | 16370 | 25698
| Steam Usage (lbs) | 13410 | 14010 | 19540 | 26860 | 30120 | 152230 | 106610 | 54940 | 9057 | 7490 | 4430 | 4310 | 7090
| Water Usage (gallons) | 32800 | 47100 | 44600 | 46200 | 12500 | 41300 | 46600 | 36500 | 51000 | 15100 | 5000 | 1830 | 43600
| Chilled water (ton-hrs) | 93450 | 73070 | 63360 | 43080 | 37670 | 36410 | 41780 | 37230 | 50260 | 59920 | 76220 | 81520 | 90670
| Electricity Cost ($) | 1920.63 | 1822.07 | 1622.28 | 1724.45 | 1309.54 | 1611.46 | 1506.55 | 1406.18 | 1566.58 | 1319.63 | 1172.78 | 1110.37 | 1743.09
| Water Costs ($) | 232.22 | 334.25 | 316.51 | 327.86 | 88.71 | 293.09 | 330.7 | 259.03 | 361.93 | 107.16 | 3.55 | 12.98 | 309.41
| Steam Cost ($) | 104.78 | 109.46 | 152.68 | 209.88 | 235.35 | 1189.51 | 833.04 | 110.12 | 70.76 | 58.52 | 34.61 | 33.67 | 55.39
20 | UNCG - Shaw Residence Hall Renovation
| Shaw Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | 48804 | 47115 | 47333 | 52848 | 39962 | 49214 | 46143 | 41387 | 48781 | 42948 | 33373 | 32432 | 44245
| Steam Usage (lbs) | 5540 | 53240 | 164380 | 704150 | 751020 | 1089140 | 817570 | 691630 | 207770 | 139600 | 14660 | 5440 | 12360
| Water Usage (gallons) | 60400 | 83400 | 80700 | 84800 | 24500 | 72900 | 86300 | 66100 | 90000 | 24300 | 800 | 3600 | 66600
| Chilled water (ton-hrs) | 49955 | 39687 | 36569 | 33365 | 30866 | 21826 | 19329 | 25175 | 31822 | 38534 | 42917 | 41963 | 55574
| Electricity Cost ($) | 3464.97 | 3351.29 | 3015.76 | 3186.94 | 2495.19 | 3012.48 | 2765.18 | 2583.01 | 2893.68 | 2622.89 | 2263.7 | 2199.86 | 3001.13
| Water Costs ($) | 427.63 | 591.86 | 572.69 | 601.79 | 173.87 | 517.34 | 612.44 | 469.08 | 638.69 | 172.45 | 5.68 | 25.55 | 472.63
| Steam Cost ($) | 43.28 | 416.02 | 1284.49 | 5502.16 | 5868.4 | 8510.04 | 6388.41 | 5404.33 | 1623.49 | 1090.82 | 114.55 | 42.5 | 96.56
21 | WCU - Harrill Residence Hall Renovation
Western Carolina University - Harrill Hall Energy Water Use
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01
| Electricity Usage (KWhs) | 74080 | 88168 | 94347 | 79716 | 75594 | 66617 | 85340 | 76631 | 72908 | 70976 | 59228 | 60285
| Steam Usage (lbs) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Water Usage (gallons) | 20180 | 111900 | 206350 | 166780 | 170630 | 81220 | 141630 | 141240 | 52920 | 73766 | 60030 | 9290
| Elecricity Cost ($) | 5158.04 | 6351.6 | 6775.34 | 4737.52 | 4513.57 | 4111.27 | 5047.43 | 4655.49 | 4283.78 | 4205.75 | 3551.78 | 4406.35
| Steam Costs ($) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Water-Sewer Costs ($) | 62.558 | 346.89 | 639.685 | 517.018 | 528.953 | 251.782 | 439.053 | 437.844 | 164.052 | 228.6746 | 186.093 | 28.799
22 | UNCP Health Science Builidng
University of North Carolina at Pembroke - Health Science Building Energy & Natural Gas Usage |  | 2014-08-01: Total Sq. Ft. & Utility #'s p/sq/ft.
| Utility | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | Total | 87593
| Electricity Usage (KWhs) | 85778.96 | 113621.46 | 152143.24 | 180402.2 | 114532.16 | 95786.24 | 90504.5062 | 111469.9 | 86489.4 | 99097.3 | 111892.5 | 111500 | 1353217.8662 | #REF!
| Electricity Cost | 6927.5088 | 9176.0691 | 12287.0881 | 14569.2817 | 9249.6172 | 7735.6967 | 7309.1439 | 9002.3091 | 6984.8839 | 8003.0979 | 9036.4383 | 9004.74 | 109285.8749 | #REF!
| Natural Gas (Therms) | 0 | 0 | 0 | 0 | 0 | 0 | 10503 | 4632 | 3618 | 2624 | 1926 | 1450 | 24753 | #REF!
| Natural Gas Cost | 0 | 0 | 0 | 0 | 0 | 0 | 4218.0048 | 1860.2112 | 1452.9888 | 1053.7984 | 773.4816 | 582.32 | 9940.8048 | #REF!
| Natural Gas Transportation Cost | 0 | 0 | 0 | 0 | 0 | 0 | 1825.4214 | 805.0416 | 628.8084 | 456.0512 | 334.7388 | 252.01 | 4302.0714 | #REF!
| Total Natural Gas Charges | 0 | 0 | 0 | 0 | 0 | 0 | 6043.4262 | 2665.2528 | 2081.7972 | 1509.8496 | 1108.2204 | 834.33 | 14242.8762 | #REF!
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | Total
| Electricity Usage (KWhs) | 132276 | 137730 | 134465 | 124059 | 117931 | 93622 | 110748 | 109838 | 79601 | 106369 | 52332 | 111294 | 1310265 | #REF!
| Electricity Cost | 10682.6098 | 11123.0748 | 10859.3934 | 10019.0048 | 9524.1076 | 7560.9127 | 8944.0085 | 8870.5169 | 6428.5768 | 8590.3604 | 4226.3323 | 8988.1034 | 105817.0014 | #REF!
| Natural Gas (Therms) | 1577 | 1398 | 1304 | 1202 | 2179 | 2368 | 4126 | 4009 | 2298 | 2457 | 1910 | 1177 | 26005 | #REF!
| Natural Gas Cost | 633.3232 | 561.4368 | 523.6864 | 482.7232 | 875.0864 | 950.9888 | 1657.0016 | 1610.0144 | 922.8768 | 986.7312 | 767.056 | 472.6832 | 10443.608 | #REF!
| Natural Gas Transportation Cost | 274.0826 | 242.9724 | 226.6352 | 208.9076 | 378.7102 | 411.5584 | 717.0988 | 696.7642 | 399.3924 | 427.0266 | 331.958 | 204.5626 | 4519.669 | #REF!
| Total Natural Gas Charges | 907.4058 | 804.4092 | 750.3216 | 691.6308 | 1253.7966 | 1362.5472 | 2374.1004 | 2306.7786 | 1322.2692 | 1413.7578 | 1099.014 | 677.2458 | 14963.277 | #REF!
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | Total
| Water Usage (gal) | 147700 | 141500 | 131000 | 67100 | 31250 | 18300 | 9750 | 10120 | 26800 | 50000 | 94225 | 120500 | 848245
| Water Cost | 4181.387 | 4005.865 | 3708.61 | 1899.601 | 884.6875 | 518.073 | 276.0225 | 286.4972 | 758.708 | 1415.5 | 2667.5097 | 3411.355 | 24013.816 | #REF!
The water usage has been estimated based on normal cooling tower evaperation and additional building water usage per month. We will begin monthly readings of this water submeter.
23 | FSU - Renaissance Residence Hall
24 | UNCA - Overlook Residence Hall
25 | ECSU - Viking Tower Residence Hall
Elizabeth City State University - Viking Tower (New Mitchell Lewis Residence Hall)
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01
| Electricity Usage (KWhs) | 48053 | 56310 | 63175 | 64734 | 55026 | 46456 | 48327 | 49101 | 51656 | 57063 | 47757 | 43244
| Water Usage (gallons) | 48861 | 112674 | 264394 | 244725 | 139753 | 139753 | 150199 | 166150 | 151077 | 211623 | 73612 | 41488
| Elecricity Cost ($) | 4867.72 | 5951.96 | 6608.09 | 6868.25 | 5915.33 | 4915.04 | 5166.14 | 5263.58 | 5501.36 | 5991.59 | 4995.37 | 4631.39
| Water-Sewer Costs ($) | 478.84 | 1104.21 | 2617.5 | 2422.78 | 1411.51 | 1369.58 | 1486.97 | 1628.27 | 1480.55 | 2073.91 | 721.4 | 406.58
26 | UNCW Teaching Lab
TEACHING LAB | 2013-07-09 | 2013-08-09 | 2013-09-09 | 2013-10-09 | 2013-11-09 | 2013-12-09 | 2014-01-09 | 2014-02-09 | 2014-03-09 | 2014-04-09 | 2014-05-09 | 2014-06-09 | TOTAL YTD
ELECTRIC
METER READING | 1192770 | 1282096 | 1367953 | 1505553 | 1571441 | 1679793 | 1800034 | 1903785 | 2005185 | 2101424 | 2175898 | 2269373 | -----
PREVIOUS READING | 1083629 | 1192770 | 1282096 | 1367953 | 1505553 | 1571441 | 1679793 | 1800034 | 1903785 | 2005185 | 2101424 | 2175898 | -----
CHANGE | 109141 | 89326 | 85857 | 137600 | 65888 | 108352 | 120241 | 103751 | 101400 | 96239 | 74474 | 93475 | -----
KWH | 109141 | 89326 | 85857 | 137600 | 65888 | 108352 | 120241 | 103751 | 101400 | 96239 | 74474 | 93475 | 1185744
COST/KWH | 0.08 | 0.0847 | 0.0799 | 0.074 | 0.0705 | 0.0742 | 0.0707 | 0.0756 | 0.0726 | 0.0706 | 0.0696 | 0.0813 | 0.0753
COST | 8731.28 | 7565.91 | 6859.97 | 10182.4 | 4645.1 | 8039.72 | 8501.04 | 7843.58 | 7361.64 | 6794.47 | 5183.39 | 7599.52 | 89308.02
WATER
METER READING high | 473026 | 494183 | 525333 | 566617 | 576248 | 586059 | 604391 | 618147 | 636909 | 668864 | 686404 | 708452
PREVIOUS READING | 445199 | 473026 | 494183 | 525333 | 566617 | 576248 | 586059 | 604391 | 618147 | 636909 | 668864 | 686404
CHANGE - GAL | 27827 | 21157 | 31150 | 41284 | 9631 | 9811 | 18332 | 13756 | 18762 | 31955 | 17540 | 22048
METER READING low | 9474 | 94745 | 94745 | 369557 | 748737 | 1155180 | 173982 | 228770 | 279413 | 318911 | 347096 | 373144
PREVIOUS READING | 9474 | 9474 | 94745 | 94745 | 369557 | 748737 | 1155180 | 173982 | 228770 | 279413 | 318911 | 347096
CHANGE - GAL | 0 | 85271 | 0 | 274812 | 379180 | 406443 | -981198 | 54788 | 50643 | 39498 | 28185 | 26048
TOTAL GALLONS | 27827 | 106428 | 31150 | 316096 | 388811 | 416254 | -962866 | 68544 | 69405 | 71453 | 45725 | 48096 | 626923
COST/GAL | 0.0037 | 0.0037 | 0.0037 | 0.0036 | 0.0036 | 0.0037 | 0.0037 | 0.0038 | 0.0038 | 0.0037 | 0.0037 | 0.0039 | 0.0036
COST | 102.96 | 393.78 | 115.26 | 1137.95 | 1399.72 | 1540.14 | -3562.6 | 260.47 | 263.74 | 264.38 | 169.18 | 187.57 | 2272.55
SEWAGE
COST/GAL | 0.0046 | 0.005 | 0.005 | 0.0047 | 0.0047 | 0.0045 | 0.0045 | 0.0043 | 0.0043 | 0.0044 | 0.0044 | 0.005 | 0.0048
COST | 128 | 532.14 | 155.75 | 1485.65 | 1827.41 | 1873.14 | -4332.9 | 294.74 | 298.44 | 314.39 | 201.19 | 240.48 | 3018.43
FUEL OIL
GALLONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHILLED WATER
TON_HR |  |  | 80296 | 95195 | 43466 | 36570 | 19051 | 23850 | 23687 | 76208 | 114941.3521 | 160071.7198 | 673336.0719
COST (SF based calculation) | 16088 | 14362 | 8271 | 7801 | 1814 | 3336 | 2530 | 2243 | 2486 | 5389 | 5703 | 12696 | 82719
HEATING HOT WATER
MBTU |  |  | 98480 | 192448.7 | 256470.9875 | 246075.9 | 413569.8875 | 367402.9125 | 327137.85 | 239755.8875 | 206739.5 | 180217.2875 | 2528298.9125
COST (SF based calculation) | 1828.29 | 1455 | 1208 | 2422 | 1567 | 3248 | 2711 | 3327 | 2821 | 1789 | 1578 | 1927 | 25881.29
- | bar: 2013-07-09 to 2014-06-09
TOTAL UTILITIES | 8962.24 | 8491.83 | 16609.98 | 23029 | 11253.23 | 18037 | 5846.54 | 13968.79 | 13230.82 | 14551.24 | 12834.76 | 22650.57 | 169466
= | bar: 2013-07-09 to 2014-06-09
TRASH | 78.92 | 157.84 | 177.57 | 177.57 | 157.84 | 138.11 | 177.57 | 157.84 | 177.57 | 157.84 | 118.38 | 78.92 | 1755.97
Jul-13 began using water on line meter reading from the graphics UNCW meter page.
Jan water low flow meter reading?
Jul usage 6/21/13-8/1/13 | 2013-07-09: Sep usage 9/3/13-10/1/13; 2013-09-09: Nov usage 11/14/13-12/2/13; 2013-11-09: Jan usage 1/3/14-2/3/14; 2014-01-09: Mar usage 3/3/14-4/1/14; 2014-03-09: May usage 5/1/14-5/28/14
Aug usage 8/1/13-9/3/13 | 2013-07-09: Oct usage 10/1/13-11/14/13; 2013-09-09: Dec usage 12/2/13-1/3/14; 2013-11-09: Feb usage 2/3/14-3/3/14; 2014-01-09: Apr usage 4/1/14-5/1/14; 2014-03-09: Jun usage 5/28/14-7/1/14
| 83301 1830392826 CEIC 413 Ind. Pk. Ave. | 7/11-8/12 | 8/12-9/10 | 9/10-10/9 | 10/9-11/12 | 11/12-12/11 | 12/11-1/15 | 1/15-2/11 | 2/11-3/12 | 3/12-4/10 | 4/10-5/9 | 5/9-6/10 | 6/10-7/9 | CF | gals
| Usage (cf) | 87 | 119 | 118 | 146 | 109 | 82 | 110 | 187 | 157 | 199 | 110 | 137 | 1561 | 11676.28
| Days in Period | 32 | 29 | 29 | 34 | 29 | 35 | 27 | 29 | 29 | 29 | 32 | 29
| Water | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 14.74 | 13.95 | 15.05 | 13.77 | 13.77 | 167.67
| Sewer | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 17.81 | 17.02 | 18.12 | 16.84 | 16.84 | 204.51
| Total | 30.61 | 30.61 | 30.61 | 30.61 | 30.61 | 30.61 | 30.61 | 32.55 | 30.97 | 33.17 | 30.61 | 30.61 | 372.18
| 2014-05-09: Tolal Utility |  | 372.18
27 | 2013-07-09: UNCA - Rhoades Hall Renovation
28 | 2013-07-09: ECU - Ross Hall
East Carolina University - Ledyard E. Ross Hall Energy & Water Use
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity Usage (KWhs) | 186286.46 | 190588.42 | 188476.34 | 187630.31 | 177812.54 | 176182.44 | 184912.54 | 167556.58 | 187339.86 | 186005.46 | 201417.79 | 186189 | 190007 | 191943
Natural Gas Usage (CCF)
Steam Usage (lbs)
Water Usage (gallons)
| Elecricity Cost ($) | 17510.9272 | 17915.3115 | 17716.776 | 17637.2491 | 16714.3788 | 16561.1494 | 17381.7788 | 15750.3185 | 17609.9468 | 17484.5132 | 18933.2723 | 17501.766 | 17860.658 | 18042.642
Steam Costs ($)
Water-Sewer Costs ($)
29 | 2013-07-09: Gaston College - Lena Sue Beam Renovation
30 | 2013-07-09: NCSU - Hunt Library
NCSU - Hunt Library
Utility |  | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 |  | Total | Units
Electric (kWh) |  | 360279.8329 | 365608.5497 | 337257.4034 | 350749.6654 | 357953.9482 | 365680.8245 | 375253.554 | 367059.5389 | 350414.1822 | 349761.6153 | 329313.9403 | 325871.9224 | 341362.9913 | 347227.0203 | 347058.96 | 352408.0811 | 352410.8887 |  | 5975672.9183 | kwh
Chilled Water (Dtherms) |  | 940.23 | 1387.3 | 2109.55 | 2555.68 | 1777.59 | 385.3984 | 768.36 | 928.36 | 802.45 | 905.56 | 790.99 | 663.48 | 268.4 | 7223.208 | 6896.752 | 6485.24 | 6501.92 |  | 41390.4684 | dthrms
Steam (1,000 lbs) | * | 1037 | 1049 | 1003 | NA | NA | NA | NA | 5385 | 1274 | 1539 | 1287 | 1275 | 1023 | 1024 | 985 | 343.2969 | 345.3047 |  | 17569.6016 | 1000 lbs
Water (CCF) |  | 136.5309 | 112.3247 | 63.2194 | 72.4439 | 91.7172 | 145.9627 | 164.3336 | 157.079 | 112.4944 | 112.1846 | 126.3049 | 164.661 | 175.0607 | 120.1814 | 575 | 341 | 301 |  | 2971.4986 | CCF
Electric Cost ($) |  | 30263.506 | 30711.1182 | 28329.6219 | 30515.2209 | 31141.9935 | 31814.2317 | 32647.0592 | 31934.1799 | 30486.0338 | 30429.2605 | 28650.3128 | 28350.8572 | 29698.5802 | 30208.7508 | 30194.1295 | 30659.5031 | 30659.7473 |  | 516694.1065 | $
Chilled Water Cost ($) |  | 12899.9556 | 19033.756 | 28943.026 | 35038.3728 | 24370.7589 | 5283.8125 | 10534.2156 | 12727.8156 | 11001.5895 | 12415.2276 | 10844.4729 | 9096.3108 | 3679.764 | 99030.1817 | 94554.4699 | 93387.456 | 93627.648 |  | 576468.8334 | $
Steam Cost ($) | * | 14300.23 | 14465.71 | 13831.37 | NA | NA | NA | NA | 77651.7 | 18371.08 | 22192.38 | 18558.54 | 18385.5 | 14751.66 | 14766.08 | 14203.7 | 4761.5277 | 4789.376 |  | 251028.8537 | $
Water Cost ($) |  | 897.0083 | 737.9734 | 415.3512 | 474.5077 | 600.7479 | 956.0556 | 1076.385 | 1028.8676 | 736.8385 | 734.8092 | 827.2972 | 1078.5298 | 1146.6478 | 787.1883 | 3766.25 | 2680.26 | 2365.86 |  | 20310.5775 | $
* Steam data is questionable. Meter calibration/operation issues.
31 | UNCC - Rose Football Center | bar: 2013-04-01 to 2014-04-01; 2014-07-01 to 2014-08-01
| Judy W. Rose Football Center | 2013-05-01: 08-07833-02A
|  | Jul 13 | Aug 13 | Sep 13 | Oct 13 | Nov 13 | Dec 13 | Jan 14 | Feb 14 | Mar 14 | Apr 14 | May 14 | Jun 14
Consumption
| Electric (KWH) | 161849 | 167621 | 182746 | 175264 | 165377 | 138223 | 119830 | 116370 | 194940 | 100670 | 146090 | 143280
| Nat Gas (Therms) | 1562 | 1694 | 2077 | 2277 | 3889 | 3340 | 4159 | 3475 | 3298 | 2174 | 1014 | 1031
| Water (CF) | 5490 | 15661 | 14440 | 14072 | 9708 | 2193 | 5277 | 5689 | 12523 | 7430 | 5461 | 5332
excludes irrigation
Costs $
| Electric | 10816.3926 | 11123.9578 | 12342.0604 | 10621.0155 | 9495.834 | 8068.3053 | 6866.8615 | 6784.821 | 11549.652 | 5723.008 | 8433.7633 | 9293.4421
| Nat Gas | 1421.581 | 1536.5429 | 1890.94 | 2070.68 | 3632.33 | 3098.56 | 3905.05 | 3217.44 | 2833.32 | 1794.83 | 905.17 | 940.95
| Water | 470.2122 | 1189.5074 | 1072.9039 | 1096.4836 | 768.9339 | 190.5639 | 363.5897 | 471.9012 | 863.9214 | 540.1076 | 406.323 | 404.7615
32 | DOA - VA - VA Home Kinston | bar: 2013-04-01 to 2014-04-01; 2014-07-01 to 2014-08-01
| NCDVA - NC State Veterans Home- | 2013-06-01: NC State Veterans Home - Kinston
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-14 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity Usage (KWhs) | 150800 | 161600 | 141600 | 143400 | 149400 | 154400 | 156800 | 156600 | 130000 | 173200 | 135800 | 186000 | 170800
| Gas Usage (lbs) | 651 | 723 | 739 | 865 | 963 | 922 | 1343 | 902 | 1093 | 1216 | 1071 | 1119 | 1251
| Water Usage (gallons) | 107680 | 159550 | 81300 | 71600 | 112300 | 137480 | 124050 | 143200 | 136010 | 116500 | 141800 | 161100 | 182600
| Elecricity Cost ($) | 8632.47 | 13344.33 | 12036.47 | 12116.49 | 12380.97 | 12747.97 | 12650.83 | 12896.19 | 12896.19 | 13921.29 | 11155.12 | 15036.73 | 14221.17
| Gas Cost ($) | 609.44 | 674.14 | 688.52 | 801.75 | 917.8 | 872.94 | 1277.49 | 903.14 | 1878.26 | 1015.77 | 951.11 | 1019.18 | 1166.66
| Water-Sewer Costs ($) | 749.22 | 1017.19 | 651.76 | 606.46 | 796.53 | 914.12 | 865.11 | 953.61 | 907.25 | 816.15 | 934.29 | 1024.43 | 1124.83
33 | Randolph Community College - Kaussner Building Renovation
| CEIC | 2013-04-01: July 2013 - June 2014
|  | July | August | September | October | November | December | January | February | March | April | May | June | Total
053 029 3190 TJ9935 CEIC
| kWh Usage | 64600 | 53900 | 64100 | 54700 | 49500 | 41600 | 31300 | 36600 | 44300 | 60400 | 61700 | 76000 | 638700
| KW | 147 | 144 | 162 | 165 | 143 | 156 | 105 | 111 | 120 | 212 | 218 | 147 | 152.5
| Days in period | 31 | 28 | 30 | 30 | 33 | 33 | 30 | 28 | 29 | 33 | 30 | 32
| Amount | 5090.56 | 4487.73 | 5212.95 | 4215.84 | 3841.59 | 3433.28 | 2464.73 | 2788.5 | 3321.54 | 4740.77 | 4845.83 | 5346.96 | 49790.28
| Lighting | 805.28 | 805.28 | 805.28 | 805.28 | 805.28 | 797.6 | 793.76 | 793.76 | 793.76 | 793.76 | 793.76 | 793.76 | 9586.56
| 3% Sales Tax | 176.88 | 158.79 | 180.55 | 150.63 | 139.41 | 126.93 | 97.75 | 107.47 | 123.46 | 166.04 | 169.19 | 184.22 | 1781.32
| Total Bill | 6072.72 | 5451.8 | 6198.78 | 5171.75 | 4786.28 | 4357.81 | 3356.24 | 3689.73 | 4238.76 | 5700.57 | 5808.78 | 6324.94 | 61158.16
1003287462001 859461 CEIC 412 Industrial Pk
| Therms Used | 239 | 273 | 152 | 702 | 843 | 1057 | 1141 | 1560 | 1110 | 732 | 311 | 259 | 8379
| Amount | 228.42 | 257.78 | 153.28 | 666.39 | 764.96 | 963.02 | 1048.32 | 1372.94 | 893.73 | 599.66 | 287.59 | 243.18 | 7479.27
| Excise Tax/Sales Tax | 10.77 | 11.96 | 7.14 | 26.97 | 31.91 | 39.4 | 42.34 | 57 | 41.25 | 28.02 | 13.29 | 17.02 | 327.07
| Total Bill | 239.19 | 269.74 | 160.42 | 693.36 | 796.87 | 1002.42 | 1090.66 | 1429.94 | 934.98 | 627.68 | 300.88 | 260.2 | 7806.34
| 83301 1830392826 CEIC 413 Ind. Pk. Ave. | 7/11-8/12 | 8/12-9/10 | 9/10-10/9 | 10/9-11/12 | 11/12-12/11 | 12/11-1/15 | 1/15-2/11 | 2/11-3/12 | 3/12-4/10 | 4/10-5/9 | 5/9-6/10 | 6/10-7/9 | CF | gals
| Usage (cf) | 87 | 119 | 118 | 146 | 109 | 82 | 110 | 187 | 157 | 199 | 110 | 137 | 1561 | 11676.28
| Days in Period | 32 | 29 | 29 | 34 | 29 | 35 | 27 | 29 | 29 | 29 | 32 | 29
| Water | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 14.74 | 13.95 | 15.05 | 13.77 | 13.77 | 167.67
| Sewer | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 17.81 | 17.02 | 18.12 | 16.84 | 16.84 | 204.51
| Total | 30.61 | 30.61 | 30.61 | 30.61 | 30.61 | 30.61 | 30.61 | 32.55 | 30.97 | 33.17 | 30.61 | 30.61 | 372.18
[11 empty] | Tolal Utility |  |  | 69336.68
34 | ASU - Plemmons Student Union Addition | bar: 2013-04-01
App State - Plemmons, Cone, Summit Utility Data
ELECTRICITY
Bldg. # | Building Name | time axis 2010-07-01 to 2014-07-01
204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 227800 | 214280 | 225000 | 221480 | 190120 | 186400 | 149800 | 169880 | 176080 | 194280 | 202520 | 204080 | 185200 | 182360 | 221240 | 184480 | 192240 | 159400 | 93960 | 150160 | 161304.8 | 184936.24 | 200038.48 | 212508.96 | 164809.92 | 171163.76 | 191234.64 | 181865.2 | 160043.52 | 158691.04 | 162637.92 | 156600.48 | 163100.8 | 182870.4 | 170412.48 | 195797.84 | 172848.4 | 181802.96 | 239736.72 | 193410.72 | 167832.32 | 158616.24 | 151638.48 | 173009.88 | 145604.08 | 167482.6 | 163268.2 | 150024.64 | 154229.68
315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 30920 | 42883 | 87000 | 89330 | 74095 | 65520 | 51680 | 65760 | 67200 | 67922 | 67325 | 54118 | 61002 | 47297 | 97209 | 82790 | 74640 | 78640 | 59040 | 75280 | 68445.6 | 81539.28 | 78760.56 | 70425.12 | 83354.24 | 95440.72 | 106644.08 | 90944.4 | 79893.44 | 75534.88 | 61110.24 | 77534.56 | 66657.6 | 76348.8 | 74618.56 | 100114.48 | 92674.8 | 96643.12 | 114833.84 | 95351.84 | 74287.04 | 71859.28 | 63800.56 | 84077.36 | 66297.76 | 75581.2 | 80548.4 | 73478.08 | 82502.96
452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2649.6 | 3444.48 | 4680.96 | 12305.92 | 75868.84 | 94233.52 | 103495.28 | 93234.4 | 90349.04 | 82741.08 | 67491.84 | 96344.96 | 85841.6 | 96620.8 | 94928.96 | 110927.68 | 86316.8 | 107513.92 | 140709.44 | 116877.44 | 96720.64 | 88444.48 | 70200.96 | 106069.76 | 76516.16 | 90139.2 | 97414.4 | 90465.28 | 92359.36
204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 15780.47 | 14844.63 | 15586.66 | 15343 | 13172.29 | 12914.8 | 11564.69 | 14007.85 | 14518.63 | 16018.03 | 16696.88 | 16825.4 | 15269.98 | 15036 | 18239.12 | 15210.66 | 15849.97 | 13144.46 | 7847.46 | 13989.73 | 14719.5 | 17232.4816 | 18638.2484 | 19799.0325 | 15359.0554 | 15950.5038 | 17818.7533 | 16946.6228 | 14915.3845 | 14789.4924 | 12597.1118 | 14489.8107 | 15087.0346 | 16885.8919 | 15705.2025 | 17941.6669 | 15826.806 | 16105.9043 | 21296.4452 | 17214.78 | 14999.8414 | 14213.2466 | 14023.0962 | 15671.5612 | 12939.7978 | 14853.0983 | 14424.6939 | 13218.7814 | 13631.797
315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 2171.15 | 3005.4 | 6059.14 | 6220.42 | 5153.51 | 4559.95 | 4010.19 | 5442.32 | 5560.96 | 5620.45 | 5571.26 | 4483.21 | 5050.33 | 3921.26 | 8033.24 | 6845.34 | 6173.9 | 6503.44 | 4947.92 | 7032.02 | 6267.55 | 7604.4363 | 7345.7837 | 6569.8954 | 7773.3804 | 8898.4197 | 9941.2685 | 8479.8905 | 7451.2315 | 7045.5273 | 4741.0025 | 7186.1608 | 6173.8085 | 7059.0927 | 6888.4709 | 9205.3588 | 8520.2409 | 8598.2021 | 10227.8989 | 8508.3279 | 6649.7124 | 6446.9613 | 5908.2048 | 7624.8998 | 5899.6245 | 6712.9535 | 7134.1322 | 6494.8624 | 7323.4779
452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07 | 392.9622 | 890.9878 | 1979.8021 | 7087.7942 | 8797.3266 | 9659.2982 | 8704.2166 | 8435.684 | 7727.5203 | 5244.5257 | 8933.1385 | 7953.5968 | 8926.5754 | 8747.6766 | 10137.8643 | 7867.493 | 9500.1636 | 12473.9959 | 10394.3221 | 8649.9062 | 7939.7522 | 6503.649 | 9620.539 | 6814.5477 | 8000.3182 | 8603.7338 | 7962.9562 | 8147.895
STEAM
Bldg. # | Building Name | time axis 2010-07-01 to 2014-07-01
204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 519706.6 | 395410.8 | 316161.8 | 308654 | 493012.2 | 947651.2 | 982687.6 | 474659.8 | 401250.2 | 322001.2 | 351198.2 | 274451.8 | 37539 | 404587 | 459644.2 | 527214.4 | 569758.6 | 608966 | 654847 | 620644.8 | 524711.8 | 1393948.2 | 601458.2 | 583105.8 | 642334 | 733261.8 | 677370.4 | 742438 | 886754.6 | 978516.6 | 1117828 | 953490.6 | 797495.2 | 533888 | 681541.4 | 413763.2 | 726588.2 | 731593.4 | 461312.6 | 842542 | 674867.8 | 809174 | 1115325.4 | 682375.6 | 902604.4 | 724919.8 | 504691 | 397913.4 | 470488.8
315 | Cone Residence Hall Steam Use in Lbs. | 41710 | 62565 | 100104 | 153492.8 | 163503.2 | 216892 | 296141 | 200208 | 166840 | 135140.4 | 94264.6 | 101772.4 | 79249 | 165171.6 | 141814 | 164337.4 | 206881.6 | 207048.44 | 208216.32 | 242752.2 | 211052.6 | 160166.4 | 82585.8 | 59228.2 | 65901.8 | 85922.6 | 171011 | 170176.8 | 208550 | 219394.6 | 291970 | 254848.1 | 229405 | 171011 | 145985 | 52554.6 | 59228.2 | 95933 | 132637.8 | 192700.2 | 214389.4 | 207715.8 | 381229.4 | 204379 | 255265.2 | 206881.6 | 81751.6 | 45881 | 58394
452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210652.184 | 60696.392 | 83545.13 | 170660.636 | 189229.928 | 343473.508 | 382747.644 | 356320.188 | 498426.158 | 606463.4 | 623147.4 | 367048 | 385400.4 | 272783.4 | 340353.6 | 437120.8 | 359540.2 | 462981 | 530551.2 | 387068.8 | 846713 | 451302.2 | 542230 | 358706 | 216892 | 246923.2 | 286964.8
204 & 445 | Plemmons Student Union Total Steam Cost | 22867.09 | 17398.08 | 13911.12 | 13580.78 | 21692.54 | 41696.65 | 43238.25 | 20885.04 | 17655.01 | 14168.05 | 15452.72 | 5764.08 | 788.4 | 8497.2 | 9653.52 | 11072.64 | 11966.16 | 12789.6 | 13753.2 | 13034.88 | 11020.08 | 29275.92 | 12631.92 | 12246.48 | 13490.4 | 15400.08 | 14226.24 | 15592.8 | 18623.76 | 20550.96 | 23476.8 | 20025.36 | 16749.12 | 11212.8 | 14313.84 | 8689.92 | 15259.92 | 15365.04 | 9688.56 | 17695.2 | 14173.68 | 16994.4 | 23424.24 | 14331.36 | 18956.64 | 15224.88 | 10599.6 | 8357.04 | 9881.28
315 | Cone Residence Hall Steam Costs | 1835.24 | 2752.86 | 4404.58 | 6753.68 | 7194.14 | 9543.25 | 13030.2 | 8809.15 | 7340.96 | 5946.18 | 4147.64 | 2137.44 | 1664.4 | 3468.96 | 2978.4 | 3451.44 | 4344.96 | 4348.46 | 4372.99 | 5098.32 | 4432.56 | 3363.84 | 1734.48 | 1243.92 | 1384.08 | 1804.56 | 3591.6 | 3574.08 | 4380 | 4607.76 | 6132 | 5352.36 | 4818 | 3591.6 | 3066 | 1103.76 | 1243.92 | 2014.8 | 2785.68 | 4047.12 | 4502.64 | 4362.48 | 8006.64 | 4292.4 | 5361.12 | 4344.96 | 1716.96 | 963.6 | 1226.4
452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4424.15 | 1274.76 | 1754.66 | 3584.31 | 3974.24 | 7213.61 | 8038.46 | 7483.56 | 10467.99 | 14829.71 | 15237.68 | 8975.34 | 9424.1 | 6670.31 | 8322.59 | 10688.82 | 8791.75 | 11321.17 | 12973.44 | 9464.91 | 19687.45 | 11035.59 | 13259.03 | 8771.36 | 5303.61 | 6037.95 | 7017.09
WATER & SEWER
Bldg. # | Building Name | time axis 2010-07-01 to 2014-07-01
204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 227000 | 183000 | 225000 | 344000 | 215000 | 164000 | 101000 | 391000 | 303000 | 172000 | 150000 | 200400 | 209000 | 258000 | 385000 | 387000 | 287000 | 151000 | 196000 | 287000 | 294000 | 310000 | 145000 | 210000 | 278000 | 501000 | 459000 | 439000 | 368000 | 227000 | 500000 | 275000 | 181000 | 279000 | 200000 | 219000 | 244000 | 333000 | 427000 | 475900 | 456359 | 390001 | 507000 | 540918 | 183918 | 228589 | 211785 | 332555.459 | 156555
315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 20000 | 83000 | 139000 | 174000 | 119000 | 108000 | 53000 | 231000 | 190000 | 54000 | 27000 | 6000 | 12000 | 81000 | 174000 | 147000 | 146000 | 93000 | 112000 | 196000 | 164000 | 158000 | 65000 | 18000 | 27000 | 114000 | 166000 | 176000 | 172000 | 77000 | 129000 | 170000 | 133000 | 167000 | 113000 | 86000 | 150000 | 128000 | 190000 | 224300 | 173473 | 80000 | 185000 | 190346 | 140346 | 186283 | 77895 | 33085.173 | 78085
452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5992 | 32528 | 100152 | 205440 | 208008 | 197736 | 89880 | 160072 | 212288 | 172056 | 219136 | 77896 | 11128 | 11128 | 139528 | 218280 | 274768 | 222064 | 95872 | 182328 | 224152 | 172792 | 245264 | 117648 | 78184.368 | 95304
204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 2093.02 | 1370.77 | 1567.19 | 2355.2 | 1751.58 | 1112.4 | 702.32 | 2027.61 | 1806.48 | 1939.76 | 1447.95 | 1348.36 | 1842.05 | 1678.25 | 2296 | 3225.7 | 3158.8 | 2030.4 | 1351.5 | 1658.65 | 2290.3 | 3059.25 | 2194.5 | 2112 | 1325.3 | 2441.1 | 4465.2 | 3722.6 | 3126.7 | 2551.7 | 2913.5 | 2847 | 2453.7 | 2472.6 | 3117.5 | 2551.5 | 3401.1 | 3105.9 | 3993.7 | 4651.87 | 5036.2027 | 5584.5 | 5330.1 | 6721.467 | 3878.967 | 2495.034 | 2707.638 | 4023.6185 | 2575.653
315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 91.64 | 273.77 | 1081.38 | 1295.16 | 1062.99 | 859.46 | 529.02 | 1387.37 | 1148.25 | 1097.17 | 662.24 | 199.4 | 114.9 | 301.5 | 861.15 | 1559.7 | 1444.65 | 1232.2 | 1012.75 | 1203.2 | 1681.8 | 1794.6 | 1224.5 | 535.15 | 221.45 | 602.15 | 1095.55 | 1536.15 | 1584.55 | 1415.95 | 969.05 | 1568.75 | 1608.35 | 1646.05 | 1822.75 | 1223.75 | 1805.75 | 1544.15 | 1671.75 | 2134.24 | 2191.1569 | 1597.75 | 1582.75 | 2376.999 | 2081.999 | 1987.448 | 1603.436 | 599.4195 | 440.441
452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.74 | 100.84 | 2320.58 | 6556.74 | 603.22 | 573.43 | 413.45 | 592.27 | 955.3 | 722.64 | 1604.7 | 1894.11 | 568.17 | 194.27 | 770.52 | 1875.28 | 2525.21 | 2638.7704 | 1900.79 | 1666.76 | 2584.974 | 2497.664 | 2537.948 | 2148.846 | 1009.822 | 633.346
35 | ASU - Summit Living Learning Center | bar: 2010-07-01; 2012-01-01; 2012-04-01
App State - Plemmons, Cone, Summit Utility Data
ELECTRICITY
Bldg. # | Building Name | time axis 2010-07-01 to 2014-07-01
204 & 445 | Plemmons Student Union Total Electricity Use (with 45.9% RUB added) | 227800 | 214280 | 225000 | 221480 | 190120 | 186400 | 149800 | 169880 | 176080 | 194280 | 202520 | 204080 | 185200 | 182360 | 221240 | 184480 | 192240 | 159400 | 93960 | 150160 | 161304.8 | 184936.24 | 200038.48 | 212508.96 | 164809.92 | 171163.76 | 191234.64 | 181865.2 | 160043.52 | 158691.04 | 162637.92 | 156600.48 | 163100.8 | 182870.4 | 170412.48 | 195797.84 | 172848.4 | 181802.96 | 239736.72 | 193410.72 | 167832.32 | 158616.24 | 151638.48 | 173009.88 | 145604.08 | 167482.6 | 163268.2 | 150024.64 | 154229.68
315 | Cone Hall Electricity Use (with 17.3 % RUB added) | 30920 | 42883 | 87000 | 89330 | 74095 | 65520 | 51680 | 65760 | 67200 | 67922 | 67325 | 54118 | 61002 | 47297 | 97209 | 82790 | 74640 | 78640 | 59040 | 75280 | 68445.6 | 81539.28 | 78760.56 | 70425.12 | 83354.24 | 95440.72 | 106644.08 | 90944.4 | 79893.44 | 75534.88 | 61110.24 | 77534.56 | 66657.6 | 76348.8 | 74618.56 | 100114.48 | 92674.8 | 96643.12 | 114833.84 | 95351.84 | 74287.04 | 71859.28 | 63800.56 | 84077.36 | 66297.76 | 75581.2 | 80548.4 | 73478.08 | 82502.96
452 & 453 | Summit Hall and Summit Annex Electricity Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2649.6 | 3444.48 | 4680.96 | 12305.92 | 75868.84 | 94233.52 | 103495.28 | 93234.4 | 90349.04 | 82741.08 | 67491.84 | 96344.96 | 85841.6 | 96620.8 | 94928.96 | 110927.68 | 86316.8 | 107513.92 | 140709.44 | 116877.44 | 96720.64 | 88444.48 | 70200.96 | 106069.76 | 76516.16 | 90139.2 | 97414.4 | 90465.28 | 92359.36
204 & 445 | Plemmons Student Union Total Electricity Cost (with 45.9% RUB added) | 15780.47 | 14844.63 | 15586.66 | 15343 | 13172.29 | 12914.8 | 11564.69 | 14007.85 | 14518.63 | 16018.03 | 16696.88 | 16825.4 | 15269.98 | 15036 | 18239.12 | 15210.66 | 15849.97 | 13144.46 | 7847.46 | 13989.73 | 14719.5 | 17232.4816 | 18638.2484 | 19799.0325 | 15359.0554 | 15950.5038 | 17818.7533 | 16946.6228 | 14915.3845 | 14789.4924 | 12597.1118 | 14489.8107 | 15087.0346 | 16885.8919 | 15705.2025 | 17941.6669 | 15826.806 | 16105.9043 | 21296.4452 | 17214.78 | 14999.8414 | 14213.2466 | 14023.0962 | 15671.5612 | 12939.7978 | 14853.0983 | 14424.6939 | 13218.7814 | 13631.797
315 | Cone Residence Hall Electricity Cost (with 17.3% of RUB added) | 2171.15 | 3005.4 | 6059.14 | 6220.42 | 5153.51 | 4559.95 | 4010.19 | 5442.32 | 5560.96 | 5620.45 | 5571.26 | 4483.21 | 5050.33 | 3921.26 | 8033.24 | 6845.34 | 6173.9 | 6503.44 | 4947.92 | 7032.02 | 6267.55 | 7604.4363 | 7345.7837 | 6569.8954 | 7773.3804 | 8898.4197 | 9941.2685 | 8479.8905 | 7451.2315 | 7045.5273 | 4741.0025 | 7186.1608 | 6173.8085 | 7059.0927 | 6888.4709 | 9205.3588 | 8520.2409 | 8598.2021 | 10227.8989 | 8508.3279 | 6649.7124 | 6446.9613 | 5908.2048 | 7624.8998 | 5899.6245 | 6712.9535 | 7134.1322 | 6494.8624 | 7323.4779
452 & 453 | Summit Hall and Summit Annex Electricity Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07 | 392.9622 | 890.9878 | 1979.8021 | 7087.7942 | 8797.3266 | 9659.2982 | 8704.2166 | 8435.684 | 7727.5203 | 5244.5257 | 8933.1385 | 7953.5968 | 8926.5754 | 8747.6766 | 10137.8643 | 7867.493 | 9500.1636 | 12473.9959 | 10394.3221 | 8649.9062 | 7939.7522 | 6503.649 | 9620.539 | 6814.5477 | 8000.3182 | 8603.7338 | 7962.9562 | 8147.895
STEAM
Bldg. # | Building Name | time axis 2010-07-01 to 2014-07-01
204 & 445 | Plemmons Student Union Total Steam Use in Lbs. | 519706.6 | 395410.8 | 316161.8 | 308654 | 493012.2 | 947651.2 | 982687.6 | 474659.8 | 401250.2 | 322001.2 | 351198.2 | 274451.8 | 37539 | 404587 | 459644.2 | 527214.4 | 569758.6 | 608966 | 654847 | 620644.8 | 524711.8 | 1393948.2 | 601458.2 | 583105.8 | 642334 | 733261.8 | 677370.4 | 742438 | 886754.6 | 978516.6 | 1117828 | 953490.6 | 797495.2 | 533888 | 681541.4 | 413763.2 | 726588.2 | 731593.4 | 461312.6 | 842542 | 674867.8 | 809174 | 1115325.4 | 682375.6 | 902604.4 | 724919.8 | 504691 | 397913.4 | 470488.8
315 | Cone Residence Hall Steam Use in Lbs. | 41710 | 62565 | 100104 | 153492.8 | 163503.2 | 216892 | 296141 | 200208 | 166840 | 135140.4 | 94264.6 | 101772.4 | 79249 | 165171.6 | 141814 | 164337.4 | 206881.6 | 207048.44 | 208216.32 | 242752.2 | 211052.6 | 160166.4 | 82585.8 | 59228.2 | 65901.8 | 85922.6 | 171011 | 170176.8 | 208550 | 219394.6 | 291970 | 254848.1 | 229405 | 171011 | 145985 | 52554.6 | 59228.2 | 95933 | 132637.8 | 192700.2 | 214389.4 | 207715.8 | 381229.4 | 204379 | 255265.2 | 206881.6 | 81751.6 | 45881 | 58394
452 & 453 | Summit Residence Hall and Summit Annex Steam Use in Lbs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210652.184 | 60696.392 | 83545.13 | 170660.636 | 189229.928 | 343473.508 | 382747.644 | 356320.188 | 498426.158 | 606463.4 | 623147.4 | 367048 | 385400.4 | 272783.4 | 340353.6 | 437120.8 | 359540.2 | 462981 | 530551.2 | 387068.8 | 846713 | 451302.2 | 542230 | 358706 | 216892 | 246923.2 | 286964.8
204 & 445 | Plemmons Student Union Total Steam Cost | 22867.09 | 17398.08 | 13911.12 | 13580.78 | 21692.54 | 41696.65 | 43238.25 | 20885.04 | 17655.01 | 14168.05 | 15452.72 | 5764.08 | 788.4 | 8497.2 | 9653.52 | 11072.64 | 11966.16 | 12789.6 | 13753.2 | 13034.88 | 11020.08 | 29275.92 | 12631.92 | 12246.48 | 13490.4 | 15400.08 | 14226.24 | 15592.8 | 18623.76 | 20550.96 | 23476.8 | 20025.36 | 16749.12 | 11212.8 | 14313.84 | 8689.92 | 15259.92 | 15365.04 | 9688.56 | 17695.2 | 14173.68 | 16994.4 | 23424.24 | 14331.36 | 18956.64 | 15224.88 | 10599.6 | 8357.04 | 9881.28
315 | Cone Residence Hall Steam Costs | 1835.24 | 2752.86 | 4404.58 | 6753.68 | 7194.14 | 9543.25 | 13030.2 | 8809.15 | 7340.96 | 5946.18 | 4147.64 | 2137.44 | 1664.4 | 3468.96 | 2978.4 | 3451.44 | 4344.96 | 4348.46 | 4372.99 | 5098.32 | 4432.56 | 3363.84 | 1734.48 | 1243.92 | 1384.08 | 1804.56 | 3591.6 | 3574.08 | 4380 | 4607.76 | 6132 | 5352.36 | 4818 | 3591.6 | 3066 | 1103.76 | 1243.92 | 2014.8 | 2785.68 | 4047.12 | 4502.64 | 4362.48 | 8006.64 | 4292.4 | 5361.12 | 4344.96 | 1716.96 | 963.6 | 1226.4
452 & 453 | Summit Residence Hall and Summit Annex Steam Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4424.15 | 1274.76 | 1754.66 | 3584.31 | 3974.24 | 7213.61 | 8038.46 | 7483.56 | 10467.99 | 14829.71 | 15237.68 | 8975.34 | 9424.1 | 6670.31 | 8322.59 | 10688.82 | 8791.75 | 11321.17 | 12973.44 | 9464.91 | 19687.45 | 11035.59 | 13259.03 | 8771.36 | 5303.61 | 6037.95 | 7017.09
WATER & SEWER
Bldg. # | Building Name | time axis 2010-07-01 to 2014-07-01
204 & 445 | Plemmons Student Union Water Use (with 45.9% RUB added) | 227000 | 183000 | 225000 | 344000 | 215000 | 164000 | 101000 | 391000 | 303000 | 172000 | 150000 | 200400 | 209000 | 258000 | 385000 | 387000 | 287000 | 151000 | 196000 | 287000 | 294000 | 310000 | 145000 | 210000 | 278000 | 501000 | 459000 | 439000 | 368000 | 227000 | 500000 | 275000 | 181000 | 279000 | 200000 | 219000 | 244000 | 333000 | 427000 | 475900 | 456359 | 390001 | 507000 | 540918 | 183918 | 228589 | 211785 | 332555.459 | 156555
315 | Cone Residence Hall Water Use (with 17.3% RUB added) | 20000 | 83000 | 139000 | 174000 | 119000 | 108000 | 53000 | 231000 | 190000 | 54000 | 27000 | 6000 | 12000 | 81000 | 174000 | 147000 | 146000 | 93000 | 112000 | 196000 | 164000 | 158000 | 65000 | 18000 | 27000 | 114000 | 166000 | 176000 | 172000 | 77000 | 129000 | 170000 | 133000 | 167000 | 113000 | 86000 | 150000 | 128000 | 190000 | 224300 | 173473 | 80000 | 185000 | 190346 | 140346 | 186283 | 77895 | 33085.173 | 78085
452 & 453 | Summit Residence Hall and Summit Annex Water Use (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5992 | 32528 | 100152 | 205440 | 208008 | 197736 | 89880 | 160072 | 212288 | 172056 | 219136 | 77896 | 11128 | 11128 | 139528 | 218280 | 274768 | 222064 | 95872 | 182328 | 224152 | 172792 | 245264 | 117648 | 78184.368 | 95304
204 & 445 | Plemmons Student Union Total Water & Sewer Cost (with 45.9% RUB added) | 2093.02 | 1370.77 | 1567.19 | 2355.2 | 1751.58 | 1112.4 | 702.32 | 2027.61 | 1806.48 | 1939.76 | 1447.95 | 1348.36 | 1842.05 | 1678.25 | 2296 | 3225.7 | 3158.8 | 2030.4 | 1351.5 | 1658.65 | 2290.3 | 3059.25 | 2194.5 | 2112 | 1325.3 | 2441.1 | 4465.2 | 3722.6 | 3126.7 | 2551.7 | 2913.5 | 2847 | 2453.7 | 2472.6 | 3117.5 | 2551.5 | 3401.1 | 3105.9 | 3993.7 | 4651.87 | 5036.2027 | 5584.5 | 5330.1 | 6721.467 | 3878.967 | 2495.034 | 2707.638 | 4023.6185 | 2575.653
315 | Cone Hall Water & Sewer Cost (with 17.3% RUB added) | 91.64 | 273.77 | 1081.38 | 1295.16 | 1062.99 | 859.46 | 529.02 | 1387.37 | 1148.25 | 1097.17 | 662.24 | 199.4 | 114.9 | 301.5 | 861.15 | 1559.7 | 1444.65 | 1232.2 | 1012.75 | 1203.2 | 1681.8 | 1794.6 | 1224.5 | 535.15 | 221.45 | 602.15 | 1095.55 | 1536.15 | 1584.55 | 1415.95 | 969.05 | 1568.75 | 1608.35 | 1646.05 | 1822.75 | 1223.75 | 1805.75 | 1544.15 | 1671.75 | 2134.24 | 2191.1569 | 1597.75 | 1582.75 | 2376.999 | 2081.999 | 1987.448 | 1603.436 | 599.4195 | 440.441
452 & 453 | Summit Residence Hall and Summit Annex Water & Sewer Cost (with 36.8% RUB added) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.74 | 100.84 | 2320.58 | 6556.74 | 603.22 | 573.43 | 413.45 | 592.27 | 955.3 | 722.64 | 1604.7 | 1894.11 | 568.17 | 194.27 | 770.52 | 1875.28 | 2525.21 | 2638.7704 | 1900.79 | 1666.76 | 2584.974 | 2497.664 | 2537.948 | 2148.846 | 1009.822 | 633.346
36 | UNCW - MARBIONC | bar: 2010-07-01 to 2011-07-01; 2011-10-01 to 2012-02-01
MARBIONIC FACILITY | 2013-07-09 | 2013-08-09 | 2013-09-09 | 2013-10-09 | 2013-11-09 | 2013-12-09 | 2014-01-09 | 2014-02-09 | 2014-03-09 | 2014-04-09 | 2014-05-09 | 2014-06-09 | TOTAL YTD
ELECTRIC
KWH |  | 0 | 271000 | 257600 | 248800 | 232400 | 217000 | 188400 | 237000 | 238000 | 322800 | 334000 | 2547000
DEMAND |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 702 | 1280
COST |  | 17.51 | 23490.26 | 21781.91 | 21124.71 | 19507.65 | 18410.8 | 16373.78 | 19835.29 | 19906.51 | 26005.39 | 25641.94 | 212095.75
GAS
MCF |  | 705 | 423.4 | 510.3 | 755.6 | 1098.6 | 1300.4 | 1061.6 | 383.5 | 713 | 697.4 | 642.9 | 8291.7
COST |  | 6474.16 | 3897.67 | 4973.81 | 7089.77 | 10403.16 | 12397.04 | 9757.84 | 7047.09 | 6044.15 | 6028.34 | 5710.61 | 79823.64
WATER
METER READING |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PREVIOUS READING |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GAL CHANGE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COST/GAL |  | 0.0037 | 0.0037 | 0.0036 | 0.0036 | 0.0037 | 0.0037 | 0.0038 | 0.0038 | 0.0037 | 0.0037 | 0.0039
COST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEWAGE
COST/GAL |  | 0.005 | 0.005 | 0.0047 | 0.0047 | 0.0045 | 0.0045 | 0.0043 | 0.0043 | 0.0044 | 0.0044 | 0.0046
COST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2013-07-09 to 2014-06-09
TOTAL UTILITIES |  | 6491.67 | 27387.93 | 26755.72 | 28214.48 | 29910.81 | 30807.84 | 26131.62 | 26882.38 | 25950.66 | 32033.73 | 31352.55 | 291919.39
= | bar: 2013-07-09 to 2014-06-09
TOTAL TRASH |  | 0 | 256.49 | 256.49 | 256.49 | 236.76 | 236.76 | 236.76 | 256.49 | 236.76 | 256.49 | 256.49 | 2485.98
MARBIONC - 25%
ELECTRIC |  | 4.38 | 5872.57 | 5445.48 | 5281.18 | 4876.91 | 4602.7 | 4093.45 | 4958.82 | 4976.63 | 6501.35 | 6410.49 | 53023.96
GAS |  | 1618.54 | 974.42 | 1243.45 | 1772.44 | 2600.79 | 3099.26 | 2439.46 | 1761.77 | 1511.04 | 1507.09 | 1427.65 | 19955.91
WATER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEWER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2013-07-09 to 2013-08-09; 2013-10-09 to 2014-06-09
TOTAL UTILITIES |  | 1622.92 | 6846.99 | 6688.93 | 7053.62 | 7477.7 | 7701.96 | 6532.91 | 6720.59 | 6487.67 | 8008.44 | 7838.14 | 72979.87
= | bar: 2013-07-09 to 2013-08-09; 2013-10-09 to 2014-06-09
TRASH |  | 0 | 64.12 | 64.12 | 64.12 | 59.19 | 59.19 | 59.19 | 64.12 | 59.19 | 64.12 | 64.12 | 621.48
UNCW - 75%
ELECTRIC |  | 13.13 | 17617.7 | 16336.43 | 15843.53 | 14630.74 | 13808.1 | 12280.34 | 14876.47 | 14929.88 | 19504.04 | 19231.46 | 159071.82
GAS |  | 4855.62 | 2923.25 | 3730.36 | 5317.33 | 7802.37 | 9297.78 | 7318.38 | 5285.32 | 4533.11 | 4521.26 | 4282.96 | 59867.74
WATER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEWER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | bar: 2013-07-09 to 2013-08-09; 2013-10-09 to 2014-06-09
TOTAL UTILITIES |  | 4868.75 | 20540.95 | 20066.79 | 21160.86 | 22433.11 | 23105.88 | 19598.72 | 20161.79 | 19462.99 | 24025.3 | 23514.42 | 218939.56
= | bar: 2013-07-09 to 2014-06-09
TRASH |  | 0 | 192.37 | 192.37 | 192.37 | 177.57 | 177.57 | 177.57 | 192.37 | 177.57 | 192.37 | 192.37 | 1864.5
Aug electric is for new service charge only. No water, sewer or trash charges yet.
No water or sewer charges. No water meter at the facility and awaiting information about how to charge for water and sewer.
TOTAL UTILITIES | 0 | 4855.625 | 3243.865 | 4050.9747 | 5637.9447 | 8098.3245 | 9593.7345 | 7614.3343 | 5605.9343 | 4829.0644 | 4841.8744 | 4603.5746 | 62975.2504
= | bar: 2013-07-09 to 2014-06-09
TRASH
BASIC SERVICE | 39.456 | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 512.976
EXTRA PICK UP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.73 | 0 | 0 | 0 | 0 | 19.73
- | bar: 2013-07-09 to 2014-06-09
TOTAL TRASH | 39.456 | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 59.19 | 39.46 | 59.19 | 39.46 | 39.46 | 532.706
= | bar: 2013-07-09 to 2014-06-09
Gross Sqft: 69644
Net Sqft: 65721
Dec. estimated water. Meter was under water and could not read.
Mar. estimated water. Meter was under water and could not read.
Jul usage 6/21/13-8/1/13 | 2013-07-09: Sep usage 9/3/13-10/1/13; 2013-09-09: Nov usage 11/14/13-12/2/13; 2013-11-09: Jan usage 1/3/14-2/3/14; 2014-01-09: Mar usage 3/3/14-4/1/14; 2014-03-09: May usage 5/1/14-5/28/14
Aug usage 8/1/13-9/3/13 | 2013-07-09: Oct usage 10/1/13-11/14/13; 2013-09-09: Dec usage 12/2/13-1/3/14; 2013-11-09: Feb usage 2/3/14-3/3/14; 2014-01-09: Apr usage 4/1/14-5/1/14; 2014-03-09: Jun usage 5/28/14-7/1/14
CHILLED WATER
TON_HR | 166225 | 167925 | 129275 | 102217 | 47075 | 42608 | 25117 | 20575 | 44867 | 74842 | 112958 | 149900
COST (SF based calculation)
HEATING HOT WATER | 328600 | 319000 | 251800 | 339700 | 596800 | 877900 | 10008000 | 593200 | 644700 | 327800 | 293200 | 315801
MBTU
COST (SF based calculation)
37 | 2013-07-09: DOA - NC State Bar HQ
The North Carolina State Bar-Electricity and Water Usage 5/2013 thru 9/2014
Utility | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-01
Electricity Usage (KWhs) | 106000 | 95400 | 89400 | 77200 | 67000 | 69200 | 82600 | 78200 | 73400 | 81800 | 69800 | 74800 | 76400 | 65400 | 62600 | 75400 | 72000
Water Usage (CCF) | 17 | 14 | 15 | 16 | 22 | 20 | 21 | 17 | 13 | 20 | 19 | 18 | 19 | 16 | 27 | 23 | 22
Elecricity Cost ($) | 8606.91 | 9907.79 | 7575.88 | 6633 | 5764.64 | 5997.1 | 7048.17 | 6695.62 | 6475.23 | 7165.66 | 6044.77 | 6288.27 | 6432.95 | 5628.77 | 5526.73 | 6463.28 | 6206.95
Water-Sewer Costs ($) | 139.69 | 120.57 | 178.72 | 185.57 | 226.64 | 212.95 | 219.79 | 192.41 | 165.03 | 212.95 | 210.2 | 211.56 | 218.4 | 197.87 | 304.75 | 276.69 | 269.68
38 | 2013-07-09: FSU - Science and Technology Building
39 | 2013-07-09: UNCW - Student Rec Facility Addition
RECREATION CENTER | 2013-07-09 | 2013-08-09 | 2013-09-09 | 2013-10-09 | 2013-11-09 | 2013-12-09 | 2014-01-09 | 2014-02-09 | 2014-03-09 | 2014-04-09 | 2014-05-09 | 2014-06-09 | TOTAL YTD
ELECTRIC
METER READING | 24625 | 24782 | 24925 | 25136 | 25212 | 25341 | 25473 | 25598 | 25732 | 25878 | 26004 | 26173
PREVIOUS READING | 24429 | 24625 | 24782 | 24925 | 25136 | 25212 | 25341 | 25473 | 25598 | 25732 | 25878 | 26004
CHANGE | 196 | 157 | 143 | 211 | 76 | 129 | 132 | 125 | 134 | 146 | 126 | 169
KWH (CHANGE X1000) | 196000 | 157000 | 143000 | 211000 | 76000 | 129000 | 132000 | 125000 | 134000 | 146000 | 126000 | 169000 | 1744000
COST/KWH | 0.08 | 0.0847 | 0.0799 | 0.074 | 0.0705 | 0.0742 | 0.0707 | 0.0756 | 0.0726 | 0.0706 | 0.0696 | 0.0813 | 0.0758
COST | 15680 | 13297.9 | 11425.7 | 15614 | 5358 | 9571.8 | 9332.4 | 9450 | 9728.4 | 10307.6 | 8769.6 | 13739.7 | 132275.1
GAS
METER READING | 11486 | 11506 | 11532 | 11567 | 11578 | 11592 | 11618 | 11650 | 11675 | 11709 | 11723 | 11744
PREVIOUS READING | 11464 | 11486 | 11506 | 11532 | 11567 | 11578 | 11592 | 11618 | 11650 | 11675 | 11709 | 11723
MCF CHANGE | 22 | 20 | 26 | 35 | 11 | 14 | 26 | 32 | 25 | 34 | 14 | 21 | 280
COST/MCF | 5.39 | 5.14 | 5.21 | 5.03 | 5.46 | 5.7 | 6.14 | 7.48 | 6.33 | 5.85 | 6.15 | 5.94 | 5.86
COST | 118.58 | 102.8 | 135.46 | 176.05 | 60.06 | 79.8 | 159.64 | 239.36 | 158.25 | 198.9 | 86.1 | 124.74 | 1639.74
WATER
METER READING | 31716400 | 31792400 | 31926800 | 32120500 | 32169000 | 32264000 | 32333300 | 32461100 | 32664100 | 32702500 | 32776100 | 32858900
PREVIOUS READING | 31691400 | 31716400 | 31792400 | 31926800 | 32120500 | 32169000 | 32264000 | 32333300 | 32461100 | 32664100 | 32702500 | 32776100
CHANGE IN GAL | 25000 | 76000 | 134400 | 193700 | 48500 | 95000 | 69300 | 127800 | 203000 | 38400 | 73600 | 82800 | #REF!
COST/GAL | 0.0037 | 0.0037 | 0.0037 | 0.0036 | 0.0036 | 0.0037 | 0.0037 | 0.0038 | 0.0038 | 0.0037 | 0.0037 | 0.0039 | #REF!
COST | 92.5 | 281.2 | 497.28 | 697.32 | 174.6 | 351.5 | 256.41 | 485.64 | 771.4 | 142.08 | 272.32 | 322.92 | 4345.17
SEWAGE
COST/GAL | 0.0046 | 0.005 | 0.005 | 0.0047 | 0.0047 | 0.0045 | 0.0045 | 0.0043 | 0.0043 | 0.0044 | 0.0044 | 0.0046 | #REF!
COST | 115 | 380 | 672 | 910.39 | 227.95 | 427.5 | 311.85 | 549.54 | 872.9 | 168.96 | 323.84 | 380.88 | 5340.81
FUEL OIL
GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.2 | 0 | 0 | 0 | 0 | 62.2
COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.72 | 0 | 0 | 0 | 0 | 210.72
- | bar: 2013-07-09 to 2014-06-09
CHILLED WATER
TON_HR | 166225 | 167925 | 129275 | 102217 | 47075 | 42608 | 25117 | 20575 | 44867 | 74842 | 112958 | 149900 | 1083584
COST (SF based calculation) | 16008 | 14362 | 8271 | 7801 | 1814 | 3336 | 2530 | 2243 | 2486 | 5389 | 5703 | 12696 | 82639
HEATING HOT WATER
MBTU | 328600 | 319000 | 251800 | 339700 | 596800 | 877900 | 10008000 | 593200 | 644700 | 327800 | 293200 | 315801 | 14896501
COST (SF based calculation) | 1828 | 1544 | 1208 | 2422 | 1567 | 3248 | 2711 | 3327 | 2821 | 1789 | 1578 | 1924 | 25967
TOTAL UTILITIES | 33842.08 | 29967.9 | 22209.44 | 27620.76 | 9201.61 | 17014.6 | 15301.3 | 16505.26 | 16837.95 | 17995.54 | 16732.86 | 29188.24 | 252417.54
= | bar: 2013-07-09 to 2014-06-09
TRASH
BASIC SERVICE | 39.456 | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 512.976
EXTRA PICK UP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.73 | 0 | 0 | 0 | 0 | 19.73
- | bar: 2013-07-09 to 2014-06-09
TOTAL TRASH | 39.456 | 39.46 | 39.46 | 59.19 | 39.46 | 39.46 | 39.46 | 59.19 | 39.46 | 59.19 | 39.46 | 39.46 | 532.706
= | bar: 2013-07-09 to 2014-06-09
Gross Sqft: 69644
Net Sqft: 65721
Dec. estimated water. Meter was under water and could not read.
Mar. estimated water. Meter was under water and could not read.
Jul usage 6/21/13-8/1/13 | 2013-07-09: Sep usage 9/3/13-10/1/13; 2013-09-09: Nov usage 11/14/13-12/2/13; 2013-11-09: Jan usage 1/3/14-2/3/14; 2014-01-09: Mar usage 3/3/14-4/1/14; 2014-03-09: May usage 5/1/14-5/28/14
Aug usage 8/1/13-9/3/13 | 2013-07-09: Oct usage 10/1/13-11/14/13; 2013-09-09: Dec usage 12/2/13-1/3/14; 2013-11-09: Feb usage 2/3/14-3/3/14; 2014-01-09: Apr usage 4/1/14-5/1/14; 2014-03-09: Jun usage 5/28/14-7/1/14
CHILLED WATER
TON_HR | 166225 | 167925 | 129275 | 102217 | 47075 | 42608 | 25117 | 20575 | 44867 | 74842 | 112958 | 149900
COST (SF based calculation)
HEATING HOT WATER | 328600 | 319000 | 251800 | 339700 | 596800 | 877900 | 10008000 | 593200 | 644700 | 327800 | 293200 | 315801
MBTU
COST (SF based calculation)
40 | 2013-07-09: WSSU - Reaves Student Activities Center
Winston-Salem State University - Donald J. Reaves Student Activities Center (06-07181-01A)
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity Usage (Prorated by GSF) (KWH) | 151265.4862 | 160590.071 | 144457.0593 | 125807.8897 | 113819.1379 | 103014.4603 | 121367.6113 | 106566.6831 | 120479.5556 | 123587.7505 | 138388.6787 | 154373.6812 | 152005.5326 | 164734.3309
| Natural Gas (therms-prorated by GSF) for Steam Generation | 4256.8407 | 4722.49 | 4849.2352 | 5621.7063 | 8284.6067 | 9198.3225 | 10961.5066 | 9524.727 | 10187.2855 | 7054.9861 | 4238.3414 | 4485.9155 | 4407.3351 | 4609.7442
| Natural Gas (Other) | 114 | 118 | 307 | 340 | 412 | 2094 | 1802 | 1176 | 903 | 1012 | 881 | 324 | 283 | 678
| Water Usage (gallons) | 41890.8 | 11362.8795 | 24850.221 | 91479.0345 | 66987.8775 | 22404.0975 | 93760.587 | 93184.5885 | 62185.3965 | 95832.6855 | 22493.8635 | 21850.5405 | 9747.0915 | 74617.9875
| Elecricity Cost ($) (Prorated by GSF) | 10835.3747 | 11766.4687 | 10554.2845 | 7913.7332 | 7299.0547 | 6490.4562 | 7579.7297 | 7021.3441 | 7629.1442 | 7864.7182 | 9521.0548 | 11935.943 | 11603.9277 | 12774.3448
| Prorated Natural Gas for Steam Costs ($) | 2238.4588 | 2348.8855 | 2460.0488 | 2782.3234 | 4471.4077 | 5180.1537 | 6460.6775 | 6728.5291 | 6080.235 | 4188.1283 | 2661.0513 | 2609.6057 | 2469.0235 | 2305.1888
| Natural Gas Cost (Other) | 107.8792 | 111.6645 | 290.5169 | 321.7451 | 389.8793 | 1958.65 | 1710.31 | 1089.45 | 765.71 | 854.38 | 807.61 | 319.6 | 282.14 | 601.01
| Water-Sewer Costs ($) | 404.39 | 167.8 | 260.32 | 826.98 | 618.54 | 282.63 | 827.71 | 750.55 | 570.96 | 861.08 | 263.41 | 278.3 | 163.58 | 684.94
41 | 2013-07-09: UNCC - Belk Residence Hall
Belk Residence Hall | 2013-08-09: 10-08450-02A
|  |  | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun
Consumption
Electric (KWH) |  |  | 163324 | 175940 | 215472 | 177599 | 155770 | 138580 | 148199 | 131000 | 153381 | 161007 | 160801 | 37260
Nat Gas (Therms) |  |  | 2134 | 2912 | 3806 | 3609 | 4632 | 5855 | 6585 | 5964 | 5972 | 3972 | 1376 | 268
Water (CF) |  |  | 14673.7968 | 64347.5936 | 97355.615 | 40498.6631 | 42875.6684 | 54553.4759 | 59014.7059 | 62072.1925 | 74533.4225 | 62820.8556 | 21835.5615 | 6530.7487
Costs $
Electric |  |  | 10914.9671 | 11676.0378 | 14552.2661 | 10762.5167 | 8944.2066 | 8089.144 | 8492.5478 | 7637.8066 | 9087.397 | 9153.1177 | 9283.0281 | 2416.7619
Nat Gas |  |  | 1942.16 | 2641.33 | 3444.74 | 3267.71 | 4321.62 | 5413.39 | 6168.68 | 5504.48 | 5110.77 | 3259.05 | 1219.61 | 262.65
Water |  |  | 1256.7939 | 4887.4235 | 7233.6021 | 3155.6367 | 3396.0193 | 4740.5033 | 4066.1627 | 5148.8732 | 5141.8203 | 4566.6246 | 1624.664 | 495.7607
42 | NCSU - Cherry Building Renovation
NCSU - Early College High School/Cherry
| Utility |  |  |  |  | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 |  | Total | Units
| Electric (kWh) |  |  |  |  | 19200 | 12120 | 13440 | 20280 | 24960 | 26520 | 26160 | 15240 | 15120 | 14280 | 11280 | 14219.29 | 13560 |  | 226379.29 | kwh
| Water (CCF) |  |  |  |  | 0 | 2 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 11 | CCF
| Electric Cost ($) |  |  |  |  | 1451.38 | 945.06 | 1123.35 | 1527.15 | 1714.14 | 1839.47 | 1873.1 | 1184.81 | 1193.87 | 1052.54 | 1080.61 | 736.23 | 1071.77 |  | 16793.48 | $
| Water Cost ($) |  |  |  |  | 48.83 | 116.33 | 48.83 | 55.665 | 104.495 | 48.83 | 55.665 | 55.665 | 55.665 | 55.665 | 55.665 | 55.665 | 55.665 |  | 812.635 | $
43 | UNCC - Hunt Residence Hall | bar: 2014-08-01
Hunt Residence Hall |  | 10-08610-03A
|  |  | Jul 13 | Aug 13 | Sep 13 | Oct 13 | Nov 13 | Dec 13 | Jan 14 | Feb 14 | Mar 14 | Apr 14 | May 14 | Jun 14
Consumption
Electric (KWH) |  |  | 62719 | 135317 | 83282 | 75172 | 106109 | 86868 | 82705 | 91894 | 91196 | 96122 | 77072 | 63855
Nat Gas (Therms) |  |  | 100 | 281 | 690 | 675 | 783 | 617 | 821 | 1211 | 907 | 1007 | 613 | 125
Water (CF) |  |  | 1999 | 25635 | 50734 | 35367 | 39687 | 16640 | 38589 | 35870 | 30818 | 26888 | 22548 | 2485
Costs $
Electric |  |  | 4191.52 | 8980.1433 | 5624.5908 | 4555.4305 | 6092.706 | 5070.6289 | 4739.4123 | 5357.7756 | 5403.109 | 5464.4579 | 4449.36 | 4141.7696
Nat Gas |  |  | 113.07 | 276.93 | 644.48 | 631.01 | 750.81 | 592.3 | 790.46 | 1137.14 | 796.9 | 844.47 | 556.86 | 134
Water |  |  | 171.2121 | 1947.0674 | 3769.5778 | 2755.7799 | 3143.4569 | 1445.9569 | 2658.8145 | 2975.4077 | 2126.0344 | 1954.5643 | 1677.6727 | 188.6407
For this reporting period Hunt Hall was the only building connected to RUP 4
All costs associated with RUP4 were assigned to Hunt Hall
RUP 4
|  |  | Jul 13 | Aug 13 | Sep 13 | Oct 13 | Nov 13 | Dec 13 | Jan 14 | Feb 14 | Mar 14 | Apr 14 | May 14 | Jun 14
Consumption
Electric (KWH) |  |  | 68260 | 100193 | 42411 | 47279 | 32134 | 34367 | 30431 | 29943 | 32510 | 41846 | 60551 | 81591
Nat Gas (Therms) |  |  | 4395 | 2624 | 3702 | 3797 | 5182 | 6851 | 8615 | 7688 | 6823 | 5657 | 5944 | 7918
Water (CF) |  |  | 11841 | 11101 | 19915 | 3684 | 6915 | 1799 | 1980 | 2209 | 2775 | 11714 | 17125 | 24294
Costs $
Electric |  |  | 4561.8259 | 6649.183 | 2864.2987 | 2865.112 | 1845.1123 | 2006.0587 | 1743.8493 | 1745.7927 | 1926.1269 | 2378.9112 | 3495.6041 | 5292.1638
Nat Gas |  |  | 3974.06 | 2382.51 | 3351.28 | 3436.65 | 4831.87 | 6330.11 | 8062.81 | 7088.6 | 5835.57 | 4631.26 | 5187.41 | 7063.42
Water |  |  | 1014.1681 | 843.1596 | 1479.7008 | 287.0555 | 547.711 | 156.3267 | 136.4237 | 183.236 | 191.4383 | 851.5236 | 1274.1771 | 1844.2004
44 | NCSU - Wolf Ridge 6 | bar: 2014-08-01
NCSU - Wolf Ridge Building 6
| Utility |  |  |  |  | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 |  | Total | Units
| Electric (kWh) |  |  |  |  | 44583.3417 | 42479.1701 | 41397.0032 | 37326.004 | 34498.9929 | 36833.0078 | 38876.0071 | 38966.98 | 38203.0029 | 36464.0198 | 37791 | 37184 | 38392 |  | 502994.5296 | kwh
| Chilled Water (Dtherms) |  |  |  |  | 315.5308 | 235.0539 | 103.2827 | 74.8926 | 8.2824 | 14 | 18 | 26 | 84 | 161 | 305 | 332 | 286 |  | 1963.0423 | dthrms
| Steam (1,000 lbs) |  |  |  | * | 57.4639 | 69.8354 | 102.9491 | 203.1206 | 277.7183 | 376.1128 | 265.0368 | 261.3553 | 91.1047 | 47.6145 | 43.78 | 50.9 | 25.23 |  | 1872.2212 | 1000 lbs
| Water (CCF) |  |  |  |  | 119 | 187 | 159 | 125 | 178 | 116 | 125 | 79 | 88 | 53 | 68 | 54 | 62 |  | 1413 | CCF
| Electric Cost ($) |  |  |  |  | 3878.7507 | 3695.6878 | 3601.5393 | 3247.3624 | 3001.4124 | 3204.4717 | 3382.2126 | 3390.1273 | 3323.6613 | 3172.3697 | 3287.817 | 3235.008 | 3340.104 |  | 43760.5241 | $
| Chilled Water Cost ($) |  |  |  |  | 4325.9268 | 3222.5889 | 1416.006 | 1026.7769 | 113.5511 | 191.94 | 246.78 | 356.46 | 1151.64 | 2207.31 | 4181.55 | 4780.8 | 4118.4 |  | 27339.7297 | $
| Steam Cost ($) |  |  |  | * | NA | NA | NA | NA | NA | 5423.5465 | 3821.8309 | 3768.743 | 1313.7296 | NA | 631.3076 | 705.983 | 349.9401 |  | 16015.0807 | $
| Water Cost ($) |  |  |  |  | 779.45 | 1224.85 | 1041.45 | 818.75 | 1165.9 | 759.8 | 818.75 | 517.45 | 576.4 | 347.15 | 445.4 | 424.44 | 487.32 |  | 9407.11 | $
* Steam data does not include domestic hot water. Data was unavailable.
45 | NCSU - Wolf Ridge 1 | bar: 2014-08-01
NCSU - Wolf Ridge Building 1
| Utility |  |  |  |  | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 |  | Total | Units
| Electric (kWh) |  |  |  |  | 157530.2898 | 151838.6459 | 151949.9969 | 135144.989 | 130012.9547 | 137597.1069 | 144941.0095 | 144964.9353 | 139818.0542 | 135489.9902 | 131695.9229 | 131431.0303 | 136429.0771 |  | 1828844.0029 | kwh
| Chilled Water (Dtherms) |  |  |  |  | 1488.6334 | 650.1258 | 416.5971 | 263.3448 | 122 | 96 | 102 | 157 | 341 | 668 | 978 | 1035 | 976 |  | 7293.7011 | dthrms
| Steam (1,000 lbs) |  |  |  | * | 120.6742 | 146.6543 | 216.1931 | 426.5532 | 583.2083 | 1383.7269 | 1169.2073 | 639.135 | 321.8167 | 211.4602 | 157 | 169 | 175 |  | 5719.6292 | 1000 lbs
| Water (CCF) |  |  |  |  | 155 | 190 | 215 | 255 | 170 | 185 | 255 | 195 | 215 | 90 | 110 | 105 | 190 |  | 2330 | CCF
| Electric Cost ($) |  |  |  |  | 13705.1352 | 13209.9622 | 13219.6497 | 11757.614 | 11311.1271 | 11970.9483 | 12609.8678 | 12611.9494 | 12164.1707 | 11787.6292 | 11457.5453 | 11434.4996 | 11869.3297 |  | 159109.4282 | $
| Chilled Water Cost ($) |  |  |  |  | 20409.1646 | 8913.2248 | 5711.5456 | 3610.4575 | 1672.62 | 1316.16 | 1398.42 | 2152.47 | 4675.11 | 9158.28 | 13408.38 | 14904 | 14054.4 |  | 101384.2325 | $
| Steam Cost ($) |  |  |  | * | 1740.1216 | 2114.7549 | 3117.5045 | 6150.8967 | 8409.8644 | 19953.3414 | 16859.9695 | 9216.3266 | 4640.5971 | 3049.2559 | 2263.94 | 2344.03 | 2427.25 |  | 82287.8525 | $
| Water Cost ($) |  |  |  |  | 1015.25 | 1244.5 | 1408.25 | 1670.25 | 1113.5 | 1211.75 | 1670.25 | 1277.25 | 1408.25 | 589.5 | 720.5 | 825.3 | 1493.4 |  | 15647.95 | $
* Steam data does not include domestic hot water. Data was unavailable.
46 | UNCG - Spartan Village 1 - Lee | bar: 2014-08-01
| Lee Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | 21300 | 18000 | 86700 | 102600 | 109500 | 1113400 | 84000 | 70500 | 64333 | 47264 | 43754 | 44155 | 51376
| Water Usage (gallons) | N/A | 175032 | 228888 | 210188 | 229636 | 73304 | 187748 | 222156 | 201960 | 246840 | 12716 | 1496 | 33660
| Natural Gas (Therms) | 99 | 564 | 531 | 642 | 616 | 421 | 865 | 660 | 711 | 665 | 98 | 109 | 122
| Electricity Cost ($) | 1602.01 | 1741.78 | 6531.34 | 7798.48 | 8591.68 | 8739.82 | 6881.85 | 6905.76 | 5660.98 | 4615.49 | 4401.47 | 4446.56 | 4890.97
| Water Costs ($) | N/A | 1956.28 | 2351.56 | 2214.31 | 2357.05 | 1209.64 | 2049.61 | 2302.15 | 2153.92 | 2483.32 | 764.95 | 708.98 | 954.95
| Natural Gas Cost ($) | 112.15 | 531.25 | 501.6 | 626.82 | 590.24 | 415.76 | 1245.33 | 188.72 | 607.86 | 584.78 | 110.3 | 123.14 | 135.02
47 | UNCG - Spartan Village 3 - Haywood
| Haywood Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | 49500 | 92700 | 61800 | 42300 | 61500 | 78900 | 63600 | 50100 | 39000 | 27035 | 26613 | 27287 | 32916
| Water Usage (gallons) | N/A | 75548 | 89760 | 86020 | 80784 | 18700 | 71060 | 80036 | 60588 | 63580 | 3740 | 2244 | 2992
| Natural Gas (Therms) | 70 | 312 | 299 | 375 | 331 | 259 | 482 | 329 | 364 | 318 | 378 | 346 | 195
| Electricity Cost ($) | 3557.69 | 6668.52 | 4453.19 | 3480.48 | 4810.01 | 6102.75 | 5018.61 | 4548.76 | 3405.03 | 2672.6 | 2646.87 | 2700.47 | 3046.58
| Water Costs ($) | N/A | 1226.11 | 1330.42 | 1302.97 | 1264.54 | 808.87 | 1193.17 | 1259.05 | 1116.31 | 1138.27 | 699.07 | 714.69 | 720.84
| Natural Gas Cost ($) | 85.75 | 304.79 | 293.11 | 376.29 | 328.45 | 265.16 | 472.82 | 312.15 | 325.25 | 292.37 | 360.44 | 339.7 | 201.73
48 | UNCG - Spartan Village 4
| Union Residence Hall | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity (KWhs) | N/A | N/A | 4380 | 46500 | 54900 | 68700 | 57300 | 48000 | 46395 | 34365 | 29364 | 31741 | 39247
| Water Usage (gallons) | N/A | 139128 | 178772 | 166056 | 158576 | 37400 | 155584 | 168300 | 142120 | 143616 | 748 | 1496 | 14212
| Natural Gas (Therms) | 68 | 475 | 461 | 554 | 531 | 373 | 812 | 494 | 617 | 546 | 88 | 126 | 119
| Electricity Cost ($) | N/A | N/A | 4056.36 | 4231.61 | 4800.03 | 5553.53 | 4831.13 | 4896.78 | 4151.6 | 3414.67 | 3080.44 | 3260.39 | 3731.22
| Water Costs ($) | N/A | 1692.76 | 1983.73 | 1890.4 | 1835.5 | 946.12 | 1813.54 | 1906.87 | 1714.72 | 1725.7 | 721.03 | 708.98 | 806.49
| Natural Gas Cost ($) | 83.93 | 451.27 | 438.69 | 544.25 | 512.17 | 371.14 | 779.07 | 456.45 | 533.64 | 484.5 | 101.29 | 138.67 | 132.27
49 | WSSU - Martin-Schexnider Residence Hall | bar: 2013-08-01
Winston-Salem State University - Martin-Schexnider Residence Hall (11-09099-02A)
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity Usage (Prorated by GSF) (KWH) |  |  | 83895.2233 | 73064.4875 | 66101.8716 | 59826.9215 | 70485.7408 | 61889.9188 | 69969.9915 | 71775.1142 | 80370.9362 | 89654.424 | 88279.0925 | 95671.4995
| Natural Gas (therms - prorated by GSF) for Steam Generation |  |  | 2816.2533 | 3264.8755 | 4811.3878 | 5342.0395 | 6366.0305 | 5531.603 | 5916.392 | 4097.2704 | 2461.4692 | 2605.2509 | 2559.6144 | 2677.1659
| Water Usage (gallons) |  |  | 16838.6055 | 7278.5265 | 3523.3155 | 2842.59 | 156132.996 | 178754.028 | 118296.627 | 210561.114 | 17145.306 | 161758.332 | 193146.51 | 309356.0775
| Elecricity Cost ($) (Prorated by GSF) |  |  | 6129.5312 | 4595.9984 | 4239.0163 | 3769.4127 | 4402.0217 | 4077.7324 | 4430.7198 | 4567.5324 | 5529.4703 | 6931.9464 | 6739.1245 | 7418.8587
| Prorated Natural Gas Costs for Steam ($) |  |  | 1428.7038 | 1615.8687 | 2596.8253 | 3008.4383 | 3752.1183 | 3907.6765 | 3531.1717 | 2432.3073 | 1545.4384 | 1515.5608 | 1433.9159 | 1338.7669
| Water-Sewer Costs ($) |  |  | 508.7 | 273.03 | 214.46 | 131.19 | 1306.76 | 1154.74 | 1010.44 | 1646.17 | 221.52 | 1351.49 | 1518.96 | 2226.02
50 | Cape Fear Community College - Union Station
51 | ECU - Smith-Williams Center | bar: 2013-08-01
East Carolina University - Smith-Williams Center Energy & Water Use
| Utility | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01
| Electricity Usage (KWhs) | [5 empty] | 49565 | 35870 | 26238 | 36303 | 32906 | 35271 | 33773 | 44401 | 25329
| Natural Gas Usage (CCF) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Steam Usage (lbs)
Water Usage (gallons)
| Elecricity Cost ($) | [5 empty] | 4659.11 | 3371.78 | 2466.372 | 3412.482 | 3093.164 | 3315.474 | 3174.662 | 4173.694 | 2380.926
Steam Costs ($)
Water-Sewer Costs ($)

## 12.13 Meter Data
2012/2013 Meter Data Summary
ASU - Cone Residence Hall Renovation
Utility | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 |  |  | Total | Units | Total | Units
Electricity (KWhs) | 70400 | 79760 | 91600 | 80080 | 75520 | 74400 | 59920 | 75680 | 64720 | 71920 | 67920 | 84240 |  |  | 896160 | kwhs | 2816.6309 | MMbtu
Steam (lbs) | 25026 | 37539 | 50886.2 | 170176.8 | 252762.6 | 201876.4 | 303648.8 | 283628 | 257767.8 | 179353 | 98435.6 | 12513 |  |  | 1873613.2 | lbs | 1873.6132 | MMbtu
Water (gallons) | 18000 | 27000 | 114000 | 166000 | 176000 | 172000 | 77000 | 129000 | 170000 | 133000 | 167000 | 113000 |  |  | 1462000 | gallons | 1462000 | gallons
Elecricity Cost ($) | 6565.42 | 7436.67 | 8538.78 | 7466.46 | 7042 | 6937.75 | 4651.43 | 7020.97 | 6001.44 | 6667.72 | 6297.56 | 7807.78 |  |  | 82433.98 |  | 82433.98
Steam Costs ($) | 1384.08 | 1804.56 | 3591.6 | 3574.08 | 4380 | 4607.76 | 6132 | 5352.36 | 4818 | 3591.6 | 3066 | 1103.76 |  |  | 43405.8 |  | 43405.8
125839.78
NCCU - Chidley North Residence Hall
Utility |  |  | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | Total | Units | Total | Units
Electricity (KWhs) |  |  | 192858 | 139482 | 138822 | 111327 | 71743 | 107158 | 86119 | 109632 | 124337 | 111701 | 166836 | 197374 | 1557389 | kwhs | 4894.8736 | MMbtu
Steam (lbs) |  | * | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | 0 | lbs | 2757 | ***MMbtu
Natural Gas (Therms) |  |  | 0 | 0 | 0 | 0 | 0 | 8 | 29 | 0 | 0 | 158 | 280 | 299 | 774 | therms | 77.3815 | MMbtu
Water (gallons) |  | ** | 10629 | 17430 | 13248 | 17123 | 3067 | 14609 | 93783 | 97231.5 | 100680 | 5521 | 121632 | 193313 | 688266.5 | gallons | 688266.5 | gallons
Elecricity Cost ($) |  |  | 13885.78 | 9484.78 | 8329.32 | 6568.29 | 4448.07 | 6429.48 | 5253.26 | 6687.55 | 7584.56 | 6702.06 | 12345.86 | 11823 | 99542.01 |  | 99542.01
Steam Costs ($) |  | * | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data |  | No data
Natural Gas ( $) |  |  | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 24.82 | 29 | 17.5 | 0 | 158 | 291.38 | 309.81 | 918.01 |  | 918.01
|  | * Steam data is not available. Meter calibration/operation issues. | [14 empty] | 100460.02
|  | **April water data is an average of March and May | [15 empty] | *** Modeled Steam Data
NCSU - Student Health Center Addition and Renovation
Utility |  | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 |  | Total | Units | Total | Units
Electric (kWh) |  | 58922 | 64433 | 27834 | 43379 | 52554 | 65640 | 42990 | 64258 | 68459 | 59732 | 31392 | 60060 |  | 639653 | kwh | 2010.4294 | MMbtu
Chilled Water (Dtherms) |  | 606.81 | 560.77 | 299.08 | 141.46 | 129.51 | 135.82 | 154.11 | 97.66 | 268.74 | 331.86 | 715.98 | 1017.16 |  | 4458.96 | dthrms | 4458.96 | MMbtu
Steam (1,000 lbs) | * | 25.08 | 25 | 67.5 | 158 | 364 | 464 | 125.83 | 489 | 451 | 178.33 | 174 | 174 |  | 2695.74 | 1000 lbs | 2695.74 | MMbtu
Water (CF) |  | 2917.67 | 1691.9 | 3271.34 | 2003.71 | 4794.52 | 1859.64 | 2031.25 | 3090.73 | 2363.03 | 959.48 | 2798.29 | 3467.83 |  | 31249.39 | CF | 233745.4372 | gallons
Electric Cost ($) |  | 4949.45 | 5412.37 | 2338.06 | 3643.84 | 4414.54 | 5513.76 | 3611.16 | 5397.67 | 5750.56 | 5017.49 | 2636.93 | 5225.22 |  | 53911.05 |  | 53911.05
Chilled Water Cost ($) |  | 8325.43 | 7693.76 | 4103.38 | 1940.83 | 1776.88 | 1863.45 | 2114.39 | 1339.9 | 3687.11 | 4553.12 | 9823.25 | 13945.26 |  | 61166.76 |  | 61166.76
Steam Cost ($) | * | 345 | 344 | 930.87 | 2183.37 | 5019.56 | 6398.56 | 1735.2 | 6743.31 | 6219.29 | 2459.17 | 2401.8 | 2511.53 |  | 37291.66 |  | 37291.66
| * Steam data is questionable. Meter calibration/operation issues. | [15 empty] | 152369.47
UNCC - Prospector Hall Renovation Phase II
Utility |  | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 |  | Total | Units | Total | Units
Electricity (KWhs) |  | 80189 | 41330 | 69306 | 72328 | 34592 | 56617 | 36235 | 56903 | 71169 | 66909 | 62812 | 63690 |  | 712080 | kwhs | 2238.0674 | MMbtu
Nat Gas (Therms) |  | 1162 | 1964 | 1936 | 2482 | 1934 | 2089 | 3239 | 2957 | 3699 | 2544 | 1462 | 1239 |  | 26707 | therms | 2670.0624 | MMbtu
Water Usage (CF) |  | 86730 | 25380 | 42300 | 16160 | 3131 | 13750 | 12902 | 14330 | 22060 | 5960 | 12210 | 7650 |  | 262563 | CF | 1963971.24 | gallons
Elecricity Cost ($) |  | 5408.3346 | 2785.1918 | 4156.1595 | 4034.1956 | 1951.4847 | 3201.9714 | 2067.006 | 3295.5937 | 4031.8882 | 3737.8323 | 3975.6598 | 4256.4121 |  | 42901.7298 |  | 42901.7298
Nat Gas Costs ($) |  | 362.87 | 1528.27 | 1506.83 | 2173.01 | 1729.56 | 1863.85 | 2697.22 | 2402.16 | 2780.23 | 2216.75 | 1338.26 | 1137.86 |  | 21736.87 |  | 21736.87
64638.5998
UNCC - Miltimore Residence Hall
Utility |  | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 |  | Total | Units | Total | Units
Electricity (KWhs) |  | 191805 | 83027 | 74038 | 153854.8 | 125895.2 | 158940 | 94338 | 127579 | 149201 | 150041 | 165852 | 217457 |  | 1692028 | kwhs | 5318.044 | MMbtu
Nat Gas (Therms) |  | 3419 | 3804 | 3546 | 4091 | 4203 | 6054 | 7674 | 6875 | 5399 | 3005 | 3130 | 3277 |  | 54477 | therms | 5446.3993 | MMbtu
Water Usage (CF) |  | 80504.8 | 53768 | 104464 | 48863 | 43098 | 66001 | 40038 | 54450 | 62052 | 30982 | 81030 | 23765 |  | 689015.8 | CF | 5153838.184 | gallons
Elecricity Cost ($) |  | 12936.2583 | 5595.1153 | 4439.9293 | 8581.4671 | 7102.2941 | 8988.8431 | 5381.4602 | 7388.8645 | 8452.5813 | 8381.9531 | 10497.5343 | 14532.6835 |  | 102278.9841 |  | 102278.9841
Nat Gas Costs ($) |  | 2557.45 | 2821.99 | 2756.36 | 3581.7 | 3729.23 | 5400.26 | 6370.93 | 5370.34 | 4061.04 | 2618.45 | 2699.4 | 2815.15 |  | 44782.3 |  | 44782.3
147061.2841
UNCC - EPIC
Utility |  | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 |  | Total | Units | Total | Units
Electricity (KWhs) |  | 396280 | 337140 | 393790 | 395750 | 330230 | 360480 | 347280 | 359070 | 332600 | 400060 | 405050 | 360773 |  | 4418503 | kwhs | 13887.3549 | MMbtu
Nat Gas (Therms) |  | 118 | 181 | 587 | 3335 | 2316 | 3598 | 5093 | 5112 | 4113 | 906 | 535 | 499 |  | 26393 | therms | 2638.6699 | MMbtu
Water Usage (CF) |  | 2260 | 3480 | 2044 | 2770 | 210 | 460 | 380 | 590 | 300 | 379 | 260 | 6260 |  | 19393 | CF | 145059.64 | gallons
Elecricity Cost ($) |  | 26727.0428 | 22719.5633 | 23614.8972 | 22073.5108 | 18629.7061 | 20386.927 | 19810.3999 | 20795.8956 | 18842.5582 | 22349.119 | 25637.4737 | 24110.5129 |  | 265697.6066 |  | 265697.6066
Nat Gas Costs ($) |  | 36.85 | 140.84 | 456.87 | 2919.82 | 2071.18 | 3210.21 | 4241.11 | 4152.8 | 3091.4 | 789.46 | 489.72 | 458.27 |  | 22058.53 |  | 22058.53
287756.1366
Pitt CC - Russell Classroom Building
Utility |  | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 |  | Total | Units | Total | Units
Electricity (KWhs) | * | 72384 | 61248 | 67008 | 65000 | 62784 | 57792 | 50205 | 55872 | 62784 | 67008 | 61248 | 72384 |  | 755717 | kwhs | 2375.2185 | MMbtu
Gas Usage (CCF) | ** | 470.5 | 167 | 463 | 1528 | 2113 | 2787 | 2470 | 2289 | 1954 | 1445 | 985 | 774 |  | 17445.5 | CCF | 1791.6528 | MMbtu
Water (gallons) CCF? | * | 34.73 | 41.97 | 39.06 | 43.42 | 31.83 | 8.66 | 52.09 | 41.97 | 41.97 | 34.73 | 11.57 | 13.02 |  | 395.02 | CCF | 295474.96 | gallons
Elecricity Cost ($) | * | 3567.08 | 3018.3 | 3302.15 | 3203.2 | 3094 | 2847.99 | 2474.25 | 2753.37 | 3094 | 3302.15 | 3018.3 | 3567.08 |  | 37241.87 |  | 37241.87
Gas Cost ($) | ** | 497.195 | 189.8 | 472.53 | 1343.94 | 1926.01 | 2582.16 | 2301.64 | 2141.48 | 1846.07 | 1397.47 | 990.42 | 804.59 |  | 16493.305 |  | 16493.305
| * Meter data not available. Aug through Dec data estimated by lwt. | [15 empty] | 53735.175
**August gas estimated as average of Sep 12 and Jul 13 by lwt
WCU - Harrill Residence Hall Renovation
Utility |  |  | 2012-09-01 | 2012-10-01 | Nov-12 | Dec-12 | Jan-13 | Feb-13 | Mar-13 | Apr-13 | May-13 | Jun-13 | Jul-13 | Aug-13 | Total | Units | Total | Units
Electricity (KWhs) |  | * | 62414 | 70687 | 77990 | 67997 | 74994 | 86154 | 70687 | 45568 | 62414 | 64758 | 63102 | 65657 | 812422 | kwhs | 2553.4423 | MMbtu
Water (gallons) |  | * | 121000 | 121000 | 100000 | 75000 | 80000 | 121000 | 100000 | 121000 | 72000 | 26000 | 20000 | 112000 | 1069000 | gallons | 1069000 | gallons
Elecricity Cost ($) |  | * | 3617.44 | 4022.8 | 4528.1 | 4031.24 | 4392.6 | 4998.03 | 4022.8 | 2660.66 | 3617.44 | 4626.72 | 4393.66 | 4571.6969 | 49483.1869 |  | 49483.1869
* Meter data not available. Sep through Jan data estimated by lwt.
UNCG - Bailey Residence Hall Renovation
Utility |  |  | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | Total | Units | Total | Units
Electricity (KWhs) |  |  | 27314 | 25544 | 24015 | 22868 | 23105 | 23733 | 27737 | 26171 | 20858 | 15845 | 17235 | 25624 | 280049 | kwhs | 880.194 | MMbtu
Steam Usage (lbs) |  |  | 14185 | 18300 | 19250 | 17900 | 11890 | 141540 | 32580 | 22660 | 7410 | 4190 | 4430 | 10070 | 304405 | lbs | 304.405 | MMbtu
Chilled water (ton-hrs) |  |  | 24100 | 25800 | 6300 | 8700 | 6800 | 7100 | 8800 | 15000 | 17000 | 20000 | 24000 | 26000 | 189600 | ton-hrs | 2275.2 | MMbtu
Water Usage (gallons) |  |  | 59000 | 52500 | 41800 | 18800 | 38400 | 48900 | 42800 | 48800 | 12500 | 900 | 500 | 38300 | 403200 | gallons | 403200 | gallons
Electricity Cost ($) |  |  | 1978.29 | 1669.48 | 1379.69 | 1402.35 | 1447.58 | 1445.74 | 1720.97 | 1579.63 | 1250.45 | 1069.96 | 1240.86 | 1819.24 | 18004.24 |  | 18004.24
Steam Cost ($) |  |  | 110.835 | 142.99 | 150.41 | 139.86 | 92.9 | 1105.93 | 254.56 | 177.05 | 57.9 | 32.74 | 34.62 | 78.68 | 2267.64 |  | 2267.64
Chilled Water ($) |  |  | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data |  |  | 20271.88
UNCG Coit Residence Hall Renovation
Utility |  |  | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | Total | Units | Total | Units
Electricity (KWhs) |  |  | 26275 | 25135 | 23402 | 23069 | 23260 | 23590 | 25880 | 26283 | 19119 | 15390 | 16654 | 24291 | 272348 | kwhs | 855.9898 | MMbtu
Steam Usage (lbs) |  |  | 32640 | 55500 | 59890 | 100570 | 91070 | 68930 | 135630 | 76900 | 36950 | 3850 | 4080 | 9780 | 675790 | lbs | 675.79 | MMbtu
Chilled water (ton-hrs) |  |  | 11000 | 28000 | 12000 | 14000 | 10000 | 9000 | 12000 | 15000 | 14000 | 20000 | 25000 | 25000 | 195000 | ton-hrs | 2340 | MMbtu
Water Usage (gallons) |  |  | 60900 | 53000 | 44200 | 22000 | 39500 | 50000 | 44700 | 57000 | 14300 | 700 | 400 | 34000 | 420700 | gallons | 420700 | gallons
Electricity Cost ($) |  |  | 1903.04 | 1642.95 | 1334.47 | 1414.68 | 1457.3 | 1437.03 | 1605.75 | 1586.39 | 1146.19 | 1039.24 | 1199.03 | 1724.6 | 17490.67 |  | 17490.67
Steam Cost ($) |  |  | 255.035 | 433.65 | 467.95 | 785.81 | 711.58 | 538.59 | 1059.75 | 600.86 | 288.71 | 30.08 | 31.88 | 76.42 | 5025.28 |  | 5025.28
Chilled Water ($) |  |  | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data |  |  | 22515.95
22515.95
UNCG Cotten Residence Hall Renovation
Utility |  |  | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | Total | Units | Total | Units
Electricity (KWhs) |  |  | 27684 | 26216 | 24877 | 24731 | 23302 | 22299 | 27461 | 26587 | 19537 | 17126 | 18528 | 25985 | 284333 | kwhs | 893.6586 | MMbtu
Steam Usage (lbs) |  |  | 65785 | 114060 | 230110 | 248900 | 234570 | 200880 | 249800 | 58670 | 13340 | 7550 | 7720 | 17510 | 1448895 | lbs | 1448.895 | MMbtu
Chilled water (ton-hrs) |  |  | 14100 | 26100 | 10800 | 12500 | 7900 | 6600 | 10200 | 1400 | 11200 | 13700 | 16500 | 20100 | 151100 | ton-hrs | 1813.2 | MMbtu
Water Usage (gallons) |  |  | 57500 | 48700 | 42000 | 21600 | 36800 | 46600 | 45600 | 50700 | 11600 | 1300 | 300 | 41400 | 404100 | gallons | 404100 | gallons
Electricity Cost ($) |  |  | 2005.09 | 1713.4 | 1429.21 | 1516.6 | 1459.93 | 1358.38 | 1703.84 | 1604.74 | 1171.25 | 1156.47 | 1333.95 | 1844.87 | 18297.73 |  | 18297.73
Steam Cost ($) |  |  | 514.015 | 891.21 | 1797.97 | 1944.79 | 1832.82 | 1569.58 | 1951.82 | 458.42 | 104.23 | 58.99 | 60.32 | 136.82 | 10806.97 |  | 10806.97
Chilled Water ($) |  |  | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data |  |  | 29104.7
29104.7
UNCG Gray Residence Hall Renovation
Utility |  |  | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | Total | Units | Total | Units
Electricity (KWhs) |  |  | 27754 | 25834 | 24168 | 24141 | 23146 | 24026 | 27725 | 27357 | 21502 | 17073 | 19805 | 27005 | 289536 | kwhs | 910.0116 | MMbtu
Steam Usage (lbs) |  |  | 51560 | 92800 | 117770 | 136210 | 137600 | 148740 | 154340 | 36400 | 8490 | 4260 | 8090 | 10320 | 906580 | lbs | 906.58 | MMbtu
Chilled water (ton-hrs) |  |  | 18000 | 11000 | 8000 | 6000 | 7000 | 6000 | 6000 | 9000 | 13000 | 16000 | 18000 | 22000 | 140000 | ton-hrs | 1680 | MMbtu
Water Usage (gallons) |  |  | 60200 | 52100 | 44700 | 22500 | 42300 | 51800 | 45000 | 54700 | 13000 | 700 | 700 | 36500 | 424200 | gallons | 424200 | gallons
Electricity Cost ($) |  |  | 2010.16 | 1688.44 | 1484.19 | 1584.24 | 1618.56 | 1573.72 | 1602.89 | 1559.29 | 1548.76 | 1744.49 | 1859.95 | 1834.15 | 20108.84 |  | 20108.84
Steam Cost ($) |  |  | 402.87 | 725.1 | 920.2 | 1064.28 | 1075.14 | 1162.18 | 1205.94 | 284.41 | 66.34 | 33.29 | 63.21 | 80.64 | 6680.73 |  | 6680.73
Chilled Water ($) |  |  | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data |  |  | 26789.57
26789.57
UNCG Hinshaw Residence Hall Renovation
Utility |  |  | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | Total | Units | Total | Units
Electricity (KWhs) |  |  | 31337 | 29489 | 27971 | 28908 | 26763 | 27672 | 31291 | 30512 | 25464 | 19405 | 21420 | 30854 | 331086 | kwhs | 1040.6033 | MMbtu
Steam Usage (lbs) |  |  | 51560 | 92800 | 96840 | 125400 | 125050 | 151390 | 144990 | 184780 | 10300 | 7640 | 8030 | 15530 | 1014310 | lbs | 1014.31 | MMbtu
Chilled water (ton-hrs) |  |  | 21000 | 12200 | 9100 | 9100 | 18900 | 7300 | 9900 | 13500 | 13900 | 15800 | 19300 | 26100 | 176100 | ton-hrs | 2113.2 | MMbtu
Water Usage (gallons) |  |  | 41350 | 46900 | 39800 | 19400 | 32000 | 42400 | 37400 | 45600 | 12100 | 2600 | 2800 | 35800 | 358150 | gallons | 358150 | gallons
Electricity Cost ($) |  |  | 2269.67 | 1927.32 | 1606.96 | 1772.75 | 1676.77 | 1685.69 | 1941.48 | 1841.64 | 1526.58 | 1310.36 | 1542.16 | 2190.56 | 21291.94 |  | 21291.94
Steam Cost ($) |  |  | 402.87 | 725.1 | 756.66 | 979.82 | 977.08 | 1182.89 | 1132.88 | 1443.78 | 80.48 | 59.7 | 62.74 | 121.34 | 7522.47 |  | 7522.47
Chilled Water ($) |  |  | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data |  |  | 28814.41
28814.41
UNCG Jamison Residence Hall Renovation
Utility |  |  | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | Total | Units | Total | Units
Electricity (KWhs) |  |  | 27770 | 26421 | 25025 | 25443 | 20716 | 25336 | 23549 | 26961 | 22441 | 18315 | 18909 | 27052 | 287938 | kwhs | 904.9891 | MMbtu
Steam Usage (lbs) |  |  | 14185 | 18300 | 19250 | 21780 | 22750 | 50090 | 28480 | 16650 | 9890 | 6550 | 6880 | 13410 | 228215 | lbs | 228.215 | MMbtu
Chilled water (ton-hrs) |  |  | 11000 | 30000 | 4000 | 5000 | 3000 | 4000 | 4000 | 6000 | 7000 | 7000 | 9000 | 8000 | 98000 | ton-hrs | 1176 | MMbtu
Water Usage (gallons) |  |  | 56100 | 49300 | 43000 | 22800 | 34600 | 46300 | 41900 | 48700 | 12100 | 600 | 900 | 32800 | 389100 | gallons | 389100 | gallons
Electricity Cost ($) |  |  | 2011.32 | 1726.8 | 1437.71 | 1560.26 | 1297.91 | 1543.39 | 1461.12 | 1627.31 | 1345.35 | 1236.76 | 1361.38 | 1920.63 | 18529.94 |  | 18529.94
Steam Cost ($) |  |  | 110.835 | 142.99 | 150.41 | 170.18 | 177.76 | 391.38 | 222.53 | 130.1 | 77.28 | 51.18 | 53.75 | 104.78 | 1672.34 |  | 1672.34
Chilled Water ($) |  |  | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data |  |  | 20202.28
20202.28
UNCG Shaw Residence Hall Renovation
Utility |  |  | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | Total | Units | Total | Units
Electricity (KWhs) |  |  | 52787 | 47182 | 41178 | 42583 | 39584 | 41946 | 52401 | 49958 | 41964 | 32814 | 35588 | 48804 | 526789 | kwhs | 1655.6978 | MMbtu
Steam Usage (lbs) |  |  | 198280 | 391020 | 332710 | 435580 | 410910 | 609370 | 925610 | 197840 | 63070 | 7700 | 3820 | 5540 | 3581450 | lbs | 3581.45 | MMbtu
Chilled water (ton-hrs) |  |  | 45000 | 10600 | 23700 | 27400 | 20100 | 22100 | 28200 | 32700 | 38200 | 39400 | 41900 | 49900 | 379200 | ton-hrs | 4550.4 | MMbtu
Water Usage (gallons) |  |  | 92800 | 82500 | 69400 | 36900 | 64000 | 79100 | 77500 | 90900 | 22000 | 2700 | 2700 | 60400 | 680900 | gallons | 680900 | gallons
Electricity Cost ($) |  |  | 3823.24 | 3083.68 | 2365.72 | 2611.35 | 2480.03 | 2555.21 | 3251.26 | 3015.36 | 2515.76 | 2215.83 | 2562.2 | 3464.97 | 33944.61 |  | 33944.61
Steam Cost ($) |  |  | 1549.265 | 3055.25 | 2599.64 | 3403.42 | 3210.66 | 4761.33 | 7232.28 | 1545.83 | 492.8 | 60.16 | 29.85 | 43.28 | 26434.5 |  | 26434.5
Chilled Water ($) |  |  | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data |  |  | 60379.11
60379.11
UNCA - Overlook Residence Hall
Utility |  |  | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | Total | Units | Total | Units
Electricity (KWhs) |  |  | 133296 | 119403 | 112577 | 71941 | 114723 | 108426 | 101057 | 112318 | 116347 | 109347 | 127593 | 138924 | 1365952 | kwhs | 4293.1871 | MMbtu
Water Usage (gallons) |  |  | 169796 | 193732 | 121924 | 7480 | 264792 | 235620 | 211684 | 234872 | 20944 | 44880 | 56100 | 176528 | 1738352 | gallons | 1738352 | gallons
Elecricity Cost ($) |  |  | 10594.22 | 9143.86 | 8779.23 | 5616.48 | 9381.54 | 8335.41 | 7833.73 | 8409.23 | 9199.07 | 8724.42 | 10207.72 | 10828.03 | 107052.94 |  | 107052.94
UNCP Health Science Builidng
Utility | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 |  |  | Total | Units | Total | Units
Electricity (KWhs) | 85778.96 | 113621.46 | 152143.24 | 180402.2 | 114532.16 | 95786.24 | 90504.5062 | 111469.9 | 86489.4 | 99097.3 | 111892.5 | 111500 |  |  | 1353217.8662 | kwhs | 4253.1638 | MMbtu
Nat Gas (Therms) | 2102 | 2784 | 3728 | 4420 | 2806 | 2347 | 2217 | 2731 | 2119 | 2428 | 2741 | 2732 |  |  | 33155 | therms | 3314.7084 | MMbtu
Water (gallons) | 4632 | 6135 | 8215 | 9741 | 6184 | 5172 | 4887 | 6019 | 4670 | 5351 | 6042 | 6021 |  |  | 73069 | gallons | 73069 | gallons
Electricity Cost ($) | 6927.5088 | 9176.0691 | 12287.0881 | 14569.2817 | 9249.6172 | 7735.6967 | 7309.1439 | 9002.3091 | 6984.8839 | 8003.0979 | 9036.4383 | 9004.74 |  |  | 102358.3661 |  | 102358.3661
Nat Gas Costs ($) | 844.1632 | 1118.0544 | 1497.1648 | 1775.072 | 1126.8896 | 942.5552 | 890.3472 | 1096.7696 | 850.9904 | 975.0848 | 1100.7856 | 1097.1712 |  |  | 12470.8848 |  | 12470.8848
114829.2509
ECSU - Viking Tower
Utility | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 |  |  | Total | Units | Total | Units
Electricity Usage (KWhs) | 47081 | 30708 | 65943 | 66790 | 53679 | 46195 | 47003 | 49174 | 48672 | 56553 | 53063 | 47081 |  |  | 611942 | kwhs | 1923.3337 | MMbtu
Water Usage (gallons) | 8967 | 139932 | 165960 | 181700 | 181700 | 181700 | 110600 | 174615 | 106988 | 194743 | 103497 | 8967 |  |  | 1559369 | gallons | 1559369 | gallons
Elecricity Cost ($) | 5065.92 | 3239.65 | 7029.52 | 6819.22 | 5625.51 | 4905.87 | 5052.83 | 5217.33 | 5134.88 | 5887.15 | 5709.58 | 5065.92 |  |  | 64753.38 |  | 64753.38 |  | 0.10582
ECSU - Gilchrist Ed & Psych Bldg
Utility | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 |  |  | Total | Units | Total | Units
Electricity Usage (KWhs) | 54336 | 58368 | 53952 | 53376 | 45888 | 48576 | 46848 | 58752 | 55296 | 53376 | 50304 | 52800 |  |  | 631872 | kwhs | 1985.9737 | MMbtu
Water Usage (gallons) | 4943.65 | 6841.98 | 6520.6 | 6752.78 | 5081.9 | 2234.21 | 3043.51 | 4648 | 3766.27 | 6580.2 | 4356.57 | 5399.32 |  |  | 60168.99 | gallons | 60168.99 | gallons
Elecricity Cost ($) | 6578.89 | 7712.48 | 6939.67 | 6326.58 | 5448.14 | 5286.63 | 5312.63 | 7388.65 | 6443.39 | 6751.35 | 6442.57 | 6710.76 |  |  | 77341.74 |  | 77341.74 |  | 0.1224
NCSU - Student Health Center Addition and Renovation
Utility |  | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 |  | Total | Units | Total | Units
Electric (kWh) |  | 58922 | 64433 | 27834 | 43379 | 52554 | 65640 | 42990 | 64258 | 68459 | 59732 | 31392 | 60060 |  | 639653 | kwh | 2010.4294 | Mbtu
Chilled Water (Dtherms) |  | 606.81 | 560.77 | 299.08 | 141.46 | 129.51 | 135.82 | 154.11 | 97.66 | 268.74 | 331.86 | 715.98 | 1017.16 |  | 4458.96 | dthrms | 4458.96 | Mbtu
Steam (1,000 lbs) | * | 25.08 | 25 | 67.5 | 158 | 364 | 464 | 125.83 | 489 | 451 | 178.33 | 174 | 174 |  | 2695.74 | 1000 lbs | 2695.74 | Mbtu | 9165.1294
Water (CF) |  | 2917.67 | 1691.9 | 3271.34 | 2003.71 | 4794.52 | 1859.64 | 2031.25 | 3090.73 | 2363.03 | 959.48 | 2798.29 | 3467.83 |  | 31249.39 | CF | 233745.4372 | gallons
Electric Cost ($) |  | 4949.45 | 5412.37 | 2338.06 | 3643.84 | 4414.54 | 5513.76 | 3611.16 | 5397.67 | 5750.56 | 5017.49 | 2636.93 | 5225.22 |  | 53911.05 |  | 53911.05
Chilled Water Cost ($) |  | 8325.43 | 7693.76 | 4103.38 | 1940.83 | 1776.88 | 1863.45 | 2114.39 | 1339.9 | 3687.11 | 4553.12 | 9823.25 | 13945.26 |  | 61166.76 |  | 61166.76
Steam Cost ($) | * | 345 | 344 | 930.87 | 2183.37 | 5019.56 | 6398.56 | 1735.2 | 6743.31 | 6219.29 | 2459.17 | 2401.8 | 2511.53 |  | 37291.66 |  | 37291.66
| * Steam data is questionable. Meter calibration/operation issues. | [15 empty] | 152369.47

## 12.13 Raw Meter
UNCG QUAD
Bailey | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01
Electricity (KWhs) | 20647 | 27314 | 25544 | 24015 | 22868 | 23105 | 23733 | 27737 | 26171 | 20858 | 15845 | 17235 | 25624
Steam Usage (lbs) | No Data | No Data | 18300 | 19250 | 17900 | 11890 | 141540 | 32580 | 22660 | 7410 | 4190 | 4430 | 10070
Water Usage (gallons) | 75800 | 59000 | 52500 | 41800 | 18800 | 38400 | 48900 | 42800 | 48800 | 12500 | 900 | 500 | 38300
Chilled water (ton-hrs) | No Data | 24100 | 25800 | 6300 | 8700 | 6800 | 7100 | 8800 | 15000 | 17000 | 20000 | 24000 | 26000
Electricity Cost ($) | 1492.33 | 1978.29 | 1669.48 | 1379.69 | 1402.35 | 1447.58 | 1445.74 | 1720.97 | 1579.63 | 1250.45 | 1069.96 | 1240.86 | 1819.24
Water Cost ($) | 533.15 | 414.05 | 368.43 | 293.34 | 131.93 | 269.48 | 343.17 | 303.02 | 345.5 | 88.5 | 6.37 | 3.54 | 271.16
Steam Cost ($) | No Data | No Data | 142.99 | 150.41 | 139.86 | 92.9 | 1105.93 | 254.56 | 177.05 | 57.9 | 32.74 | 34.62 | 78.68
Coit | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01
Electricity (KWhs) | 20088 | 26275 | 25135 | 23402 | 23069 | 23260 | 23590 | 25880 | 26283 | 19119 | 15390 | 16654 | 24291
Steam Usage (lbs) | No Data | No Data | 55500 | 59890 | 100570 | 91070 | 68930 | 135630 | 76900 | 36950 | 3850 | 4080 | 9780
Water Usage (gallons) | 30532 | 60900 | 53000 | 44200 | 22000 | 39500 | 50000 | 44700 | 57000 | 14300 | 700 | 400 | 34000
Chilled water (ton-hrs) | No Data | 11000 | 28000 | 12000 | 14000 | 10000 | 9000 | 12000 | 15000 | 14000 | 20000 | 25000 | 25000
Electricity Cost ($) | 1451.93 | 1903.04 | 1642.95 | 1334.47 | 1414.68 | 1457.3 | 1437.03 | 1605.75 | 1586.39 | 1146.19 | 1039.24 | 1199.03 | 1724.6
Water Costs ($) | 214.27 | 427.38 | 371.94 | 310.19 | 154.39 | 277.2 | 350.89 | 316.48 | 403.56 | 101.24 | 4.96 | 2.83 | 240.72
Steam Cost ($) | No Data | No Data | 433.65 | 467.95 | 785.81 | 711.58 | 538.59 | 1059.75 | 600.86 | 288.71 | 30.08 | 31.88 | 76.42
Cotten | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01
Electricity (KWhs) | 22137 | 27684 | 26216 | 24877 | 24731 | 23302 | 22299 | 27461 | 26587 | 19537 | 17126 | 18528 | 25985
Steam Usage (lbs) | No Data | No Data | 114060 | 230110 | 248900 | 234570 | 200880 | 249800 | 58670 | 13340 | 7550 | 7720 | 17510
Water Usage (gallons) | 89495 | 57500 | 48700 | 42000 | 21600 | 36800 | 46600 | 45600 | 50700 | 11600 | 1300 | 300 | 41400
Chilled water (ton-hrs) | N/A | 14100 | 26100 | 10800 | 12500 | 7900 | 6600 | 10200 | 1400 | 11200 | 13700 | 16500 | 20100
Electricity Cost ($) | 1600.03 | 2005.09 | 1713.4 | 1429.21 | 1516.6 | 1459.93 | 1358.38 | 1703.84 | 1604.74 | 1171.25 | 1156.47 | 1333.95 | 1844.87
Water Costs ($) | 628.06 | 403.52 | 341.77 | 294.75 | 151.58 | 258.25 | 327.03 | 322.85 | 358.96 | 82.13 | 9.2 | 2.12 | 293.11
Steam Cost ($) | No Data | No Data | 891.21 | 1797.97 | 1944.79 | 1832.82 | 1569.58 | 1951.82 | 458.42 | 104.23 | 58.99 | 60.32 | 136.82
Gray | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01
Electricity (KWhs) | 23914 | 27754 | 25834 | 24168 | 24141 | 23146 | 24026 | 27725 | 27357 | 21502 | 17073 | 19805 | 27005
Steam Usage (lbs) | No Data | No Data | 92800 | 117770 | 136210 | 137600 | 148740 | 154340 | 36400 | 8490 | 4260 | 8090 | 10320
Water Usage (gallons) | 45200 | 60200 | 52100 | 44700 | 22500 | 42300 | 51800 | 45000 | 54700 | 13000 | 700 | 700 | 36500
Chilled water (ton-hrs) | No Data | 18000 | 11000 | 8000 | 6000 | 7000 | 6000 | 6000 | 9000 | 13000 | 16000 | 18000 | 22000
Electricity Cost ($) | 1728.46 | 2010.16 | 1688.44 | 1484.19 | 1584.24 | 1618.56 | 1573.72 | 1602.89 | 1559.29 | 1548.76 | 1744.49 | 1859.95 | 1834.15
Water Costs ($) | 315.97 | 422.47 | 365.63 | 313.69 | 157.9 | 196.85 | 363.52 | 318.6 | 387.28 | 92.04 | 4.96 | 4.96 | 258.42
Steam Cost ($) | No Data | No Data | 725.1 | 920.2 | 1064.28 | 1075.14 | 1162.18 | 1205.94 | 284.41 | 66.34 | 33.29 | 63.21 | 80.64
Hinshaw | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01
Electricity (KWhs) | 25679 | 31337 | 29489 | 27971 | 28908 | 26763 | 27672 | 31291 | 30512 | 25464 | 19405 | 21420 | 30854
Steam Usage (lbs) | No Data | No Data | No Data | 96840 | 125400 | 125050 | 151390 | 144990 | 184780 | 10300 | 7640 | 8030 | 15530
Water Usage (gallons) | No Data | No Data | 46900 | 39800 | 19400 | 32000 | 42400 | 37400 | 45600 | 12100 | 2600 | 2800 | 35800
Chilled water (ton-hrs) | No Data | 21000 | 12200 | 9100 | 9100 | 18900 | 7300 | 9900 | 13500 | 13900 | 15800 | 19300 | 26100
Electricity Cost ($) | 1856.04 | 2269.67 | 1927.32 | 1606.96 | 1772.75 | 1676.77 | 1685.69 | 1941.48 | 1841.64 | 1526.58 | 1310.36 | 1542.16 | 2190.56
Water Costs ($) | No Data | No Data | 329.13 | 279.31 | 136.14 | 224.57 | 297.55 | 264.79 | 322.85 | 85.67 | 18.41 | 19.82 | 253.46
Steam Cost ($) | No Data | No Data | No Data | 756.66 | 979.82 | 977.08 | 1182.89 | 1132.88 | 1443.78 | 80.48 | 59.7 | 62.74 | 121.34
Jamison | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01
Electricity (KWhs) | 21632 | 27770 | 26421 | 25025 | 25443 | 20716 | 25336 | 23549 | 26961 | 22441 | 18315 | 18909 | 27052
Steam Usage (lbs) | No Data | No Data | No Data | No Data | 21780 | 22750 | 50090 | 28480 | 16650 | 9890 | 6550 | 6880 | 13410
Water Usage (gallons) | 29700 | 56100 | 49300 | 43000 | 22800 | 34600 | 46300 | 41900 | 48700 | 12100 | 600 | 900 | 32800
Chilled water (ton-hrs) | No Data | 11000 | 30000 | 4000 | 5000 | 3000 | 4000 | 4000 | 6000 | 7000 | 7000 | 9000 | 8000
Electricity Cost ($) | 1563.53 | 2011.32 | 1726.8 | 1437.71 | 1560.26 | 1297.91 | 1543.39 | 1461.12 | 1627.31 | 1345.35 | 1236.76 | 1361.38 | 1920.63
Water Costs ($) | 208.22 | 393.7 | 345.98 | 301.76 | 160.01 | 242.82 | 324.92 | 296.65 | 344.8 | 95.67 | 4.25 | 6.37 | 232.22
Steam Cost ($) | No Data | No Data | No Data | No Data | 170.18 | 177.76 | 391.38 | 222.53 | 130.1 | 77.28 | 51.18 | 53.75 | 104.78
Shaw | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01
Electricity (KWhs) | 15397 | 52787 | 47182 | 41178 | 42583 | 39584 | 41946 | 52401 | 49958 | 41964 | 32814 | 35588 | 48804
Steam Usage (lbs) | No Data | No Data | 391020 | 332710 | 435580 | 410910 | 609370 | 925610 | 197840 | 63070 | 7700 | 3820 | 5540
Water Usage (gallons) | 56200 | 92800 | 82500 | 69400 | 36900 | 64000 | 79100 | 77500 | 90900 | 22000 | 2700 | 2700 | 60400
Chilled water (ton-hrs) | No Data | 45000 | 10600 | 23700 | 27400 | 20100 | 22100 | 28200 | 32700 | 38200 | 39400 | 41900 | 49900
Electricity Cost ($) | 1112.87 | 3823.24 | 3083.68 | 2365.72 | 2611.35 | 2480.03 | 2555.21 | 3251.26 | 3015.36 | 2515.76 | 2215.83 | 2562.2 | 3464.97
Water Costs ($) | 394.4 | 651.25 | 578.97 | 487.03 | 258.96 | 449.14 | 555.11 | 548.7 | 643.57 | 155.76 | 19.12 | 19.12 | 427.63
Steam Cost ($) | No Data | No Data | 3055.25 | 2599.64 | 3403.42 | 3210.66 | 4761.33 | 7232.28 | 1545.83 | 492.8 | 60.16 | 29.85 | 43.28
Elizabeth City State University - Gilchrist Education & Psychology Building
Utility | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01
Electricity Usage (KWhs) | 54336 | 58368 | 53952 | 53376 | 45888 | 48576 | 46848 | 58752 | 55296 | 53376 | 50304 | 52800
Water Usage (gallons) | 4943.65 | 6841.98 | 6520.6 | 6752.78 | 5081.9 | 2234.21 | 3043.51 | 4648 | 3766.27 | 6580.2 | 4356.57 | 5399.32
Elecricity Cost ($) | 6578.89 | 7712.48 | 6939.67 | 6326.58 | 5448.14 | 5286.63 | 5312.63 | 7388.65 | 6443.39 | 6751.35 | 6442.57 | 6710.76
Water-Sewer Costs ($) | 651.3101 | 763.5355 | 687.0273 | 626.3314 | 539.3659 | 523.3764 | 525.9504 | 731.4764 | 637.8956 | 668.3837 | 637.8144 | 664.3652
Elizabeth City State University - Viking Tower (New Mitchell Lewis Residence Hall)
Utility | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01
Electricity Usage (KWhs) | 0 | 30708 | 65943 | 66790 | 53679 | 46195 | 47003 | 49174 | 48672 | 56553 | 53063 | 47081
Water Usage (gallons) | 0 | 139932 | 165960 | 181700 | 181700 | 181700 | 110600 | 174615 | 106988 | 194743 | 103497 | 8967
Elecricity Cost ($) | 0 | 3239.65 | 7029.52 | 6819.22 | 5625.51 | 4905.87 | 5052.83 | 5217.33 | 5134.88 | 5887.15 | 5709.58 | 5065.92
Water-Sewer Costs ($) | 0 | 1371.33 | 1626.41 | 1798.83 | 1798.83 | 1798.33 | 1106 | 1746.15 | 1068.88 | 1947.43 | 1014.27 | 85.93
Pitt Community College - Russell Classroom Building Energy Use 2012 / 2013
Utility | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01
Gas Usage (CCF) |  | 167 | 463 | 1528 | 2113 | 2787 | 2470 | 2289 | 1954 | 1445 | 985 | 774
Electricity Usage (KWhs) | *** | *** | *** | *** | *** | 57792 | 50205 | 55872 | 62784 | 67008 | 61248 | 72384
Water Usage (gallons) | *** | *** | 39.06 | 43.42 | 31.83 | 8.66 | 52.09 | 41.97 | 41.97 | 34.73 | 11.57 | 13.02
Gas Cost ($) |  | 189.8 | 472.53 | 1343.94 | 1926.01 | 2582.16 | 2301.64 | 2141.48 | 1846.07 | 1397.47 | 990.42 | 804.59
Elecricity Cost ($) | *** | *** | *** | *** | *** | 2847.99 | 2474.25 | 2753.37 | 3094 | 3302.15 | 3018.3 | 3567.08
Water-Sewer Costs ($) | *** | *** | 230.31 | 246.81 | 202.97 | 115.32 | 279.61 | 241.33 | 241.33 | 213.94 | 126.34 | 131.82
| *** | Account was in Centurion's name until October 2012
| *** | CER, CIT, and FSC are all on one meter, therefore we do not have access to information for each individual building.
As a result we must rely on GUC to provide us with any information for these individual meters.
GUC is only able to pull information from this calendar year, therefore they provided me with January 2013 to present.
In addition, the information provided by GUC is just the KWHs and does not include any demand usage.
Pitt Community College - Russell Classroom Building Energy Use | [5 empty] | data from 03/06/14 email from Steve Campbell/PDC
[11 empty] | June | July | August | September | October | November | December | January | February
Gas Usage (CCF) | [10 empty] | 6285 | 5997 | 5925 | 6197 | 6678 | 7345 | 7872 | 9243 | 8223
Electricity Usage (KWhs) | [10 empty] | 779.2 | 632.3 | 627.7 | 569.5 | 510.4 | 401.8 | 287.5 | 329.5
Water Usage (gallons) | [10 empty] | 10560 | 6334 | 5644 | 5322 | 5841 | 5419 | 4256 | 6332 | 7040
NCCU Chidley Residence Hall
Utility | July 012 | Aug 012 | Sept 012 | Oct 012 | Nov 012 | Dec 012 | Jan 013 | Feb 013 | Mar 013 | April 013 | May 013 | June 013 | July013 | Aug013
Electricity Usage (KWhs) | 151502 | 172355 | 192858 | 139482 | 138822 | 111327 | 71743 | 107158 | 86119 | 109632 | 124337 | 111701 | 166836 | 197374
Steam Usage (lbs) | na | na | na | na | na | na | na | na | na | na | na | na | na | na
Natural Gas ( Therms) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 29 | 0 | 0 | 158 | 280 | 299
Water Usage (gallons) | 269 | 621 | 10629 | 17430 | 13248 | 17123 | 3067 | 14609 | 93783 | 5825827 | 100680 | 5521 | 121632 | 193313
Elecricity Cost ($) | 9999.13 | 12409.56 | 13885.78 | 9484.78 | 8329.32 | 6568.29 | 4448.07 | 6429.48 | 5253.26 | 6687.55 | 7584.56 | 6702.06 | 12345.86 | 11823
Steam Costs ($) | na | na | na | na | na | na | na | na | na | na | na | na | na | na
Natural Gas ( $) | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 24.82 | 29 | 17.5 | 0 | 158 | 291.38 | 309.81
Water-Sewer Costs ($) | 197.52 | 206.7 | 294.2 | 353.65 | 317.1 | 350.97 | 228.09 | 329 | 1021.19 | 51138.26 | 4064.32 | 1402.93 | 1276.9 | 3674.22
NOTE: Chidley North has 2 water meters. Water meter No 1 and Water meter No 2.
●Water bill for April 013:City Durham activated water meter No 2 in April 2012. NCCU had to pay city Durham water used from Meter 2* since meter installed in 011
●Steam Usage (lbs): na. Monthly steam data ( lbs) is not reliable. Control contractor is working on it.
●Steam meter : Need to calibrate the meter and Schneider Electric ( BAS) Programer is working with our IT for internet access to building BAS . Expect having steam data in coming months
Student Health Center Addition
Actual Utility Usage*
Utility | 2012-08-12 | 2012-09-21 | 2012-10-14 | 2012-11-15 | 2012-12-12 | 2013-01-18 | 2013-02-14 | 2013-03-13 | 2013-04-12 | 2013-05-18 | 2013-06-20 | 2012-07-23 10:00 | Total
Electric Usage (kWh) | 58922 | 64433 | 27834 | 43379 | 52554 | 65640 | 42990 | 64258 | 68459 | 59732 | 31392 | 60060 | 639653
Chilled Water Usage (Dtherms) | 606.81 | 560.77 | 299.08 | 141.46 | 129.51 | 135.82 | 154.11 | 97.66 | 268.74 | 331.86 | 715.98 | 1017.16 | 4458.96
Water (ccf) | 2917.67 | 1691.9 | 3271.34 | 2003.71 | 4794.52 | 1859.64 | 2031.25 | 3090.73 | 2363.03 | 959.48 | 2798.29 | 3467.83 | 31249.39
Steam Usage (1,000 lbs)** | 25.08 | 25 | 67.5 | 158 | 364 | 464 | 125.83 | 489 | 451 | 178.33 | 174 | 174 | 2695.74
Electric Cost ($) | 4949.45 | 5412.37 | 2338.06 | 3643.84 | 4414.54 | 5513.76 | 3611.16 | 5397.67 | 5750.56 | 5017.49 | 2636.93 | 5225.22 | 53911.05
Chilled Water Cost ($) | 8325.43 | 7693.76 | 4103.38 | 1940.83 | 1776.88 | 1863.45 | 2114.39 | 1339.9 | 3687.11 | 4553.12 | 9823.25 | 13945.26 | 61166.76
Water ($) | 444.09 | 257.52 | 497.92 | 304.98 | 729.76 | 283.05 | 309.17 | 470.43 | 359.67 | 146.04 | 425.92 | 529.44 | 4757.99
Steam Cost ($)** | 345 | 344 | 930.87 | 2183.37 | 5019.56 | 6398.56 | 1735.2 | 6743.31 | 6219.29 | 2459.17 | 2401.8 | 2511.53 | 37291.66
*Only whole building meter installed
** Steam meter is not reading properly

## 11.12 Meter Data
`